## Selection
Product family |  | Product type | Auxiliary voltage | Part
Drive: | Aux. Contr. Volt.: | Part category: | Part type: | Part: | Qty: | Remarks:
Clear selections

## Tmax settings
ACS800 MCB:t ja MCCB:t taulukosta "ACS800 mains cable fuses and circuit breakers"
ACS800 Nsin filtterit katalogista
Relase and Tmax frame size
Electronic release PR22x must be used
Only the recommended Tmax frame size is allowed to be used
Settings
| I1 | I1*In >=Icntmax
| t1 | 3s, if not mentioned otherwise
If S and I functions are alternative the I-function must be used
| I3 | 3x
If bigger release than the recommended is used then smaller I-factor must be used to have the same RMS level (three times the nominal current (In) of the release unit)
Example
For Tmax T4 recommended release type is 250A, but 320A release module is used
The L-factor must have value 0.8 (250/320=0.78)
The I-factor must have value 2.5 (3*250/320=2.34)
Installation and placement
Follow instructions given by circuit breaker manufacturer on assembly conditions. Make sure that escaping hot ionised gases don't cause harm.
Loadability
Follow instructions given by circuit breaker manufacturer on loadability under actual conditions.

## ACS850_ACSM1_ACQ810
|  |  | Supply cables |  | Supply cable fuses (gG) | [20 empty] | Supply cable fuses (aR) | [15 empty] | Supply cable fuses (UL) | [23 empty] | DC connection fuses (aR) | [14 empty] | Miniature circuit breakers (MCB) for max. 400V supply | [12 empty] | Miniature circuit breakers (MCB) for max. 500V supply | [11 empty] | Limiters for S800 series MCB's |  |  |  | Moulded case circuit breakers (MCCB) | [8 empty] | Main Contactor | [29 empty] | du/dt filters (IP22) |  |  |  |  | du/dt filters (IP54) |  |  |  |  | du/dt filters (IP00) |  | Braking resistors
Type |  | Current rating | Mains Cables |  | gG Fuses | [20 empty] | aR Fuses | [15 empty] | UL Fuses | [23 empty] | aR Fuses | [14 empty] | Miniature circuit breakers (MCB) | [12 empty] | Miniature circuit breakers (MCB) | [11 empty] | Limiters |  |  |  | Moulded case circuit breakers (MCCB) | [8 empty] | Contactor | [29 empty] | du/dt filters |  |  |  |  | du/dt filters |  |  |  |  | du/dt filters |  | Braking resistors
[5 empty] | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG | gG |  |  | aR | aR | aR | aR | aR | aR | aR Fuses | aR | aR Fuses | aR | aR Fuses | aR | aR Fuses | aR | aR Fuses | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class T / CSA HRCI-T | UL Class L / CSA HRCI-L | UL Class L / CSA HRCI-L | L-class | aR | aR | aR | aR | aR | aR | aR | aR | aR | aR | aR | aR | aR | aR | aR | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 15kA@400V | Icu = 50kA@400V | Icu = 50kA@400V |  | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 15kA@500V | Icu = 10kA@500V |  | Icu = 100kA@400V, 50kA@500V | Icu = 100kA@400V, 50kA@500V | Icu = 100kA@400V, 50kA@500V |  |  | Icu = 85kA@400V | Icu = 120kA@400V | Icu = 120kA@400V | Icu = 120kA@400V | Tmax Moulded Case Circuit Breaker | Icu = 100kA@400V | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | IP22 | IP22 | IP22 | IP22 |  | IP54 | IP54 | IP54 | IP54 |  | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20
|  | I2N |  |  | ABB: OFAF000H6, 6A/500V, DIN000 | ABB: OFAF000H10, 10A/500V, DIN000 | ABB: OFAF000H16, 16A/500V, DIN000 | ABB: OFAF000H20, 20A/500V, DIN000 | ABB: OFAF000H25, 25A/500V, DIN000 | ABB: OFAF000H32, 32A/500V, DIN000 | ABB: OFAF000H40, 40A/500V, DIN000 | ABB: OFAF000H50, 50A/500V, DIN000 | ABB: OFAF000H63, 63A/500V, DIN000 | ABB: OFAF000H80, 80A/500V, DIN000 | ABB: OFAF000H100, 100A/500V, DIN000 | ABB: OFAF00H125, 125A/500V, DIN00 | ABB: OFAF00H160, 160A/500V, DIN00 | ABB: OFAF1H200, 200A/500V, DIN1 | ABB: OFAF1H224, 224A/500V, DIN1 | ABB: OFAF1H250, 250A/500V, DIN1 | ABB: OFAF2H315, 315A/500V, DIN2 | ABB: OFAF3H500, 500A/500V, DIN3 | ABB: OFAF3H630, 630A/500V, DIN3 | ABB: OFAF3H800, 800A/500V, DIN3 | gG fuse is too slow for this drive | NOT DEFINED | Bussmann: 170M1569, 160A/690V, DIN000 | Bussmann: 170M1572, 315A/690V, DIN000 | Bussmann: 170M3817, 315A/690V, DIN1 | Bussmann: 170M3819, 400A/690V, DIN1 | Bussmann: 170M5810, 500A/690V, DIN2 | Bussmann: 170M5811, 550A/690V, DIN2 | Bussmann: 170M6810D 630A, 690V, 490 kA2s | Bussmann: 170M6812, 800A/690V, DIN3 | Bussmann: 170M6812D 800A, 690V, 490 kA2s | Bussmann: 170M6814, 1000A/690V, DIN3 | Bussmann: 170M6814D 1000A, 690V, 985 kA2s | Bussmann: 170M8554, 1250A/690V, DIN3 | Bussmann: 170M8554D 1250A, 690V, 2150 kA2s | Bussmann: 170M8555, 1400A/690V, DIN3 | Bussmann: 170M8557D 1600A, 690V,4150 kA2s | Bussmann: JJS-6, 6A/600V | Bussmann: JJS-10, 10A/600V | Bussmann: JJS-15, 15A/600V | Bussmann: JJS-20, 20A/600V | Bussmann: JJS-25, 25A/600V | Bussmann: JJS-35, 35A/600V | Bussmann: JJS-45, 45A/600V | Bussmann: JJS-50, 50A/600V | Bussmann: JJS-70, 70A/600V | Bussmann: JJS-80, 80A/600V | Bussmann: JJS-100, 100A/600V | Bussmann: JJS-125, 125A/600V | Bussmann: JJS-150, 150A/600V | Bussmann: JJS-200, 200A/600V | Bussmann: JJS-225, 225A/600V | Bussmann: JJS-250, 250A/600V | Bussmann: JJS-300, 300A/600V | Bussmann: JJS-350, 350A/600V | Bussmann: JJS-400, 400A/600V | Bussmann: JJS-500, 500A/600V | Bussmann: JJS-600, 600A/600V | Ferraz: A4BY800, 800A/600V | Ferraz: A4BY900, 900A/600V | Ferraz: A4BY1000, 1000A/600V | Bussmann: 170M1559, 16A/690V, DIN000 | Bussmann: 170M1560, 20A/690V, DIN000 | Bussmann: 170M1562, 32A/690V, DIN000 | Bussmann: 170M1565, 63A/690V, DIN000 | Bussmann: 170M1567, 100A/690V, DIN000 | Bussmann: 170M1569, 160A/690V, DIN000 | Bussmann: 170M3815, 200A/690V, DIN1 | Bussmann: 170M3817, 315A/690V, DIN1 | Bussmann: 170M3819, 400A/690V, DIN1 | Bussmann: 170M5810, 500A/690V, DIN2 | Bussmann: 170M5811, 550A/690V, DIN2 | Bussmann: 170M6812, 800A/690V, DIN3 | Bussmann: 170M6814, 1000A/690V, DIN3 | Bussmann: 170M8554, 1250A/690V, DIN3 | Bussmann: 170M8557, 1600A/690V, DIN3 | S 203 M-K06 | S 203 M-K10 | S 203 M-K13 | S 203 M-K16 | S 203 M-K20 | S 203 M-K25 | S 203 M-K32 | S 203 M-K40 | S 203 M-K50 | S 203 M-K63 | S 803 S-K80 | S 803 S-K100 | NOT AVAILABLE | S 803 S-K10 | S 803 S-K13 | S 803 S-K16 | S 803 S-K20 | S 803 S-K25 | S 803 S-K32 | S 803 S-K40 | S 803 S-K50 | S 803 S-K63 | S 803 S-K80 | S 803 S-K100 | NOT AVAILABLE | S 803 S-SCL32 | S 803 S-SCL63 | S 803 S-SCL125 | NOT AVAILABLE | NOT AVAILABLE | T2L160 PR221DS-LS/I | T4L250 PR221DS-LS/I | T4L320 PR221DS-LS/I | T5L630 PR221DS-LS/I | ABB: 1SDA054412R1 (T5H 630 PR221DS-LS/I In=630 3p F F) | T6L800 PR221DS-LS/I | ABB: 1SDA069428R1 (T6V 800 PR221DS-LS/I In=800 3p F F) | ABB: 1SDA062770R1 (T7H 1000 PR231/P LS/I In=1000A 3p F F) | ABB: A9-30-22-80 (25A,690V 220-230V/50Hz) | ABB: A9-30-22-84 (25A,690V 110-1200V/60Hz) | ABB: A12-30-22-80 (27A,690V 220-230V/50Hz) | ABB: A12-30-22-84 (27A,690V 110-1200V/60Hz) | ABB: A16-30-22-80 (30A,690V 220-230V/50Hz) | ABB: A16-30-22-84 (30A,690V 110-1200V/60Hz) | ABB: A26-30-22-80 (45A,690V 220-230V/50Hz) | ABB: A26-30-22-84 (45A,690V 110-1200V/60Hz) | ABB: A30-30-22-80 (55A,690V 220-230V/50Hz) | ABB: A30-30-22-84 (55A,690V 110-1200V/60Hz) | ABB: A40-30-22-80 (60A,690V 220-230V/50Hz) | ABB: A40-30-22-84 (60A,690V 110-1200V/60Hz) | ABB: A50-30-22-80 (100A,690V 220-230V/50Hz) | ABB: A50-30-22-84 (100A,690V 110-1200V/60Hz) | ABB: A75-30-22-80 (125A,690V 220-230V/50Hz) | ABB: A75-30-22-84 (125A,690V 110-1200V/60Hz) | ABB: A110-30-22-80 (160A,690V 220-230V/50Hz) | ABB: A110-30-22-84 (160A,690V 110-1200V/60Hz) | ABB: A145-30-22-80 (250A,1000V 220-230V/50Hz) | ABB: A145-30-22-84 (250A,1000V 110-120V/60Hz) | ABB: A185-30-22-80 (275A,1000V 220-230V/50Hz) | ABB: A185-30-22-84 (275A,1000V 110-120V/60Hz) | ABB: A210-30-22-80 (350A,1000V 220-230V/50Hz) | ABB: A210-30-22-84 (350A,1000V 110-120V/60Hz) | ABB: A300-30-22-80 (450A,1000V 220-230V/50Hz) | ABB: A300-30-22-84 (450A,1000V 110-120V/60Hz) | ABB: AF400-30-22-70 (600A,1000V 100-250V/50-60Hz) | ABB: AF460-30-22-70 (700A,1000V 100-250V/50-60Hz) | ABB: AF580-30-22-70 (800A,1000V 100-250V/50-60Hz) | ABB: AF750-30-22-70 (1050A,1000V 100-250V/50-60Hz) | NOCH0016-62 | NOCH0030-62 | NOCH0070-62 | NOCH0120-62 | NOT AVAILABLE | NOCH0016-65 | NOCH0030-65 | NOCH0070-65 | NOCH0120-65 | NOT AVAILABLE | ABB Drives: FOCH0610-70 | ABB Drives: FOCH0875-70 | JBR-01 | JBR-03 | JBR-04 | JBR-05 | JBR-06 | JBR-09 | SAFUR90F575 | SAFUR80F500 | SAFUR125F500 | SAFUR200F500 | SAFUR210F575 | NOT AVAILABLE
| Frame |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230 | 115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
|  |  |  | Remarks -> | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See aR or UL fuses | See gG or UL fuses | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | See Hardware manual for additional requirements on fuse selection | [12 empty] | See MCCB's | [11 empty] | See MCCB's |  |  |  | See MCCB's | See MCB's | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings | Please see "Tmax settings" sheet for correct MCCB settings
UN = 200 … 240 V |  |  | Cu | Al
ACS850-04-03A0-2 | R2 | 3 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-03A6-2 | R2 | 3.6 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-04A8-2 | R2 | 4.8 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-06A0-2 | R2 | 6 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-08A0-2 | R2 | 8 | 3x1.5+1.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-010A-2 | R3 | 10 | 3x2.5+2.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
ACS850-04-014A-2 | R3 | 14 | 3x2.5+2.5 | - |  |  |  | 3 | [17 empty] | x | [18 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [8 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-018A-2 | R3 | 18 | 3x4+4 | - |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-025A-2 | R4 | 25 | 3x6+6 | 3x25+16Cu |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  | x | [10 empty] | 1 | [28 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-030A-2 | R4 | 30 | 3x6+6 | 3x25+16Cu | [5 empty] | 3 | [15 empty] | x | [20 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [12 empty] | 1 | [26 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-035A-2 | R5 | 35 | 3x10+10 | 3x25+16Cu | [6 empty] | 3 | [14 empty] | x | [20 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [14 empty] | 1 | [24 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-044A-2 | R5 | 44 | 3x10+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [21 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [5 empty] | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-050A-2 | R5 | 50 | 3x16+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [22 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-061A-2 | R6 | 61 | 3x25+16 | 3x25+16Cu | [8 empty] | 3 | [12 empty] | x | [23 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  | x | [18 empty] | 1 | [21 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-078A-2 | R6 | 78 | 3x35+16 | 3x50+16Cu | [9 empty] | 3 | [11 empty] | x | [24 empty] | 3 | [19 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [19 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-094A-2 | R6 | 94 | 3x35+16 | 3x70+21Cu | [10 empty] | 3 | [10 empty] | x | [25 empty] | 3 | [18 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [20 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
UN = 380 … 500 V |  |  | Cu | Al
ACS850-04-03A0-5 | R2 | 3 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-03A6-5 | R2 | 3.6 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-04A8-5 | R2 | 4.8 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-06A0-5 | R2 | 6 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-08A0-5 | R2 | 8 | 3x1.5+1.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACS850-04-010A-5 | R3 | 10 | 3x2.5+2.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
ACS850-04-014A-5 | R3 | 14 | 3x2.5+2.5 | - |  |  |  | 3 | [17 empty] | x | [18 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [8 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-018A-5 | R3 | 18 | 3x4+4 | - |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-025A-5 | R4 | 25 | 3x6+6 | 3x25+16Cu |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  | x | [10 empty] | 1 | [28 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-030A-5 | R4 | 30 | 3x6+6 | 3x25+16Cu | [5 empty] | 3 | [15 empty] | x | [20 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [12 empty] | 1 | [26 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-035A-5 | R5 | 35 | 3x10+10 | 3x25+16Cu | [6 empty] | 3 | [14 empty] | x | [20 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [14 empty] | 1 | [24 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-044A-5 | R5 | 44 | 3x10+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [21 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [5 empty] | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-050A-5 | R5 | 50 | 3x16+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [22 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-061A-5 | R6 | 61 | 3x25+16 | 3x25+16Cu | [8 empty] | 3 | [12 empty] | x | [23 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  | x | [18 empty] | 1 | [21 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-078A-5 | R6 | 78 | 3x35+16 | 3x50+16Cu | [9 empty] | 3 | [11 empty] | x | [24 empty] | 3 | [19 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [19 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACS850-04-094A-5 | R6 | 94 | 3x35+16 | 3x70+21Cu | [10 empty] | 3 | [10 empty] | x | [25 empty] | 3 | [18 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [20 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
ACS850-04-103A-5 | R7 | 103 | 3x50+25 | 3x70+21Cu | [11 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [17 empty] | 2 | [21 empty] | x | [11 empty] | x |  |  |  | x |  | 1 | [21 empty] | 1 | [18 empty] | 1 |  |  |  |  | 1 | [9 empty] | 1
ACS850-04-144A-5 | R7 | 144 | 3x70+35 | - | [12 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [18 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  | 1 | [23 empty] | 1 | [16 empty] | 1 |  |  |  |  | 1 | [10 empty] | 1
ACS850-04-166A-5 | R8 | 166 | 3x95+50 | 3x150+50Cu | [13 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [17 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [14 empty] | 1 |  |  |  |  | 1 | [11 empty] | 1
ACS850-04-202A-5 | R8 | 202 | 3x120+70 | 3x185+57Cu | [14 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [16 empty] | 2 | [18 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [15 empty] | x |  |  |  |  | x | [10 empty] | 1
ACS850-04-225A-5 | R8 | 225 | 3x150+70 | 3x240+95Cu | [15 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [18 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [15 empty] | x |  |  |  |  | x | [10 empty] | 1
ACS850-04-260A-5 | R8 | 260 | 3x185+70 | 3x240+95Cu | [16 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [17 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [25 empty] | 1 | [13 empty] | x |  |  |  |  | x | [10 empty] | 1
ACS850-04-290A-5 | R8 | 290 | 3x240+70 | 2x(3x95) | [16 empty] | 3 | [10 empty] | 3 | [27 empty] | 3 | [15 empty] | 2 | [16 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [27 empty] | 1 | [11 empty] | x |  |  |  |  | x | [11 empty] | 1
ACS850-04-430A-5 | R7 | 430 | 2x(3x150+95) | 2x(3x240+95Cu) | [17 empty] | 3 | [11 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [15 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [28 empty] | 1 | [9 empty] | x |  |  |  |  | x | [10 empty] | 2
ACS850-04-521A-5 | R7 | 521 | 2x(3x240+120) | 3x(3x150+50Cu) | [18 empty] | 3 | [12 empty] | 3 | [25 empty] | 3 | [15 empty] | 2 | [14 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [30 empty] | 1 | [7 empty] | x |  |  |  |  | x | [12 empty] | 2
ACS850-04-602A-5 | R7 | 602 | 3x(3x150+95) | 3x(3x240+95Cu) | [18 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [15 empty] | 2 | [13 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [32 empty] | 1 | [5 empty] | x |  |  |  |  | x | [11 empty] | 2
ACS850-04-693A-5 | R7 | 693 | 3x(3x185+95) | 3x(3x240+95Cu) | [19 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [15 empty] | 2 | [12 empty] | x | [11 empty] | x |  |  |  | x | [6 empty] | 1 | [30 empty] | 1 | [5 empty] | x |  |  |  |  | x | [10 empty] | 4
ACS850-04-720A-5 | R7 | 720 | 3x(3x185+95) | 3x(3x240+95Cu) | [19 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [15 empty] | 2 | [12 empty] | x | [11 empty] | x |  |  |  | x | [6 empty] | 1 | [30 empty] | 1 | [5 empty] | x |  |  |  |  | x | [10 empty] | 4
ACS850-04-387A-5 | G1 | 387 | 2 x (3x120) | 3 x (3x95) | [20 empty] | x | [7 empty] | 3 | [27 empty] | 3 | [31 empty] | x | [11 empty] | x |  |  |  | x | [5 empty] | 1 | [37 empty] | x |  |  |  |  | x | 1 | [9 empty] | 2
ACS850-04-500A-5 | G1 | 500 | 3 x (3x95) | 3 x (3x150) | [20 empty] | x | [9 empty] | 3 | [26 empty] | 3 | [30 empty] | x | [11 empty] | x |  |  |  | x | [5 empty] | 1 | [37 empty] | x |  |  |  |  | x | 1 | [9 empty] | 2
ACS850-04-580A-5 | G1 | 580 | 3 x (3x120) | 3 x (3x185) | [20 empty] | x | [11 empty] | 3 | [25 empty] | 3 | [29 empty] | x | [11 empty] | x |  |  |  | x | [5 empty] | 1 | [37 empty] | x |  |  |  |  | x | 1 | [10 empty] | 2
ACS850-04-650A-5 | G1 | 650 | 3 x (3x150) | 3 x (3x240) | [20 empty] | x | [11 empty] | 3 | [25 empty] | 3 | [29 empty] | x | [11 empty] | x |  |  |  | x | [7 empty] | 1 | [35 empty] | x |  |  |  |  | x | 1 | [10 empty] | 2
ACS850-04-710A-5 | G2 | 710 | 3 x (3x185) | 4 × (3×185) | [20 empty] | x | [13 empty] | 3 | [23 empty] | 3 | [29 empty] | x | [11 empty] | x |  |  |  | x | [8 empty] | 1 | [34 empty] | x |  |  |  |  | x |  | 1 | [9 empty] | 3
ACS850-04-807A-5 | G2 | 807 | 3 x (3x240) | 4 × (3×240) | [20 empty] | x | [15 empty] | 3 | [22 empty] | 3 | [28 empty] | x | [11 empty] | x |  |  |  | x | [8 empty] | 1 | [34 empty] | x |  |  |  |  | x |  | 1 | [9 empty] | 3
ACS850-04-875A-5 | G2 | 875 | 3 x (3x240) | 4 × (3×240) | [20 empty] | x | [15 empty] | 3 | [23 empty] | 3 | [27 empty] | x | [11 empty] | x |  |  |  | x | [8 empty] | 1 | [34 empty] | x |  |  |  |  | x |  | 1 | [9 empty] | 3
UN = 380 … 480 V |  |  | Cu | Al
ACSM1-04Ax-02A5-4 | R2 | 2.5 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACSM1-04Ax-03A0-4 | R2 | 3 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACSM1-04Ax-04A0-4 | R2 | 4 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACSM1-04Ax-05A0-4 | R2 | 5 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACSM1-04Ax-07A0-4 | R2 | 7 | 3x1.5+1.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [6 empty] | 1
ACSM1-04Ax-09A5-4 | R3 | 9.5 | 3x2.5+2.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
ACSM1-04Ax-012A-4 | R3 | 12 | 3x2.5+2.5 | - |  |  |  | 3 | [17 empty] | x | [18 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [8 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-016A-4 | R3 | 16 | 3x4+4 | - |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-024A-4 | R4 | 24 | 3x6+6 | 3x25+16Cu |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  | x | [10 empty] | 1 | [28 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-031A-4 | R4 | 31 | 3x6+6 | 3x25+16Cu | [5 empty] | 3 | [15 empty] | x | [20 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [12 empty] | 1 | [26 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-040A-4 | R5 | 40 | 3x10+10 | 3x25+16Cu | [6 empty] | 3 | [14 empty] | x | [21 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [5 empty] | 1 |  |  | x | [14 empty] | 1 | [25 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-046A-4 | R5 | 46 | 3x16+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [22 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Cx-024A-4 | R4 | 24 | 3x6+6 | 3x25+16Cu |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  | x | [10 empty] | 1 | [28 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Cx-031A-4 | R4 | 31 | 3x6+6 | 3x25+16Cu | [5 empty] | 3 | [15 empty] | x | [20 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [12 empty] | 1 | [26 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Cx-040A-4 | R5 | 40 | 3x10+10 | 3x25+16Cu | [6 empty] | 3 | [14 empty] | x | [21 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [5 empty] | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Cx-046A-4 | R5 | 46 | 3x16+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [22 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-060A-4 | R6 | 60 | 3x25+16 | 3x25+16Cu | [8 empty] | 3 | [12 empty] | x | [23 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  | x | [18 empty] | 1 | [21 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-073A-4 | R6 | 73 | 3x35+16 | 3x50+16Cu | [9 empty] | 3 | [11 empty] | x | [24 empty] | 3 | [19 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [19 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Ax-090A-4 | R6 | 90 | 3x35+16 | 3x70+21Cu | [10 empty] | 3 | [10 empty] | x | [25 empty] | 3 | [18 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [41 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
ACSM1-04Cx-060A-4 | R6 | 60 | 3x25+16 | 3x25+16Cu | [8 empty] | 3 | [12 empty] | x | [23 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  | x | [18 empty] | 1 | [21 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Cx-073A-4 | R6 | 73 | 3x35+16 | 3x50+16Cu | [9 empty] | 3 | [11 empty] | x | [24 empty] | 3 | [19 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [19 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1
ACSM1-04Cx-090A-4 | R6 | 90 | 3x35+16 | 3x70+21Cu | [10 empty] | 3 | [10 empty] | x | [25 empty] | 3 | [18 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [20 empty] | 1 |  |  |  |  | 1 | [7 empty] | 1
ACSM1-04Ax-110A-4 | R8 | 110 | 3x95+50 | 3x150+50Cu | [12 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [17 empty] | 2 | [20 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [20 empty] | 1 | [18 empty] | 1 |  |  |  |  | 1 | [11 empty] | 1
ACSM1-04Ax-135A-4 | R8 | 135 | 3x120+70 | 3x185+57Cu | [13 empty] | 3 | [11 empty] | 3 | [24 empty] | 3 | [17 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [22 empty] | 1 | [17 empty] | x |  |  |  |  | x | [10 empty] | 1
ACSM1-04Ax-175A-4 | R8 | 175 | 3x150+70 | 3x240+95Cu | [13 empty] | 3 | [12 empty] | 3 | [24 empty] | 3 | [16 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [15 empty] | x |  |  |  |  | x | [10 empty] | 1
ACSM1-04Ax-210A-4 | R8 | 210 | 3x185+70 | 3x240+95Cu | [15 empty] | 3 | [11 empty] | 3 | [25 empty] | 3 | [15 empty] | 2 | [18 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [23 empty] | 1 | [15 empty] | x |  |  |  |  | x | [10 empty] | 1
ACSM1-04Lx-110A-4 | R8 | 110 | 3x95+50 | 3x150+50Cu | [12 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [17 empty] | 2 | [20 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [20 empty] | 1 | [18 empty] | 1 |  |  |  |  | 1 | [11 empty] | 1
ACSM1-04Lx-135A-4 | R8 | 135 | 3x120+70 | 3x185+57Cu | [13 empty] | 3 | [11 empty] | 3 | [24 empty] | 3 | [17 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [22 empty] | 1 | [17 empty] | x |  |  |  |  | x | [10 empty] | 1
ACSM1-04Lx-175A-4 | R8 | 175 | 3x150+70 | 3x240+95Cu | [13 empty] | 3 | [12 empty] | 3 | [24 empty] | 3 | [16 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [15 empty] | x |  |  |  |  | x | [10 empty] | 1
ACSM1-04Lx-210A-4 | R8 | 210 | 3x185+70 | 3x240+95Cu | [15 empty] | 3 | [11 empty] | 3 | [25 empty] | 3 | [15 empty] | 2 | [18 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [23 empty] | 1 | [15 empty] | x |  |  |  |  | x | [10 empty] | 1
ACSM1-04Lx-260A-4 | R8 | 260 | 3x240+70 | 2x(3x95) | [16 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [16 empty] | 2 | [16 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [25 empty] | 1 | [13 empty] | x |  |  |  |  | x | [11 empty] | 1
ACSM1-04-390A-4 | G1 | 350 | 2 x (3x120) | 3 x (3x120) | [20 empty] | x | [7 empty] | 3 | [59 empty] | x | [11 empty] | x |  |  |  | x | [43 empty] | x |  |  |  |  | x | [11 empty] | 2
ACSM1-04-500A-4 | G1 | 450 | 3 x (3x95) | 3 x (3x150) | [20 empty] | x | [9 empty] | 3 | [57 empty] | x | [11 empty] | x |  |  |  | x | [43 empty] | x |  |  |  |  | x | [11 empty] | 2
ACSM1-04-580A-4 | G2 | 530 | 3 x (3x120) | 3 x (3x185) | [20 empty] | x | [11 empty] | 3 | [55 empty] | x | [11 empty] | x |  |  |  | x | [43 empty] | x |  |  |  |  | x | [11 empty] | 3
ACSM1-04-635A-4 | G2 | 580 | 3 x (3x150) | 3 x (3x240) | [20 empty] | x | [11 empty] | 3 | [55 empty] | x | [11 empty] | x |  |  |  | x | [43 empty] | x |  |  |  |  | x | [11 empty] | 3
UN = 200 … 240 V |  |  | Cu | Al
ACQ810-04-02A7-2 | R2 | 2.7 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-03A0-2 | R2 | 3 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-03A5-2 | R2 | 3.5 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-04A9-2 | R2 | 4.9 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-06A3-2 | R2 | 6.3 | 3x1.5+1.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-08A3-2 | R3 | 8.3 | 3x2.5+2.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-11A0-2 | R3 | 11 | 3x2.5+2.5 | - |  |  |  | 3 | [17 empty] | x | [18 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [8 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-14A4-2 | R3 | 14.4 | 3x4+4 | - |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-021A-2 | R4 | 21 | 3x6+6 | 3x25+16Cu |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  | x | [10 empty] | 1 | [28 empty] | 1 |  |  |  |  | 1 | [16 empty] | x
ACQ810-04-028A-2 | R4 | 28 | 3x6+6 | 3x25+16Cu | [5 empty] | 3 | [15 empty] | x | [20 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [12 empty] | 1 | [26 empty] | 1 |  |  |  |  | 1 | [16 empty] | x
ACQ810-04-035A-2 | R5 | 35 | 3x10+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [21 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [5 empty] | 1 |  |  | x | [14 empty] | 1 | [25 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-040A-2 | R5 | 40 | 3x16+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [22 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-053A-2 | R6 | 53 | 3x25+16 | 3x25+16Cu | [8 empty] | 3 | [12 empty] | x | [23 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-067A-2 | R6 | 67 | 3x35+16 | 3x50+16Cu | [9 empty] | 3 | [11 empty] | x | [24 empty] | 3 | [19 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [19 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-080A-2 | R6 | 80 | 3x35+16 | 3x70+21Cu | [10 empty] | 3 | [10 empty] | x | [25 empty] | 3 | [18 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [20 empty] | 1 |  |  |  |  | 1 | [14 empty] | x
UN = 380 … 480 V |  |  | Cu | Al
ACQ810-04-02A7-4 | R2 | 2.7 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-03A0-4 | R2 | 3 | 3x1.5+1.5 | - | 3 | [20 empty] | x | [15 empty] | 3 | [23 empty] | 2 | [14 empty] | 1 | [12 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-03A5-4 | R2 | 3.5 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-04A9-4 | R2 | 4.9 | 3x1.5+1.5 | - |  | 3 | [19 empty] | x | [16 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-06A3-4 | R2 | 6.3 | 3x1.5+1.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-08A3-4 | R3 | 8.3 | 3x2.5+2.5 | - |  |  | 3 | [18 empty] | x | [17 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-11A0-4 | R3 | 11 | 3x2.5+2.5 | - |  |  |  | 3 | [17 empty] | x | [18 empty] | 3 | [22 empty] | 2 | [16 empty] | 1 | [11 empty] | 1 | [8 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-14A4-4 | R3 | 14.4 | 3x4+4 | - |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [21 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | x | [8 empty] | 1 | [29 empty] | 1 |  |  |  |  | 1 | [17 empty] | x
ACQ810-04-021A-4 | R4 | 21 | 3x6+6 | 3x25+16Cu |  |  |  |  | 3 | [16 empty] | x | [19 empty] | 3 | [22 empty] | 2 | [17 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  | x | [10 empty] | 1 | [28 empty] | 1 |  |  |  |  | 1 | [16 empty] | x
ACQ810-04-028A-4 | R4 | 28 | 3x6+6 | 3x25+16Cu | [5 empty] | 3 | [15 empty] | x | [20 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 |  |  | x | [12 empty] | 1 | [26 empty] | 1 |  |  |  |  | 1 | [16 empty] | x
ACQ810-04-035A-4 | R5 | 35 | 3x10+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [21 empty] | 3 | [21 empty] | 2 | [18 empty] | 1 | [11 empty] | 1 | [5 empty] | 1 |  |  | x | [14 empty] | 1 | [25 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-040A-4 | R5 | 40 | 3x16+10 | 3x25+16Cu | [7 empty] | 3 | [13 empty] | x | [22 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-053A-4 | R6 | 53 | 3x25+16 | 3x25+16Cu | [8 empty] | 3 | [12 empty] | x | [23 empty] | 3 | [20 empty] | 2 | [19 empty] | 1 | [11 empty] | 1 |  |  |  |  | 1 |  | x | [16 empty] | 1 | [23 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-067A-4 | R6 | 67 | 3x35+16 | 3x50+16Cu | [9 empty] | 3 | [11 empty] | x | [24 empty] | 3 | [19 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [19 empty] | 1 |  |  |  |  | 1 | [15 empty] | x
ACQ810-04-080A-4 | R6 | 80 | 3x35+16 | 3x70+21Cu | [10 empty] | 3 | [10 empty] | x | [25 empty] | 3 | [18 empty] | 2 | [20 empty] | 1 | [11 empty] | 1 |  |  |  | 1 |  | x | [20 empty] | 1 | [20 empty] | 1 |  |  |  |  | 1 | [14 empty] | x
ACQ810-04-098A-4 | R7 | 98 | 3x50+25 | 3x70+21Cu | [11 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [17 empty] | 2 | [21 empty] | x | [11 empty] | x |  |  |  | x |  | 1 | [19 empty] | 1 | [20 empty] | 1 |  |  |  |  | 1 | [14 empty] | x
ACQ810-04-138A-4 | R7 | 138 | 3x70+35 | - | [12 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [18 empty] | 2 | [19 empty] | x | [11 empty] | x |  |  |  | x |  | 1 | [23 empty] | 1 | [16 empty] | 1 |  |  |  |  | 1 | [14 empty] | x
ACQ810-04-162A-4 | R8 | 162 | 3x120+70 | 3x185+57Cu | [14 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [16 empty] | 2 | [18 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [15 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-203A-4 | R8 | 203 | 3x150+70 | 3x240+95Cu | [15 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [18 empty] | x | [11 empty] | x |  |  |  | x |  |  | 1 | [24 empty] | 1 | [15 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-240A-4 | R8 | 240 | 3x185+70 | 3x240+95Cu | [16 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [17 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [23 empty] | 1 | [15 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-286A-4 | R8 | 286 | 3x240+70 | 2x(3x95) | [16 empty] | 3 | [10 empty] | 3 | [27 empty] | 3 | [15 empty] | 2 | [16 empty] | x | [11 empty] | x |  |  |  | x |  |  |  | 1 | [27 empty] | 1 | [11 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-302A-4 | R7 | 302 | 2x(3x150+95) | 2x(3x240+95Cu) | [17 empty] | 3 | [11 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [15 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [26 empty] | 1 | [11 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-361A-4 | R7 | 361 | 2x(3x150+95) | 2x(3x240+95Cu) | [17 empty] | 3 | [11 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [15 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [28 empty] | 1 | [9 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-414A-4 | R7 | 414 | 2x(3x150+95) | 2x(3x240+95Cu) | [17 empty] | 3 | [11 empty] | 3 | [26 empty] | 3 | [15 empty] | 2 | [15 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [28 empty] | 1 | [9 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-477A-4 | R7 | 477 | 2x(3x240+120) | 3x(3x150+50Cu) | [18 empty] | 3 | [12 empty] | 3 | [25 empty] | 3 | [15 empty] | 2 | [14 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [30 empty] | 1 | [7 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-550A-4 | R7 | 550 | 3x(3x150+95) | 3x(3x240+95Cu) | [18 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [15 empty] | 2 | [13 empty] | x | [11 empty] | x |  |  |  | x |  |  |  |  | 1 | [30 empty] | 1 | [7 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-616A-4 | R7 | 616 | 3x(3x185+95) | 3x(3x240+95Cu) | [19 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [15 empty] | 2 | [12 empty] | x | [11 empty] | x |  |  |  | x | [6 empty] | 1 | [30 empty] | 1 | [5 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-704A-4 | R7 | 704 | 3x(3x185+95) | 3x(3x240+95Cu) | [19 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [15 empty] | 2 | [12 empty] | x | [11 empty] | x |  |  |  | x | [6 empty] | 1 | [30 empty] | 1 | [5 empty] | x |  |  |  |  | x | [13 empty] | x
ACQ810-04-377A-4 | G1 | 377 | 2 x (3x120) | 3 x (3x120) | [20 empty] | x | [7 empty] | 3 | [27 empty] | 3 | [31 empty] | x | [11 empty] | x |  |  |  | x | [5 empty] | 1 | [37 empty] | x |  |  |  |  | x | 1 | [12 empty] | x
ACQ810-04-480A-4 | G1 | 480 | 3 x (3x95) | 3 x (3x150) | [20 empty] | x | [9 empty] | 3 | [26 empty] | 3 | [30 empty] | x | [11 empty] | x |  |  |  | x | [5 empty] | 1 | [37 empty] | x |  |  |  |  | x | 1 | [12 empty] | x
ACQ810-04-570A-4 | G1 | 570 | 3 x (3x120) | 3 x (3x185) | [20 empty] | x | [11 empty] | 3 | [25 empty] | 3 | [29 empty] | x | [11 empty] | x |  |  |  | x | [5 empty] | 1 | [37 empty] | x |  |  |  |  | x | 1 | [12 empty] | x
ACQ810-04-634A-4 | G1 | 634 | 3 x (3x150) | 3 x (3x240) | [20 empty] | x | [11 empty] | 3 | [25 empty] | 3 | [29 empty] | x | [11 empty] | x |  |  |  | x | [7 empty] | 1 | [35 empty] | x |  |  |  |  | x | 1 | [12 empty] | x
ACQ810-04-700A-4 | G2 | 700 | 3 x (3x185) | 4 x (3x185) | [20 empty] | x | [13 empty] | 3 | [23 empty] | 3 | [29 empty] | x | [11 empty] | x |  |  |  | x | [8 empty] | 1 | [34 empty] | x |  |  |  |  | x | 1 | [12 empty] | x
ACQ810-04-785A-4 | G2 | 785 | 3 x (3x240) | 4 x (3x240) | [20 empty] | x | [14 empty] | 3 | [23 empty] | 3 | [28 empty] | x | [11 empty] | x |  |  |  | x | [8 empty] | 1 | [34 empty] | x |  |  |  |  | x |  | 1 | [11 empty] | x
ACQ810-04-857A-4 | G2 | 857 | 3 x (3x240) | 4 x (3x240) | [20 empty] | x | [14 empty] | 3 | [24 empty] | 3 | [27 empty] | x | [11 empty] | x |  |  |  | x | [8 empty] | 1 | [34 empty] | x |  |  |  |  | x |  | 1 | [11 empty] | x
OESA not known, there fore type code open for R6 fuses
OESA not known, there fore type code open for R6 fuses
OESA not known, there fore same type code open
OESA not known, there fore same type code open
OESA not known, there fore type code open for R6 fuses
OESA not known, there fore same type code open
OESA not known, there fore same type code open
OESA not known, there fore same type code open
OESA not known, there fore same type code open
OESA not known, there fore same type code open
OESA not known, there fore same type code open

## ACS880-01_04
|  |  |  | Main Cable |  | Main Fuses (gG) | [34 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [26 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [33 empty] | Main Fuses (UL) | [27 empty] | Miniature circuit breaker | [35 empty] | Mains Switch for gG fuse | [7 empty] | Mains Switch | [9 empty] | Mains Switch UL | [9 empty] | Main Contactor | [13 empty] | Output Chokes (du/dt filters) | [15 empty] | Braking Resistor | [9 empty] | Residual Current Device |  |  | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [34 empty] | aR Fuses(see footnotes) | [60 empty] | UL-class Fuses | [27 empty] | Miniature circuit breaker | [35 empty] | Switch Fuse | [7 empty] | Switch | [9 empty] | Switch UL | [9 empty] | Contactor | [13 empty] | du/dt filters | [15 empty] | Braking Resistor | [9 empty] | Residual Current Device |  |  | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | L-class | L-class | L-class | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | RCCB F 200 series | RCCB F 200 series | T4 series | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter
|  | I1N | I2cont.max |  |  | ABB: OFAF000H4 4A, 500V, 53A2s | ABB: OFAF000H6 6A, 500V, 110A2s | ABB: OFAF000H10 10A, 500V, 360A2s | ABB: OFAF000H16 16A, 500V, 740A2s | ABB: OFAF000H25 25A, 500V, 2,5kA2s | ABB: OFAF000H32 32A, 500V, 4,5kA2s | ABB: OFAF000H40 40A, 500V, 7,7A2s | ABB: OFAF000H50 50A, 500V, 16kA2s | ABB: OFAF000H63 63A, 500V, 20,1kA2s | ABB: OFAF000H80 80A, 500V, 37,5kA2s | ABB: OFAF000H100 100A, 500V, 65kASs | ABB: OFAF00H125 125A, 500V, 100kA2s | ABB: OFAF00H160 160A, 500V, 170kA2s | ABB: OFAF0H200 200A, 500V, 300kA2s | ABB: OFAF0H250 250A, 500V, 600kA2s | ABB: OFAF1H315 315A, 500V, 710kA2s | ABB: OFAF1H355 355A, 500V, 920kA2s | ABB: OFAF2H400 400A, 500V, 1000kA2s | ABB: OFAF2H425 425A, 500V, 1300kA2s | ABB: OFAF2H500 500A, 500V, 2000kA2s | ABB: OFAF3H630 630A, 500V, 2800kA2s | ABB: OFAA000GG16 16A, 690V, 1,2kA2s | ABB: OFAA000GG20 20A, 690V, 2,4kA2s | ABB: OFAA000GG25 25A, 690V, 4kA2s | ABB: OFAA000GG35 35A, 690V, 12kA2s | ABB: OFAA000GG50 50A, 690V, 24kA2s | ABB: OFAA000GG63 63A, 690V, 30kA2s | ABB: OFAA0GG80 80A, 690V, 51kA2s | ABB: OFAA0GG100 100A, 690V, 95kA2s | ABB: OFAA1GG160 160A, 690V, 240kA2s | ABB: OFAA1GG200 200A, 690V, 350kA2s | ABB: OFAA1GG250 250A, 690V, 700kA2s | ABB: OFAA2GG315 315A, 690V, 850kA2s | ABB: OFAA3GG400 400A, 690V, 1300kA2s | gG fuse is too slow for this drive | Bussmann: 170M1559 16A, 690V, 48A2s | Bussmann: 170M1560 20A, 690V, 78A2s | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1562 32A, 690V, 270A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1564 50A, 690V, 770A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2550A2s | Bussmann: 170M1567 100A, 690V, 4650A2s | Bussmann: 170M1568 125A, 690V, 8500A2s | Bussmann: 170M1569 160A, 690V, 16kA2s | Bussmann: 170M3815 200A, 690V, 15kA2s | Bussmann: 170M3816 250A, 690V, 28500A2s | Bussmann: 170M3817 315A, 690V, 46500A2s | Bussmann: 170M5808 400A, 690V, 74kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 145kA2s | Bussmann: 170M5811 550A, 690V, 190kA2s | Bussmann: 170M5812 630A, 690V, 275kA2s | Bussmann: 170M6811D 700A, 690V, 320 kA2s | Bussmann: 170M6812D 800A, 690V, 490 kA2s | Bussmann: 170M6814D 1000A, 690V, 985 kA2s | Bussmann: 170M6892D 1100A, 690V, 1400 kA2s | Bussmann: 170M8554D 1250A, 690V, 2150 kA2s | Bussmann: 170M8555D 1400A, 690V,2700 kA2s | Bussmann: 170M8556D 1500A, 690V,3350 kA2s | Bussmann: 170M8557D 1600A, 690V,4150 kA2s | Bussmann: 170M1309 16A, 690V, 0,048 kA2s | Bussmann: 170M1310 20A, 690V, 0,078 kA2s | Bussmann: 170M1311 25A, 690V, 0,130 kA2s | Bussmann: 170M1312 32A, 690V, 0,27 kA2s | Bussmann: 170M1313 40A, 690V, 0,46 kA2s | Bussmann: 170M1314 50A, 690V, 0,77 kA2s | Bussmann: 170M1315 63A, 690V, 1,45 kA2s | Bussmann: 170M1316 80A, 690V, 2,55 kA2s | Bussmann: 170M1417 100A, 690V, 4,65 kA2s | Bussmann: 170M1318 125A, 690V, 8,5 kA2s | Bussmann: 170M1319 160A, 690V, 16 kA2s | Bussmann: 170M3013 125A, 690V, 7,5 kA2s | Bussmann: 170M3014 160A, 690V, 8,5 kA2s | Bussmann: 170M3015 200A, 690V, 15 kA2s | Bussmann: 170M3016 250A, 690V, 28,5 kA2s | Bussmann: 170M3017 315A, 690V, 46,5 kA2s | Bussmann: 170M3018 350A, 690V, 68,5 kA2s | Bussmann: 170M3019 400A, 690V, 105 kA2s | Bussmann: 170M5008 400A, 690V, 74 kA2s | Bussmann: 170M5009 450A, 690V, 105 kA2s | Bussmann: 170M5010 500A, 690V, 145 kA2s | Bussmann: 170M5011 550A, 690V, 190 kA2s | Bussmann: 170M5012 630A, 690V, 275 kA2s | Bussmann: 170M5013 700A, 690V, 405 kA2s | Bussmann: 170M6010 630A, 690V, 210 kA2s | Bussmann: 170M6011 700A, 690V, 300 kA2s | Bussmann: 170M6012 800A, 690V, 465 kA2s | Bussmann: 170M6013 900A, 690V, 670 kA2s | Bussmann: 170M6014 1000A, 690V, 945 kA2s | Bussmann: 170M6015 1100A, 690V, 1300 kA2s | Bussmann: 170M6016 1250A, 690V, 1950 kA2s | Bussmann: 170M6017 1400A, 690V, 2450 kA2s | Bussmann: 170M6018 1500A, 690V, 3100 kA2s | Bussmann: 170M6269 1600A, 690V, 3900 kA2s | Bussmann: JJS-3 3A, 600V | Bussmann: JJS-6 6A, 600V | Bussmann: JJS-10 10A, 600V | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-30 30A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-100 100A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-125 125A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-250 250A, 600V | Bussmann: JJS-300 300A, 600V | Bussmann: JJS-350 350A, 600V | Bussmann: JJS-400 400A, 600V | Bussmann: JJS-500 500A, 600V | Bussmann: JJS-600 600A, 600V | Ferraz: A4BY800 800A, 600V | Ferraz: A4BY900 900A, 600V | Ferraz: A4BY1000 1000A, 600V | ABB: S 203 M/P-B/C 6 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 10 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 13 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 16 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 20 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 25 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 32 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 50 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 63 (prospective SC current 5kA) | ABB: S 803 S-B/C 6 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 10 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 13 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 20 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 25 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 32 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 50 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 63 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 75 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 80 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 125 (prospective SC current 10kA, >500V 3kA) | No miniature breaker for this drive. Select molded case breaker. | ABB: 1SDA067915R1 (XT2 L 160 Ekip LS/I In=25 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067916R1 (XT2 L 160 Ekip LS/I In=63 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067917R1 (XT2 L 160 Ekip LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067918R1 (XT2 L 160 Ekip LS/I In=160 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA068555R1 (XT4 L 250 Ekip LS/I In=250 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 20kA | ABB: 1SDA054069R1 (T4 L 250 PR221DS-LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054070R1 (T4 L 250 PR221DS-LS/I In=160 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054071R1 (T4 L 250 PR221DS-LS/I In=250 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054141R1 (T4 L 320 PR221DS-LS/I In=320 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054365R1 (T5 L 400 PR221DS-LS/I In=400 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054420R1 (T5 L 630 PR221DS-LS/I In=630 3p F F)500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054412R1 (T5H 630 PR221DS-LS/I In=630 3p F F) | ABB: 1SDA069428R1 (T6V 800 PR221DS-LS/I In=800 3p F F) | ABB: 1SDA062770R1 (T7H 1000 PR231/P LS/I In=1000A 3p F F) | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OS400D12_ (1000V, 400A, DIN 0-2) | ABB: OS630D12_ (1000V, 630A, DIN 3) |  | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT1000E_ (1000V, 1000A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) | ABB: OT1200U_ (1000V, 1200A) | ABB: AF09-30-22-13 (25A,1000V 100-250V/50-60Hz) | ABB: AF12-30-22-13 (28A,1000V 100-250V/50-60Hz) | ABB: AF26-30-22-13 (45A,1000V 100-250V/50-60Hz) | ABB: AF30-30-22-13 (50A,1000V 100-250V/50-60Hz) | ABB: AF50-30-22-70 (100A,1000V 100-250V/50-60Hz) | ABB: AF63-30-22-70 (115A,1000V 100-250V/50-60Hz) | ABB: AF75-30-22-70 (125A,1000V 100-250V/50-60Hz) | ABB: AF95-30-22-70 (145A,1000V 100-250V/50-60Hz) | ABB: AF110-30-22-70 (160A,1000V 100-250V/50-60Hz) | ABB: AF145-30-22-70 (250A,1000V 100-250V/50-60Hz) | ABB: AF185-30-22-70 (275A,1000V 100-250V/50-60Hz) | ABB: AF210-30-22-70 (350A,1000V 100-250V/50-60Hz) | ABB: AF260-30-22-70 (400A,1000V 100-250V/50-60Hz) | ABB: AF300-30-22-70 (500A,1000V 100-250V/50-60Hz) | ABB Drives: NOCH0016-60 | ABB Drives: NOCH0030-60 | ABB Drives: NOCH0070-60 | ABB Drives: NOCH0120-60 | ABB Drives: FOCH0260-70 | ABB Drives: FOCH0320-50 | ABB Drives: FOCH0610-70 | ABB Drives: FOCH0875-70 | ABB Drives: NOCH0016-62 | ABB Drives: NOCH0030-62 | ABB Drives: NOCH0070-62 | ABB Drives: NOCH0120-62 | ABB Drives: NOCH0016-65 | ABB Drives: NOCH0030-65 | ABB Drives: NOCH0070-65 | ABB Drives: NOCH0120-65 | ABB Drives: JBR-01 | ABB Drives: JBR-03 | ABB Drives: SACE08RE44 | ABB Drives: SACE15RE22 | ABB Drives: SACE15RE13 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR80F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | F204 B-63/0.3 | F204 B-125/0.3 | T4 250 A | TDK: B84143V0004R229 | TDK: B84143V0006R229 | TDK: B84143V0010R230 | TDK: B84143V0011R229 | TDK: B84143V0016R229 | TDK: B84143V0018R230 | TDK: B84143V0025R229 | TDK: B84143V0026R230 | TDK: B84143V0033R229 | TDK: B84143V0040R230 | TDK: B84143V0050R229 | TDK: B84143V0056R230 | TDK: B84143V0066R229 | TDK: B84143V0075R229 | TDK: B84143V0092R230 | TDK: B84143V0095R229 | TDK: B84143V0130R230 | TDK: B84143V0130S230 | TDK: B84143V0162S229 | TDK: B84143V0207S230 | TDK: B84143V0230S229 | TDK: B84143V0390S229 | NSIN485-6 | NSIN900-6
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/117 | 230/118
[5 empty] | Part number -> | [34 empty] | Select aR Fuses | [61 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [26 empty] | *) Alternative option | *) Alternative option | *) Alternative option | [15 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C |  |  |  | 3 filters included in the kit | [12 empty] | Connected in series |  |  |  |  | (with code +D150) | (with code +D150) | (with code +D150) | (with code +D150) Connected in parallel | (with code +D150)
UN = 230 V (208, 220, 230, 240 V)
ACS880-01-04A6-2 | R1 | 4.6 | 4.6 |  |  |  | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [25 empty] | 1 | [33 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [29 empty] | 2 | [9 empty] | 1
ACS880-01-06A6-2 | R1 | 6.6 | 6.6 |  |  |  |  | 3 | [32 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [25 empty] | 1 | [33 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [29 empty] | 2 | [9 empty] | 1
ACS880-01-07A5-2 | R1 | 7.5 | 7.5 | [5 empty] | 3 | [31 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [27 empty] | 1 | [31 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [30 empty] | 1 | [8 empty] | 1
ACS880-01-10A6-2 | R1 | 10.6 | 10.6 | [5 empty] | 3 | [32 empty] | 3 | [25 empty] | 3 | [37 empty] | 3 | [26 empty] | 1 | [31 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [30 empty] | 1 | [8 empty] | 1
ACS880-01-16A8-2 | R2 | 16.8 | 16.8 | [6 empty] | 3 | [32 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [26 empty] | 1 | [30 empty] | x | 1 | [7 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [32 empty] | 1 | [6 empty] | 1
ACS880-01-24A3-2 | R2 | 24.3 | 24.3 | [8 empty] | 3 | [32 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [25 empty] | 1 | [28 empty] | x |  | 1 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [32 empty] | 1 | [6 empty] | 1
ACS880-01-031A-2 | R3 | 31 | 31 | [9 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [25 empty] | 1 | [27 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [31 empty] | 1 | [5 empty] | 1
ACS880-01-046A-2 | R4 | 46 | 46 | [10 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [33 empty] | 1 | [17 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [30 empty] | 1 | [5 empty] | 1
ACS880-01-061A-2 | R4 | 61 | 61 | [11 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [32 empty] | 1 | [16 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [29 empty] | 1 | [6 empty] | 1
ACS880-01-075A-2 | R5 | 75 | 75 | [12 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [31 empty] | 1 |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [36 empty] | 1
ACS880-01-087A-2 | R5 | 87 | 87 | [13 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [31 empty] | 1 |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [9 empty] | 1 | [36 empty] | 1
ACS880-01-115A-2 | R6 | 115 | 115 | [14 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [31 empty] | x |  |  |  | 1 | [14 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-01-145A-2 | R6 | 145 | 145 | [15 empty] | 3 | [34 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [30 empty] | x |  |  |  |  | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-01-170A-2 | R7 | 170 | 170 | [16 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [28 empty] | x |  |  |  |  | 1 | [14 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [12 empty] | 1
ACS880-01-206A-2 | R7 | 206 | 206 | [17 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [27 empty] | x | [8 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [12 empty] | 1
ACS880-01-274A-2 | R8 | 274 | 274 | [19 empty] | 3 | [33 empty] | 3 | [27 empty] | 3 | [64 empty] | x | [20 empty] | 1 | [8 empty] | 1
UN = 400 V (380, 400, 415 V)
ACS880-01-02A4-3 | R1 | 2.4 | 2.4 |  |  | 3 | [36 empty] | 3 | [26 empty] | 3 | [31 empty] | 3 | [27 empty] | 1 | [34 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  | 1
ACS880-01-03A3-3 | R1 | 3.3 | 3.3 |  |  |  | 3 | [35 empty] | 3 | [26 empty] | 3 | [32 empty] | 3 | [26 empty] | 1 | [34 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  | 1
ACS880-01-04A0-3 | R1 | 4 | 4 |  |  |  | 3 | [35 empty] | 3 | [26 empty] | 3 | [32 empty] | 3 | [26 empty] | 1 | [34 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  | 1
ACS880-01-05A6-3 | R1 | 5.6 | 5.6 |  |  |  |  | 3 | [34 empty] | 3 | [26 empty] | 3 | [33 empty] | 3 | [26 empty] | 1 | [33 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  |  | 1
ACS880-01-07A2-3 | R1 | 8 | 7.2 |  |  |  |  | 3 | [34 empty] | 3 | [26 empty] | 3 | [33 empty] | 3 | [27 empty] | 1 | [32 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [5 empty] | 1
ACS880-01-09A4-3 | R1 | 10 | 9.4 | [5 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [26 empty] | 1 | [32 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [5 empty] | 1
ACS880-01-12A6-3 | R1 | 12.9 | 12.6 | [5 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [35 empty] | 3 | [27 empty] | 1 | [30 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [6 empty] | 1
ACS880-01-017A-3 | R2 | 17 | 17 | [6 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [27 empty] | 1 | [29 empty] | x | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | 1 | [8 empty] | 1
ACS880-01-025A-3 | R2 | 25 | 25 | [7 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [26 empty] | 1 | [28 empty] | x |  | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | 1 | [8 empty] | 1
ACS880-01-032A-3 | R3 | 32 | 32 | [8 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [35 empty] | 3 | [26 empty] | 1 | [27 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | 1 | [10 empty] | 1
ACS880-01-038A-3 | R3 | 38 | 38 | [9 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [26 empty] | 1 | [26 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | 1 | [12 empty] | 1
ACS880-01-045A-3 | R4 | 45 | 45 | [10 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [33 empty] | 1 | [18 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 1 | [12 empty] | 1
ACS880-01-061A-3 | R4 | 61 | 61 | [11 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [33 empty] | 1 | [17 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [6 empty] | 1 | [13 empty] | 1
ACS880-01-072A-3 | R5 | 72 | 72 | [12 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [34 empty] | 1 |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 1 | [14 empty] | 1
ACS880-01-087A-3 | R5 | 87 | 87 | [12 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [32 empty] | 1 |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 1 | [16 empty] | 1
ACS880-01-105A-3 | R6 | 105 | 105 | [13 empty] | 3 | [36 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [31 empty] | x |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [5 empty] | 1 | [16 empty] | 1
ACS880-01-145A-3 | R6 | 145 | 145 | [14 empty] | 3 | [35 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [30 empty] | x |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [9 empty] | 1 | [17 empty] | 1 | [5 empty] | 1 | [18 empty] | 1
ACS880-01-169A-3 | R7 | 169 | 169 | [16 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [29 empty] | x |  |  |  |  | 1 | [14 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 |  |  |  |  | 1 | [18 empty] | 1
ACS880-01-206A-3 | R7 | 206 | 206 | [17 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [27 empty] | x | [8 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [25 empty] | 1
ACS880-01-246A-3 | R8 | 246 | 246 | [18 empty] | 3 | [36 empty] | 3 | [27 empty] | 3 | [35 empty] | 3 | [26 empty] | x | [9 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [20 empty] | 1 | [23 empty] | 1
ACS880-01-293A-3 | R8 | 293 | 293 | [20 empty] | 3 | [36 empty] | 3 | [26 empty] | 3 | [35 empty] | 3 | [25 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [14 empty] | 1 | [6 empty] | 1 | [20 empty] | 1 | [24 empty] | 1
ACS880-01-363A-3 | R9 | 363 | 363 | [21 empty] | 3 | [36 empty] | 3 | [27 empty] | 3 | [34 empty] | 3 | [24 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [14 empty] | 1 | [6 empty] | 1 | [18 empty] | 2 | [25 empty] | 1
ACS880-01-430A-3 | R9 | 430 | 430 | [22 empty] | 3 | [37 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [23 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [5 empty] | 1 | [18 empty] | 2 | [25 empty] | 1
ACS880-04-505A-3 | R10 | 505 | 505 | [36 empty] | x | [26 empty] | 3 | [26 empty] | 3 | [31 empty] | 3 | [23 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 2 | [27 empty] | 1
ACS880-04-585A-3 | R10 | 585 | 585 | [36 empty] | x | [26 empty] | 3 | [28 empty] | 3 | [30 empty] | 3 | [22 empty] | x | [12 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [18 empty] | 2 | [26 empty] | 1
ACS880-04-650A-3 | R10 | 650 | 650 | [36 empty] | x | [26 empty] | 3 | [28 empty] | 3 | [30 empty] | 3 | [22 empty] | x | [12 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [21 empty] | 1 | [18 empty] | 2 | [26 empty] | 1
ACS880-04-725A-3 | R11 | 725 | 725 | [36 empty] | x | [57 empty] | 3 | [28 empty] | 3 | [22 empty] | x | [13 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 3 | [26 empty] | 1
ACS880-04-820A-3 | R11 | 820 | 820 | [36 empty] | x | [60 empty] | 3 | [26 empty] | 3 | [21 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [21 empty] | 1 | [17 empty] | 3 | [26 empty] | 1
ACS880-04-880A-3 | R11 | 880 | 880 | [36 empty] | x | [60 empty] | 3 | [27 empty] | 3 | [20 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [21 empty] | 1 | [17 empty] | 3 | [26 empty] | 1
UN = 500 V (440, 460, 480 and 500 V)
ACS880-01-02A1-5 | R1 | 2.1 | 2.1 |  |  | 3 | [36 empty] | 3 | [26 empty] | 3 | [31 empty] | 3 | [36 empty] | 1 | [25 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  | 1
ACS880-01-03A0-5 | R1 | 3 | 3 |  |  |  | 3 | [35 empty] | 3 | [26 empty] | 3 | [32 empty] | 3 | [35 empty] | 1 | [25 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  | 1
ACS880-01-03A4-5 | R1 | 3.4 | 3.4 |  |  |  | 3 | [35 empty] | 3 | [26 empty] | 3 | [32 empty] | 3 | [35 empty] | 1 | [25 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  | 1
ACS880-01-04A8-5 | R1 | 4.8 | 4.8 |  |  |  |  | 3 | [34 empty] | 3 | [26 empty] | 3 | [33 empty] | 3 | [35 empty] | 1 | [24 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  |  | 1
ACS880-01-05A2-5 | R1 | 5.2 | 5.2 |  |  |  |  | 3 | [34 empty] | 3 | [26 empty] | 3 | [33 empty] | 3 | [36 empty] | 1 | [23 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 |  |  |  | 1
ACS880-01-07A6-5 | R1 | 7.6 | 7.6 | [5 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [35 empty] | 1 | [23 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [5 empty] | 1
ACS880-01-11A0-5 | R1 | 11 | 11 | [5 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [35 empty] | 3 | [35 empty] | 1 | [22 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [5 empty] | 1
ACS880-01-014A-5 | R2 | 14 | 14 | [6 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [35 empty] | 1 | [21 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | 1 | [6 empty] | 1
ACS880-01-021A-5 | R2 | 21 | 21 | [7 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [34 empty] | 1 | [20 empty] | x | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | 1 | [8 empty] | 1
ACS880-01-027A-5 | R3 | 27 | 27 | [8 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [35 empty] | 3 | [34 empty] | 1 | [19 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | 1 | [10 empty] | 1
ACS880-01-034A-5 | R3 | 34 | 34 | [9 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [34 empty] | 1 | [18 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | 1 | [12 empty] | 1
ACS880-01-040A-5 | R4 | 40 | 40 | [10 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [33 empty] | 1 | [18 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 1 | [12 empty] | 1
ACS880-01-052A-5 | R4 | 52 | 52 | [11 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [33 empty] | 1 | [17 empty] | x |  |  | 1 | [7 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [6 empty] | 1 | [13 empty] | 1
ACS880-01-065A-5 | R5 | 65 | 65 | [12 empty] | 3 | [33 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [34 empty] | 1 |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 1 | [13 empty] | 1
ACS880-01-077A-5 | R5 | 77 | 77 | [12 empty] | 3 | [34 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [32 empty] | 1 |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 1 | [14 empty] | 1
ACS880-01-096A-5 | R6 | 96 | 96 | [13 empty] | 3 | [35 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [31 empty] | x |  |  |  |  | 1 | [12 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [5 empty] | 1 | [17 empty] | 1
ACS880-01-124A-5 | R6 | 124 | 124 | [14 empty] | 3 | [35 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [30 empty] | x |  |  |  |  | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 | [17 empty] | 1 | [5 empty] | 1 | [17 empty] | 1
ACS880-01-156A-5 | R7 | 156 | 156 | [16 empty] | 3 | [34 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [29 empty] | x |  |  |  |  | 1 | [14 empty] | 1 | [7 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 | [9 empty] | 1 | [18 empty] | 1 |  |  |  |  | 1 | [18 empty] | 1
ACS880-01-180A-5 | R7 | 180 | 180 | [17 empty] | 3 | [35 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [27 empty] | x | [8 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [23 empty] | 1
ACS880-01-240A-5 | R8 | 240 | 240 | [18 empty] | 3 | [35 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [26 empty] | x | [10 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [20 empty] | 1 | [23 empty] | 1
ACS880-01-260A-5 | R8 | 260 | 260 | [19 empty] | 3 | [37 empty] | 3 | [25 empty] | 3 | [36 empty] | 3 | [25 empty] | x | [10 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 | [20 empty] | 1 | [23 empty] | 1
ACS880-01-302A-5 | R9 | 302 | 302 | [21 empty] | 3 | [36 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [25 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [19 empty] | 1
ACS880-01-361A-5 | R9 | 361 | 361 | [22 empty] | 3 | [35 empty] | 3 | [27 empty] | 3 | [34 empty] | 3 | [24 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [14 empty] | 1 | [6 empty] | 1 | [19 empty] | 1 | [24 empty] | 1
ACS880-01-414A-5 | R9 | 414 | 414 | [22 empty] | 3 | [37 empty] | 3 | [26 empty] | 3 | [34 empty] | 3 | [23 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [5 empty] | 1 | [19 empty] | 1 | [24 empty] | 1
ACS880-04-460A-5 | R10 | 460 | 460 | [36 empty] | x | [23 empty] | 3 | [27 empty] | 3 | [32 empty] | 3 | [24 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 2 | [26 empty] | 1
ACS880-04-503A-5 | R10 | 505 | 503 | [36 empty] | x | [23 empty] | 3 | [29 empty] | 3 | [31 empty] | 3 | [23 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 2 | [27 empty] | 1
ACS880-04-583A-5 | R10 | 585 | 583 | [36 empty] | x | [23 empty] | 3 | [31 empty] | 3 | [30 empty] | 3 | [22 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [18 empty] | 2 | [26 empty] | 1
ACS880-04-635A-5 | R10 | 650 | 635 | [36 empty] | x | [26 empty] | 3 | [28 empty] | 3 | [30 empty] | 3 | [22 empty] | x | [12 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [21 empty] | 1 | [18 empty] | 2 | [26 empty] | 1
ACS880-04-715A-5 | R11 | 725 | 715 | [36 empty] | x | [57 empty] | 3 | [28 empty] | 3 | [22 empty] | x | [13 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 3 | [26 empty] | 1
ACS880-04-820A-5 | R11 | 820 | 820 | [36 empty] | x | [60 empty] | 3 | [26 empty] | 3 | [21 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [21 empty] | 1 | [17 empty] | 3 | [26 empty] | 1
ACS880-04-880A-5 | R11 | 880 | 880 | [36 empty] | x | [60 empty] | 3 | [27 empty] | 3 | [20 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [21 empty] | 1 | [17 empty] | 3 | [26 empty] | 1
UN = 690 V (525, 575, 600, 660, and 690 V)
ACS880-01-07A4-7 | R3 | 7.4 | 7.4 | [23 empty] | 3 | [13 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [45 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [31 empty] | 1 | [12 empty] | 1
ACS880-01-09A9-7 | R3 | 9.9 | 9.9 | [24 empty] | 3 | [13 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [44 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [31 empty] | 1 | [12 empty] | 1
ACS880-01-14A3-7 | R3 | 14.3 | 14.3 | [25 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [42 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [31 empty] | 1 | [15 empty] | 1
ACS880-01-019A-7 | R3 | 19 | 19 | [26 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [41 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [31 empty] | 1 | [15 empty] | 1
ACS880-01-023A-7 | R3 | 23 | 23 | [27 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [40 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [31 empty] | 1 | [17 empty] | 1
ACS880-01-027A-7 | R3 | 27 | 27 | [27 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [40 empty] | 1 | [14 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [30 empty] | 1 | [17 empty] | 1
ACS880-01-07A3-7 | R5 | 7.3 | 7.3 | [23 empty] | 3 | [13 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [35 empty] | 1 *) | [9 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  |  |  | 1
ACS880-01-09A8-7 | R5 | 9.8 | 9.8 | [24 empty] | 3 | [13 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [35 empty] | 1 *) | [8 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 2 | [9 empty] | 1 |  |  |  |  | 1
ACS880-01-14A2-7 | R5 | 14.2 | 14.2 | [25 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [34 empty] | 1 *) | [7 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | 1 | [7 empty] | 1
ACS880-01-018A-7 | R5 | 18 | 18 | [26 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [33 empty] | 1 *) | [7 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [6 empty] | 1 | [7 empty] | 1
ACS880-01-022A-7 | R5 | 22 | 22 | [27 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [33 empty] | 1 *) | [6 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [6 empty] | 1 | [9 empty] | 1
ACS880-01-026A-7 | R5 | 26 | 26 | [27 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [34 empty] | 1 *) | [5 empty] | 1 | [14 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [6 empty] | 1 | [9 empty] | 1
ACS880-01-035A-7 | R5 | 35 | 35 | [28 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [33 empty] | 1 *) | [5 empty] | 1 | [14 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | 1 | [11 empty] | 1
ACS880-01-042A-7 | R5 | 42 | 42 | [29 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [34 empty] | 1 *) |  |  |  |  | 1 |  |  | 1 *) | [13 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | 1 | [10 empty] | 1
ACS880-01-049A-7 | R5 | 49 | 49 | [29 empty] | 3 | [14 empty] | 3 | [26 empty] | 3 | [37 empty] | 3 | [34 empty] | 1 *) |  |  |  |  | 1 |  |  | 1 *) | [13 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [7 empty] | 1 | [12 empty] | 1
ACS880-01-061A-7 | R6 | 61 | 61 | [30 empty] | 3 | [15 empty] | 3 | [26 empty] | 3 | [38 empty] | 3 | [32 empty] | 1 *) |  |  |  |  | 1 |  |  | 1 *) | [12 empty] | 1 | [6 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [6 empty] | 1 | [12 empty] | 1
ACS880-01-084A-7 | R6 | 84 | 84 | [31 empty] | 3 | [15 empty] | 3 | [26 empty] | 3 | [39 empty] | 3 | [30 empty] | 1 *) |  |  |  |  | 1 |  |  | 1 *) | [12 empty] | 1 | [6 empty] | 1 | [10 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [22 empty] | 1
ACS880-01-098A-7 | R7 | 98 | 98 | [31 empty] | 3 | [17 empty] | 3 | [27 empty] | 3 | [36 empty] | 3 | [31 empty] | x |  |  |  |  | 1 |  |  | 1 *) | [11 empty] | 1 | [6 empty] | 1 | [10 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [21 empty] | 1
ACS880-01-119A-7 | R7 | 119 | 119 | [32 empty] | 3 | [16 empty] | 3 | [27 empty] | 3 | [37 empty] | 3 | [30 empty] | x |  |  |  |  | 1 |  |  | 1 *) | [11 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [11 empty] | 1 | [16 empty] | 1 | [24 empty] | 1
ACS880-01-142A-7 | R8 | 142 | 142 | [33 empty] | 3 | [19 empty] | 3 | [24 empty] | 3 | [38 empty] | 3 | [28 empty] | x |  |  |  |  | 1 |  |  | 1 *) | [11 empty] | 1 | [7 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 | [10 empty] | 1 | [17 empty] | 1 | [23 empty] | 1
ACS880-01-174A-7 | R8 | 174 | 174 | [34 empty] | 3 | [18 empty] | 3 | [25 empty] | 3 | [38 empty] | 3 | [27 empty] | x | [8 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [17 empty] | 1 | [25 empty] | 1
ACS880-01-210A-7 | R9 | 210 | 210 | [35 empty] | 3 | [20 empty] | 3 | [25 empty] | 3 | [37 empty] | 3 | [25 empty] | x | [9 empty] | 1 | [11 empty] | 1 | [6 empty] | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [24 empty] | 1
ACS880-01-271A-7 | R9 | 271 | 271 | [35 empty] | 3 | [20 empty] | 3 | [26 empty] | 3 | [36 empty] | 3 | [25 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [13 empty] | 1 | [7 empty] | 1 | [18 empty] | 1 | [24 empty] | 1
ACS880-04-330A-7 | R10 | 330 | 330 | [36 empty] | x | [21 empty] | 3 | [30 empty] | 3 | [31 empty] | 3 | [24 empty] | x | [11 empty] | 1 | [17 empty] | 1 | [10 empty] | 1 | [22 empty] | 1 | [18 empty] | 1 | [25 empty] | 1
ACS880-04-370A-7 | R10 | 370 | 370 | [36 empty] | x | [21 empty] | 3 | [32 empty] | 3 | [29 empty] | 3 | [24 empty] | x | [11 empty] | 1 | [17 empty] | 1 | [10 empty] | 1 | [22 empty] | 1 | [18 empty] | 1 | [25 empty] | 1
ACS880-04-430A-7 | R10 | 430 | 430 | [36 empty] | x | [22 empty] | 3 | [32 empty] | 3 | [28 empty] | 3 | [24 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [18 empty] | 1 | [25 empty] | 1
ACS880-04-425A-7 | R11 | 425 | 425 | [36 empty] | x | [22 empty] | 3 | [32 empty] | 3 | [28 empty] | 3 | [24 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 2 | [26 empty] | 1
ACS880-04-470A-7 | R11 | 470 | 470 | [36 empty] | x | [23 empty] | 3 | [32 empty] | 3 | [28 empty] | 3 | [23 empty] | x | [11 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 2 | [26 empty] | 1
ACS880-04-522A-7 | R11 | 522 | 522 | [36 empty] | x | [24 empty] | 3 | [32 empty] | 3 | [27 empty] | 3 | [23 empty] | x | [12 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [17 empty] | 2 | [26 empty] | 1
ACS880-04-590A-7 | R11 | 590 | 590 | [36 empty] | x | [25 empty] | 3 | [32 empty] | 3 | [27 empty] | 3 | [22 empty] | x | [12 empty] | 1 | [17 empty] | 1 | [10 empty] | 1 | [21 empty] | 1 | [17 empty] | 2 | [27 empty] | 1
ACS880-04-650A-7 | R11 | 650 | 650 | [36 empty] | x | [59 empty] | 3 | [26 empty] | 3 | [22 empty] | x | [31 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [16 empty] | 2 | [27 empty] | 1
ACS880-04-721A-7 | R11 | 721 | 721 | [36 empty] | x | [59 empty] | 3 | [26 empty] | 3 | [22 empty] | x | [31 empty] | 1 | [9 empty] | 1 | [22 empty] | 1 | [16 empty] | 2 | [27 empty] | 1

## ACS880-11_14
[6 empty] | Main fuses (gG) | [12 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [22 empty] | Main Fuses (UL) | [13 empty] | Miniature circuit breaker |  | Moulded case circuit breaker |  | Mains Switch for gG fuse |  |  |  |  | Mains Switch | [8 empty] | Mains Switch UL | [8 empty] | Main contactor | Output Chokes (du/dt filters) | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [12 empty] | aR Fuses (see footnotes) | [22 empty] | UL-class Fuses | [13 empty] | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker |  | Switch Fuse |  |  |  |  | Switch | [8 empty] | Switch UL | [8 empty] | Contactor | du/dt filters | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | Braking Resistor | RCCB F 200 series | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter
|  | I1N | I2cont.max |  |  | ABB: OFAF000H16 16A, 500V, 700A2s | ABB: OFAF000H25 25A, 500V, 2.5kA2s | ABB: OFAF000H32 32A, 500V, 4.5kA2s | ABB: OFAF000H40 40A, 500V, 7.7kA2s | ABB: OFAF000H50 50A, 500V, 15.4kA2s | ABB: OFAF000H63 63A, 500V, 21.3kA2s | ABB: OFAF000H80 80A, 500V, 37kA2s | ABB: OFAF000H100 100A, 500V, 63.6kA2s | ABB: OFAF00H125 125A, 500V, 103kA2s | ABB: OFAF00H160 160A, 500V, 185kA2s | ABB: OFAF0H250 250A, 500V, 600kA2s | ABB: OFAF1H315 315A, 500V, 710kA2s | gG fuse is too slow for this drive | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2550A2s | Bussmann: 170M1567 100A, 690V, 4650A2s | Bussmann: 170M1568 125A, 690V, 8500A2s | Bussmann: 170M1569 160A, 690V, 16kA2s | Bussmann: 170M3817 315A, 690V, 46.5kA2s | Bussmann: 170M3816D 250A, 690V, 31kA2s | Bussmann: 170M3817D 315A, 690V, 52kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 145kA2s | Bussmann: 170M5818D 400A, 690V, 79kA2s | Bussmann: 170M5808D 400A, 690V, 79kA2s | Bussmann: 170M5810D 500A, 690V, 155kA2s | Bussmann: 170M6810D 630A, 690V, 220kA2s | Bussmann: 170M6811D 700A, 690V, 320kA2s | Bussmann: 170M6812D 800A, 690V, 490kA2s | Bussmann: 170M6814D 1000A, 690V, 985kA2s | Bussmann: 170M3816 250A, 690V, 28.5kA2s | Bussmann: 170M5808 400A, 690V, 74kA2s | Bussmann: 170M5810 500A, 690V, 155kA2s | Bussmann: 170M6411 700A, 690V, 300kA2s | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-300 300A, 600V | Not available yet | No miniature breaker for this drive. Select molded case breaker. | Not available yet | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) |  | ABB: NOCH0016-6X | ABB: NOCH0030-6X | ABB: NOCH0070-6X | ABB: NOCH0120-6X | ABB: FOCH0260-70 | ABB: FOCH0260-7X | ABB: FOCH0320-5x | ABB: FOCH-0610-70 |  |  | TDK: B84143V0011R229 | TDK: B84143V0016R229 | TDK: B84143V0025R229 | TDK: B84143V0033R229 | TDK: B84143V0050R229 | TDK: B84143V0066R229 | TDK: B84143V0075R229 | TDK: B84143V0095R229 | TDK: B84143V0130S230 | TDK: B84143V0162S229 | TDK: B84143V0230S229 | TDK: B84143V0390S229 | NSIN900-6 | TDK: B84143V0207S230 | NSIN485-6
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [12 empty] | Select aR Fuses | [23 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [9 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C
UN = 400 V (380, 400, 415 V)
ACS880-11-09A4-3 | R3 | 8 | 10 |  |  | 3 | [12 empty] | 3 | [22 empty] | 3 | [13 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-11-12A6-3 | R3 | 10 | 12.9 |  |  | 3 | [12 empty] | 3 | [23 empty] | 3 | [12 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-11-017A-3 | R3 | 14 | 17 |  |  |  | 3 | [12 empty] | 3 | [23 empty] | 3 | [11 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [9 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-11-025A-3 | R3 | 20 | 25 |  |  |  |  | 3 | [11 empty] | 3 | [24 empty] | 3 | [10 empty] | x |  | x |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-11-032A-3 | R6 | 27 | 32 | [5 empty] | 3 | [11 empty] | 3 | [24 empty] | 3 | [9 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-11-038A-3 | R6 | 33 | 38 | [6 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [8 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-11-045A-3 | R6 | 40 | 45 | [7 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [7 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-11-061A-3 | R6 | 51 | 61 | [8 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [6 empty] | x |  | x |  |  |  | 1 | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-11-072A-3 | R6 | 63 | 72 | [9 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [5 empty] | x |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-11-087A-3 | R6 | 76 | 87 | [9 empty] | 3 | [11 empty] | 3 | [25 empty] | 3 |  |  |  |  | x |  | x |  |  |  | 1 | [5 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [13 empty] | 1
ACS880-11-105A-3 | R8 | 88 | 105 | [10 empty] | 3 | [11 empty] | 3 | [25 empty] | 3 |  |  |  | x |  | x |  |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-11-145A-3 | R8 | 120 | 145 | [11 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 |  |  | x |  | x | [5 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-11-169A-3 | R8 | 144 | 169 | [12 empty] | 3 | [12 empty] | 3 | [24 empty] | 3 |  | x |  | x | [5 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [14 empty] | 1
ACS880-11-206A-3 | R8 | 176 | 206 | [13 empty] | 3 | [12 empty] | 3 | [24 empty] | 3 | x |  | x | [5 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [15 empty] | 1
ACS880-14-246A-3 | R11 | 212 | 246 | [14 empty] | x | [12 empty] | 3 | [24 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-293A-3 | R11 | 257 | 293 | [14 empty] | x | [14 empty] | 3 | [22 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [15 empty] | 1
ACS880-14-363A-3 | R11 | 321 | 363 | [14 empty] | x | [15 empty] | 3 | [21 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-442A-3 | R11 | 401 | 442 | [14 empty] | x | [16 empty] | 3 | [20 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-505A-3 | R11 | 401 | 505 | [14 empty] | x | [17 empty] | 3 | [19 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-14-585A-3 | R11 | 505 | 585 | [14 empty] | x | [18 empty] | 3 | [18 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-14-650A-3 | R11 | 569 | 650 | [14 empty] | x | [18 empty] | 3 | [18 empty] | x |  | x | [14 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
UN = 500 V (440, 460, 480 and 500 V)
ACS880-11-07A6-5 | R3 | 7 | 7.6 |  |  | 3 | [12 empty] | 3 | [22 empty] | 3 | [13 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-11-11A0-5 | R3 | 9 | 11 |  |  | 3 | [12 empty] | 3 | [23 empty] | 3 | [12 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-11-014A-5 | R3 | 12 | 14 |  |  |  | 3 | [12 empty] | 3 | [23 empty] | 3 | [11 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [9 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-11-021A-5 | R3 | 17 | 21 |  |  |  |  | 3 | [11 empty] | 3 | [24 empty] | 3 | [10 empty] | x |  | x |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-11-027A-5 | R6 | 24 | 27 | [5 empty] | 3 | [11 empty] | 3 | [24 empty] | 3 | [9 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-11-034A-5 | R6 | 29 | 34 | [6 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [8 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-11-040A-5 | R6 | 34 | 40 | [7 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [7 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-11-052A-5 | R6 | 44 | 52 | [8 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [6 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-11-065A-5 | R6 | 54 | 65 | [9 empty] | 3 | [10 empty] | 3 | [25 empty] | 3 | [5 empty] | x |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-11-077A-5 | R6 | 66 | 77 | [9 empty] | 3 | [11 empty] | 3 | [25 empty] | 3 |  |  |  |  | x |  | x |  |  |  | 1 | [5 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [12 empty] | 1
ACS880-11-101A-5 | R8 | 72 | 101 | [10 empty] | 3 | [23 empty] | 3 | [13 empty] | 3 |  |  |  | x |  | x |  |  |  | 1 | [6 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-11-124A-5 | R8 | 88 | 124 | [11 empty] | 3 | [10 empty] | 3 | [26 empty] | 3 |  |  | x |  | x |  |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [13 empty] | 1
ACS880-11-156A-5 | R8 | 120 | 156 | [12 empty] | 3 | [22 empty] | 3 | [14 empty] | 3 |  | x |  | x | [5 empty] | 1 |  |  |  |  | 1 | [10 empty] | 1 | [7 empty] | 1 | [14 empty] | 1
ACS880-11-180A-5 | R8 | 144 | 180 | [13 empty] | 3 | [22 empty] | 3 | [14 empty] | 3 | x |  | x | [5 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [14 empty] | 1
ACS880-14-240A-5 | R11 | 169 | 240 | [14 empty] | x | [9 empty] | 3 | [27 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-260A-5 | R11 | 205 | 260 | [14 empty] | x | [13 empty] | 3 | [23 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-302A-5 | R11 | 249 | 302 | [14 empty] | x | [14 empty] | 3 | [22 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-14-361A-5 | R11 | 257 | 361 | [14 empty] | x | [15 empty] | 3 | [21 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-414A-5 | R11 | 321 | 414 | [14 empty] | x | [16 empty] | 3 | [20 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-14-460A-5 | R11 | 404 | 460 | [14 empty] | x | [16 empty] | 3 | [20 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [15 empty] | 1
ACS880-14-503A-5 | R11 | 455 | 505 | [14 empty] | x | [17 empty] | 3 | [19 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
UN = 690 V (525, 575, 600, 660, and 690 V)
ACS880-14-142A-7 | R11 | 123 | 142 | [14 empty] | x | [8 empty] | 3 | [28 empty] | x |  | x | [10 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [12 empty] | 1
ACS880-14-174A-7 | R11 | 149 | 174 | [14 empty] | x | [9 empty] | 3 | [27 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [17 empty] | 1
ACS880-14-210A-7 | R11 | 186 | 210 | [14 empty] | x | [13 empty] | 3 | [23 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [17 empty] | 1
ACS880-14-271A-7 | R11 | 232 | 271 | [14 empty] | x | [14 empty] | 3 | [22 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [17 empty] | 1
ACS880-14-330A-7 | R11 | 293 | 330 | [14 empty] | x | [15 empty] | 3 | [21 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [16 empty] | 1
ACS880-14-370A-7 | R11 | 330 | 370 | [14 empty] | x | [16 empty] | 3 | [20 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [16 empty] | 1
ACS880-14-430A-7 | R11 | 375 | 430 | [14 empty] | x | [16 empty] | 3 | [20 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [16 empty] | 1

## ACS880-31_34
[6 empty] | Main fuses (gG) | [12 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [21 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [7 empty] | Main Fuses (UL) | [13 empty] | Miniature circuit breaker |  | Moulded case circuit breaker |  | Mains Switch for gG fuse |  |  |  |  | Mains Switch | [8 empty] | Mains Switch UL | [8 empty] | Main contactor | Output Chokes (du/dt filters) | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [12 empty] | aR Fuses (see footnotes) | [21 empty] | aR Fuses | [7 empty] | UL-class Fuses | [13 empty] | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker |  | Switch Fuse |  |  |  |  | Switch | [8 empty] | Switch UL | [8 empty] | Contactor | du/dt filters | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | Braking Resistor | RCCB F 200 series | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter | Sine Filter
|  | I1N | I2cont.max |  |  | ABB: OFAF000H16 16A, 500V, 700A2s | ABB: OFAF000H25 25A, 500V, 2.5kA2s | ABB: OFAF000H32 32A, 500V, 4.5kA2s | ABB: OFAF000H40 40A, 500V, 7.7kA2s | ABB: OFAF000H50 50A, 500V, 15.4kA2s | ABB: OFAF000H63 63A, 500V, 21.3kA2s | ABB: OFAF000H80 80A, 500V, 37kA2s | ABB: OFAF000H100 100A, 500V, 63.6kA2s | ABB: OFAF00H125 125A, 500V, 103kA2s | ABB: OFAF00H160 160A, 500V, 185kA2s | ABB: OFAF0H250 250A, 500V, 600kA2s | ABB: OFAF1H315 315A, 500V, 710kA2s | gG fuse is too slow for this drive | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2550A2s | Bussmann: 170M1567 100A, 690V, 4650A2s | Bussmann: 170M1568 125A, 690V, 8500A2s | Bussmann: 170M1569 160A, 690V, 16kA2s | Bussmann: 170M3817 315A, 690V, 46.5kA2s | Bussmann: 170M3816D 250A, 690V, 31kA2s | Bussmann: 170M3817D 315A, 690V, 52kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 145kA2s | Bussmann: 170M5818D 400A, 690V, 79kA2s | Bussmann: 170M5808D 400A, 690V, 79kA2s | Bussmann: 170M5810D 500A, 690V, 155kA2s | Bussmann: 170M6810D 630A, 690V, 220kA2s | Bussmann: 170M6811D 700A, 690V, 320kA2s | Bussmann: 170M6812D 800A, 690V, 490kA2s | Bussmann: 170M6814D 1000A, 690V, 985kA2s | Bussmann: 170M3816 250A, 690V, 28.5kA2s | Bussmann: 170M5808 400A, 690V, 74kA2s | Bussmann: 170M5810 500A, 690V, 155kA2s | Bussmann: 170M4409 250A, 690V, 21 kA2s | Bussmann: 170M4410 315A, 690V, 42 kA2s | Bussmann: 170M5408 400A, 690V, 74 kA2s | Bussmann: 170M5410 500A, 690V, 145 kA2s | Bussmann: 170M6410 630A, 690V, 210 kA2s | Bussmann: 170M6411 700A, 690V, 300 kA2s | Bussmann: 170M6412 800A, 690V, 465 kA2s | Bussmann: 170M6414 1000A, 690V, 945 kA2s | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-300 300A, 600V | Not available yet | No miniature breaker for this drive. Select molded case breaker. | Not available yet | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) |  | ABB: NOCH0016-6X | ABB: NOCH0030-6X | ABB: NOCH0070-6X | ABB: NOCH0120-6X | ABB: FOCH0260-70 | ABB: FOCH0260-7X | ABB: FOCH0320-5x | ABB: FOCH-0610-70 |  |  | TDK: B84143V0011R229 | TDK: B84143V0016R229 | TDK: B84143V0025R229 | TDK: B84143V0033R229 | TDK: B84143V0050R229 | TDK: B84143V0066R229 | TDK: B84143V0075R229 | TDK: B84143V0095R229 | TDK: B84143V0130S230 | TDK: B84143V0162S229 | TDK: B84143V0230S229 | TDK: B84143V0390S229 | NSIN900-6 | TDK: B84143V0207S230 | NSIN485-6
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [12 empty] | Select aR Fuses | [30 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [9 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C
UN = 400 V (380, 400, 415 V)
ACS880-31-09A4-3 | R3 | 8 | 10 |  |  | 3 | [12 empty] | 3 | [29 empty] | 3 | [13 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-31-12A6-3 | R3 | 10 | 12.9 |  |  | 3 | [12 empty] | 3 | [30 empty] | 3 | [12 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-31-017A-3 | R3 | 14 | 17 |  |  |  | 3 | [12 empty] | 3 | [30 empty] | 3 | [11 empty] | x |  | x |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-31-025A-3 | R3 | 20 | 25 |  |  |  |  | 3 | [11 empty] | 3 | [31 empty] | 3 | [10 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-31-032A-3 | R6 | 27 | 32 | [5 empty] | 3 | [11 empty] | 3 | [31 empty] | 3 | [9 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-31-038A-3 | R6 | 33 | 38 | [6 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [8 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-31-045A-3 | R6 | 40 | 45 | [7 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [7 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-31-061A-3 | R6 | 51 | 61 | [8 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [6 empty] | x |  | x |  |  |  | 1 | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-31-072A-3 | R6 | 63 | 72 | [9 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [5 empty] | x |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-31-087A-3 | R6 | 76 | 87 | [9 empty] | 3 | [11 empty] | 3 | [32 empty] | 3 |  |  |  |  | x |  | x |  |  |  | 1 | [5 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [13 empty] | 1
ACS880-31-105A-3 | R8 | 88 | 105 | [10 empty] | 3 | [11 empty] | 3 | [32 empty] | 3 |  |  |  | x |  | x |  |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-31-145A-3 | R8 | 120 | 145 | [11 empty] | 3 | [10 empty] | 3 | [33 empty] | 3 |  |  | x |  | x | [5 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-31-169A-3 | R8 | 144 | 169 | [12 empty] | 3 | [12 empty] | 3 | [31 empty] | 3 |  | x |  | x | [5 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [14 empty] | 1
ACS880-31-206A-3 | R8 | 176 | 206 | [13 empty] | 3 | [12 empty] | 3 | [31 empty] | 3 | x |  | x | [5 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [15 empty] | 1
ACS880-34-246A-3 | R11 | 212 | 246 | [14 empty] | x | [12 empty] | 3 | [11 empty] | 3 | [19 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-293A-3 | R11 | 257 | 293 | [14 empty] | x | [14 empty] | 3 | [10 empty] | 3 | [18 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [15 empty] | 1
ACS880-34-363A-3 | R11 | 321 | 363 | [14 empty] | x | [15 empty] | 3 | [10 empty] | 3 | [17 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-442A-3 | R11 | 401 | 442 | [14 empty] | x | [16 empty] | 3 | [10 empty] | 3 | [16 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-505A-3 | R11 | 401 | 505 | [14 empty] | x | [17 empty] | 3 | [10 empty] | 3 | [15 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-34-585A-3 | R11 | 505 | 585 | [14 empty] | x | [18 empty] | 3 | [10 empty] | 3 | [14 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-34-650A-3 | R11 | 569 | 650 | [14 empty] | x | [18 empty] | 3 | [10 empty] | 3 | [14 empty] | x |  | x | [14 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
UN = 500 V (440, 460, 480 and 500 V)
ACS880-31-07A6-5 | R3 | 7 | 7.6 |  |  | 3 | [12 empty] | 3 | [29 empty] | 3 | [13 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-31-11A0-5 | R3 | 9 | 11 |  |  | 3 | [12 empty] | 3 | [30 empty] | 3 | [12 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-31-014A-5 | R3 | 12 | 14 |  |  |  | 3 | [12 empty] | 3 | [30 empty] | 3 | [11 empty] | x |  | x |  | 1 |  |  |  |  | 1 | [9 empty] | 1 | [9 empty] | 1 | [9 empty] | 1
ACS880-31-021A-5 | R3 | 17 | 21 |  |  |  |  | 3 | [11 empty] | 3 | [31 empty] | 3 | [10 empty] | x |  | x |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-31-027A-5 | R6 | 24 | 27 | [5 empty] | 3 | [11 empty] | 3 | [31 empty] | 3 | [9 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACS880-31-034A-5 | R6 | 29 | 34 | [6 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [8 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-31-040A-5 | R6 | 34 | 40 | [7 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [7 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-31-052A-5 | R6 | 44 | 52 | [8 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [6 empty] | x |  | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACS880-31-065A-5 | R6 | 54 | 65 | [9 empty] | 3 | [10 empty] | 3 | [32 empty] | 3 | [5 empty] | x |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACS880-31-077A-5 | R6 | 66 | 77 | [9 empty] | 3 | [11 empty] | 3 | [32 empty] | 3 |  |  |  |  | x |  | x |  |  |  | 1 | [5 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [12 empty] | 1
ACS880-31-101A-5 | R8 | 72 | 101 | [10 empty] | 3 | [23 empty] | 3 | [20 empty] | 3 |  |  |  | x |  | x |  |  |  | 1 | [6 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-31-124A-5 | R8 | 88 | 124 | [11 empty] | 3 | [10 empty] | 3 | [33 empty] | 3 |  |  | x |  | x |  |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [13 empty] | 1
ACS880-31-156A-5 | R8 | 120 | 156 | [12 empty] | 3 | [22 empty] | 3 | [21 empty] | 3 |  | x |  | x | [5 empty] | 1 |  |  |  |  | 1 | [10 empty] | 1 | [7 empty] | 1 | [14 empty] | 1
ACS880-31-180A-5 | R8 | 144 | 180 | [13 empty] | 3 | [22 empty] | 3 | [21 empty] | 3 | x |  | x | [5 empty] | 1 | [5 empty] | 1 | [9 empty] | 1 | [7 empty] | 1 | [14 empty] | 1
ACS880-34-240A-5 | R11 | 169 | 240 | [14 empty] | x | [9 empty] | 3 | [13 empty] | 3 | [20 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-260A-5 | R11 | 205 | 260 | [14 empty] | x | [13 empty] | 3 | [10 empty] | 3 | [19 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-302A-5 | R11 | 249 | 302 | [14 empty] | x | [14 empty] | 3 | [10 empty] | 3 | [18 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
ACS880-34-361A-5 | R11 | 257 | 361 | [14 empty] | x | [15 empty] | 3 | [10 empty] | 3 | [17 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-414A-5 | R11 | 321 | 414 | [14 empty] | x | [16 empty] | 3 | [10 empty] | 3 | [16 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [14 empty] | 1
ACS880-34-460A-5 | R11 | 404 | 460 | [14 empty] | x | [16 empty] | 3 | [10 empty] | 3 | [16 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [15 empty] | 1
ACS880-34-503A-5 | R11 | 455 | 505 | [14 empty] | x | [17 empty] | 3 | [10 empty] | 3 | [15 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [14 empty] | 1
UN = 690 V (525, 575, 600, 660, and 690 V)
ACS880-34-142A-7 | R11 | 123 | 142 | [14 empty] | x | [8 empty] | 3 | [13 empty] | 3 | [21 empty] | x |  | x | [10 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [12 empty] | 1
ACS880-34-174A-7 | R11 | 149 | 174 | [14 empty] | x | [9 empty] | 3 | [13 empty] | 3 | [20 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [17 empty] | 1
ACS880-34-210A-7 | R11 | 186 | 210 | [14 empty] | x | [13 empty] | 3 | [10 empty] | 3 | [19 empty] | x |  | x | [11 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [17 empty] | 1
ACS880-34-271A-7 | R11 | 232 | 271 | [14 empty] | x | [14 empty] | 3 | [10 empty] | 3 | [18 empty] | x |  | x | [12 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [17 empty] | 1
ACS880-34-330A-7 | R11 | 293 | 330 | [14 empty] | x | [15 empty] | 3 | [10 empty] | 3 | [17 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [16 empty] | 1
ACS880-34-370A-7 | R11 | 330 | 370 | [14 empty] | x | [16 empty] | 3 | [10 empty] | 3 | [16 empty] | x |  | x | [12 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [16 empty] | 1
ACS880-34-430A-7 | R11 | 375 | 430 | [14 empty] | x | [16 empty] | 3 | [10 empty] | 3 | [16 empty] | x |  | x | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [16 empty] | 1

## ACS580-01_04
|  |  |  | Main Cable |  | Main Fuses (gG) | [34 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [33 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [18 empty] | Main Fuses (UL) | [27 empty] | Miniature circuit breaker | [23 empty] | Moulded Case Circuit Breaker | [15 empty] | Mains Switch for gG fuse | [7 empty] | Mains Switch | [9 empty] | Mains Switch UL | [9 empty] | Main Contactor | [18 empty] | Braking Resistor | [19 empty] | Output Chokes (du/dt filters) | [15 empty] | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [34 empty] | aR Fuses(see footnotes) | [33 empty] | aR Fuses | [18 empty] | UL-class Fuses | [27 empty] | Miniature circuit breaker | [23 empty] | Tmax Moulded Case Circuit Breaker | [15 empty] | Switch Fuse | [7 empty] | Switch | [9 empty] | Switch UL | [9 empty] | Contactor | [18 empty] | Braking Resistor | [19 empty] | du/dt filters | [15 empty] | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | L-class | L-class | L-class | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21)
|  | I1N | I2cont.max |  |  | ABB: OFAF000H4 4A, 500V, 55A2s | ABB: OFAF000H6 6A, 500V, 110A2s | ABB: OFAF000H10 10A, 500V, 360A2s | ABB: OFAF000H16 16A, 500V, 740A2s | ABB: OFAF000H25 25A, 500V, 2,5kA2s | ABB: OFAF000H32 32A, 500V, 4kA2s | ABB: OFAF000H40 40A, 500V, 7,7A2s | ABB: OFAF000H50 50A, 500V, 16kA2s | ABB: OFAF000H63 63A, 500V, 20,1kA2s | ABB: OFAF000H80 80A, 500V, 37,5kA2s | ABB: OFAF000H100 100A, 500V, 65kASs | ABB: OFAF00H125 125A, 500V, 103kA2s | ABB: OFAF00H160 160A, 500V, 185kA2s | ABB: OFAF0H200 200A, 500V, 300kA2s | ABB: OFAF0H250 250A, 500V, 600kA2s | ABB: OFAF1H315 315A, 500V, 710kA2s | ABB: OFAF1H355 355A, 500V, 920kA2s | ABB: OFAF2H400 400A, 500V, 1000kA2s | ABB: OFAF2H425 425A, 500V, 1300kA2s | ABB: OFAF2H500 500A, 500V, 2000kA2s | ABB: OFAF3H630 630A, 500V, 2800kA2s | ABB: OFAA000GG16 16A, 690V, 1,2kA2s | ABB: OFAA000GG20 20A, 690V, 2,4kA2s | ABB: OFAA000GG25 25A, 690V, 4kA2s | ABB: OFAA000GG35 35A, 690V, 12kA2s | ABB: OFAA000GG50 50A, 690V, 24kA2s | ABB: OFAA000GG63 63A, 690V, 30kA2s | ABB: OFAA0GG80 16A, 690V, 51kA2s | ABB: OFAA0GG100 100A, 690V, 95kA2s | ABB: OFAA1GG160 160A, 690V, 240kA2s | ABB: OFAA1GG200 200A, 690V, 350kA2s | ABB: OFAA1GG250 250A, 690V, 700kA2s | ABB: OFAA2GG315 315A, 690V, 850kA2s | ABB: OFAA3GG400 400A, 690V, 1300kA2s | gG fuse is too slow for this drive | Bussmann: 170M1559 16A, 690V, 48A2s | Bussmann: 170M1560 20A, 690V, 78A2s | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1562 32A, 690V, 270A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1564 50A, 690V, 770A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2550A2s | Bussmann: 170M1567 100A, 690V, 4650A2s | Bussmann: 170M1568 125A, 690V, 8500A2s | Bussmann: 170M1569 160A, 690V, 16kA2s | Bussmann: 170M3813 125A, 690V, 3700A2s | Bussmann: 170M3814 160A, 690V, 7500A2s | Bussmann: 170M3815 200A, 690V, 15kA2s | Bussmann: 170M3816 250A, 690V, 28500A2s | Bussmann: 170M3817 315A, 690V, 46500A2s | Bussmann: 170M3818 350A, 690V, 68500A2s | Bussmann: 170M5808 400A, 690V, 74kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 145kA2s | Bussmann: 170M5811 550A, 690V, 190kA2s | Bussmann: 170M5812 630A, 690V, 275kA2s | Bussmann: 170M6810 630A, 690V, 220kA2s | Bussmann: 170M6810D 630A, 690V, 490 kA2s | Bussmann: 170M5813 700A, 690V, 405kA2s | Bussmann: 170M6811D 700A, 690V, 320 kA2s | Bussmann: 170M6812D 800A, 690V, 490 kA2s | Bussmann: 170M6813D 900A, 690V, 720 kA2s | Bussmann: 170M6814D 1000A, 690V, 985 kA2s | Bussmann: 170M6892D 1100A, 690V, 1400 kA2s | Bussmann: 170M8554D 1250A, 690V, 2150 kA2s | Bussmann: 170M8555D 1400A, 690V,2700 kA2s | Bussmann: 170M8556D 1500A, 690V,3350 kA2s | Bussmann: 170M8557D 1600A, 690V,4150 kA2s | Bussmann: 170M1311 25A, 690V, 0,130 kA2s | Bussmann: 170M1313 40A, 690V, 0,46 kA2s | Bussmann: 170M1315 63A, 690V, 1,45 kA2s | Bussmann: 170M1316 80A, 690V, 2,55 kA2s | Bussmann: 170M1417 100A, 690V, 4,65 kA2s | Bussmann: 170M1318 125A, 690V, 8,5 kA2s | Bussmann: 170M1319 160A, 690V, 16 kA2s | Bussmann: 170M3015 200A, 690V, 15 kA2s | Bussmann: 170M3016 250A, 690V, 28,5 kA2s | Bussmann: 170M3017 315A, 690V, 46,5 kA2s | Bussmann: 170M3018 350A, 690V, 68,5 kA2s | Bussmann: 170M5009 450A, 690V, 105 kA2s | Bussmann: 170M5010 500A, 690V, 145 kA2s | Bussmann: 170M5012 630A, 690V, 275 kA2s | Bussmann: 170M5013 700A, 690V, 405 kA2s | Bussmann: 170M6012 800A, 690V, 465 kA2s | Bussmann: 170M6014 1000A, 690V, 945 kA2s | Bussmann: 170M6016 1250A, 690V, 1950 kA2s | Bussmann: 170M6269 1600A, 690V, 3900 kA2s | Bussmann: JJS-3 3A, 600V | Bussmann: JJS-6 6A, 600V | Bussmann: JJS-10 10A, 600V | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-30 30A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-100 100A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-125 125A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-250 250A, 600V | Bussmann: JJS-300 300A, 600V | Bussmann: JJS-350 350A, 600V | Bussmann: JJS-400 400A, 600V | Bussmann: JJS-500 500A, 600V | Bussmann: JJS-600 600A, 600V | Ferraz: A4BY800 800A, 600V | Ferraz: A4BY900 900A, 600V | Ferraz: A4BY1000 1000A, 600V | ABB: S 203P-Z 10 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 10 (prospective SC current 20kA) | ABB: S 203P-Z 16 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 16 (prospective SC current 20kA) | ABB: S 203P-Z 20 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 20 (prospective SC current 20kA) | ABB: S 203P-Z 25 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 25 (prospective SC current 20kA) | ABB: S 203P-Z 32 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 32 (prospective SC current 12kA) | ABB: S 203P-Z 40 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 40 (prospective SC current 12kA) | ABB: S 203P-Z 50 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 50 (prospective SC current 12kA) | ABB: S 203 M/P-B/C 50 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 63 (prospective SC current 5kA) | ABB: S 803 S-B/C 6 (prospective SC current 10kA) | ABB: S 803 S-B/C 10 (prospective SC current 10kA) | ABB: S 803 S-B/C 13 (prospective SC current 10kA) | ABB: S 803 S-B/C 20 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 80 (prospective SC current 50kA, >500V 4kA) | ABB: S 803 S-B/C 100 (prospective SC current 50kA, >500V 3kA) | ABB: S 803 S-B/C 125 (prospective SC current 50kA, >500V 3kA) | No miniature breaker for this drive. Select molded case breaker. | ABB: 1SDA067914R1 (XT2 L 160 Ekip LS/I In=10 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067915R1 (XT2 L 160 Ekip LS/I In=25 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067916R1 (XT2 L 160 Ekip LS/I In=63 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067917R1 (XT2 L 160 Ekip LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067918R1 (XT2 L 160 Ekip LS/I In=160 3p F F) Prospective SC current 65kA | ABB: 1SDA068555R1 (XT4 L 250 Ekip LS/I In=250 3p F F) Prospective SC current 65kA | ABB: 1SDA054069R1 (T4 L 250 PR221DS-LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054070R1 (T4 L 250 PR221DS-LS/I In=160 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054071R1 (T4 L 250 PR221DS-LS/I In=250 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054141R1 (T4 L 320 PR221DS-LS/I In=320 3p F F) Prospective SC current 65kA | ABB: 1SDA054365R1 (T5 L 400 PR221DS-LS/I In=400 3p F F) Prospective SC current 65kA | ABB: 1SDA054420R1 (T5 L 630 PR221DS-LS/I In=630 3p F F) Prospective SC current 65kA | ABB: 1SDA054412R1 (T5H 630 PR221DS-LS/I In=630 3p F F) | ABB: 1SDA069428R1 (T6V 800 PR221DS-LS/I In=800 3p F F) | ABB: 1SDA062770R1 (T7H 1000 PR231/P LS/I In=1000A 3p F F) | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OS400D12_ (1000V, 400A, DIN 0-2) | ABB: OS630D12_ (1000V, 630A, DIN 3) |  | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT1000E_ (1000V, 1000A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) | ABB: OT1200U_ (1000V, 1200A) | ABB: AF09-30-22-13 (25A,1000V 100-250V/50-60Hz) | ABB: AF12-30-22-13 (28A,1000V 100-250V/50-60Hz) | ABB: AF16-30-22-13 (30A,1000V 100-250V/50-60Hz) | ABB: AF26-30-22-13 (45A,1000V 100-250V/50-60Hz) | ABB: AF30-30-22-13 (50A,1000V 100-250V/50-60Hz) | ABB: AF52-30-22-13 (100A,1000V 100-250V/50-60Hz) | ABB: AF65-30-22-13 (115A,1000V 100-250V/50-60Hz) | ABB: AF75-30-22-70 (125A,1000V 100-250V/50-60Hz) | ABB: AF95-30-22-70 (145A,1000V 100-250V/50-60Hz) | ABB: AF110-30-22-70 (160A,1000V 100-250V/50-60Hz) | ABB: AF146-30-22-13 (250A,1000V 100-250V/50-60Hz) | ABB: AF185-30-22-70 (275A,1000V 100-250V/50-60Hz) | ABB: AF210-30-22-70 (350A,1000V 100-250V/50-60Hz) | ABB: AF265-30-22-13 (400A,1000V 100-250V/50-60Hz) | ABB: AF300-30-22-70 (500A,1000V 100-250V/50-60Hz) | ABB: AF400-30-22-70 (600A,1000V 100-250V/50-60Hz) | ABB: AF460-30-22-70 (700A,1000V 100-250V/50-60Hz) | ABB: AF580-30-22-70 (800A,1000V 100-250V/50-60Hz) | ABB: AF750-30-22-70 (1050A,1000V 100-250V/50-60Hz) | ABB Drives: JBR-01 | Danotherm: CBH 360 C T 406 210R | Danotherm: CBR-V 330 D T 406 78R UL | Danotherm: CBR-V 560 D HT 406 39R UL | Danotherm: CBT-H 560 D HT 406 19R | Danotherm: CBT-H 760 D HT 406 16R | BRK-D brake chopper with internal brake resistor | ABB Drives: SACE08RE44 | ABB Drives: SACE15RE22 | ABB Drives: SACE15RE13 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR80F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | ABB Drives: SAFUR210F575 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | ABB Drives: SAFUR210F575 | ABB Drives: NOCH0016-60 | ABB Drives: NOCH0030-60 | ABB Drives: NOCH0070-60 | ABB Drives: NOCH0120-60 | ABB Drives: FOCH0260-70 | ABB Drives: FOCH0320-50 | ABB Drives: FOCH0610-70 | ABB Drives: FOCH0875-70 | ABB Drives: NOCH0016-62 | ABB Drives: NOCH0030-62 | ABB Drives: NOCH0070-62 | ABB Drives: NOCH0120-62 | ABB Drives: NOCH0016-65 | ABB Drives: NOCH0030-65 | ABB Drives: NOCH0070-65 | ABB Drives: NOCH0120-65 | TDK: B84143V0006R231 | TDK: B84143V0007R231 | TDK: B84143V0012R231 | TDK: B84143V0016R229 | TDK: B84143V0038R231 | TDK: B84143V0043R231 | TDK: B84143V0064R231 | TDK: B84143V0077R231 | TDK: B84143V0091R231 | TDK: B84143V0145R231 | TDK: B84143V0209R231 | TDK: B84143V0249R231 | TDK: B84143V0390S229 | TDK: B84143V0004R229 +B84143Q0002R229 | TDK: B84143V0006R229 +B84143Q0002R229 | TDK: B84143V0011R229 +B84143Q0004R229 | TDK: B84143V0016R229 +B84143Q0006R229 | TDK: B84143V0025R229 +B84143Q0008R229 | TDK: B84143V0033R229 +B84143Q0008R229 | TDK: B84143V0050R229 +B84143Q0010R229 | TDK: B84143V0066R229 +B84143Q0010R229 | TDK: B84143V0095R229 +B84143Q0012R229 | TDK: B84143V0162S229 +B84143Q0014R229 | TDK: B84143V0230S229 +B84143Q0016R229 | TDK: B84143V0390S229 +B84143Q0018R229
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [34 empty] | Select aR Fuses | [53 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [30 empty] | *) Alternative option | *) Alternative option | *) Alternative option | [15 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | Connected in series | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | [5 empty] | Connected in series | (with code +D150) | (with code +D150) | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-659 brake chopper | + NBRA-658 brake chopper
UN = 200...240 V (200, 208, 220, 230, 240 V)-IEC Ratings-
ACS580-01-04A7-2 | R1 | 4.7 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACS580-01-06A7-2 | R1 | 6.7 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACS580-01-07A6-2 | R1 | 7.6 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACS580-01-012A-2 | R1 | 12 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACS580-01-018A-2 | R1 | 16.9 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACS580-01-025A-2 | R2 | 24.5 | [9 empty] | 3 | [34 empty] | 3 | [115 empty] | 1 | [7 empty] | 1
ACS580-01-032A-2 | R2 | 31.2 | [9 empty] | 3 | [34 empty] | 3 | [115 empty] | 1 | [8 empty] | 1
ACS580-01-047A-2 | R3 | 46.7 | [11 empty] | 3 | [33 empty] | 3 | [114 empty] | 1 | [8 empty] | 1
ACS580-01-060A-2 | R3 | 60 | [11 empty] | 3 | [33 empty] | 3 | [115 empty] | 1 | [8 empty] | 1
ACS580-01-089A-2 | R5 | 89 | [14 empty] | 3 | [36 empty] | 3 | [109 empty] | 1 | [8 empty] | 1
ACS580-01-115A-2 | R5 | 115 | [14 empty] | 3 | [36 empty] | 3 | [110 empty] | 1 | [8 empty] | 1
ACS580-01-144A-2 | R6 | 144 | [16 empty] | 3 | [36 empty] | 3 | [109 empty] | 1 | [7 empty] | 1
ACS580-01-171A-2 | R7 | 171 | [17 empty] | 3 | [38 empty] | 3 | [106 empty] | 1 | [8 empty] | 1
ACS580-01-213A-2 | R7 | 213 | [18 empty] | 3 | [38 empty] | 3 | [106 empty] | 1 | [7 empty] | 1
ACS580-01-276A-2 | R8 | 276 | [20 empty] | 3 | [39 empty] | 3 | [103 empty] | 1 | [8 empty] | 1
UN = 480 V (380, 400, 415, 440, 480 V)
ACS580-01-02A7-4 | R1 | 2.1 | 2.4 |  |  | 3 | [36 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACS580-01-03A4-4 | R1 | 3 | 3.3 |  |  |  | 3 | [35 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACS580-01-04A1-4 | R1 | 3.4 | 4 |  |  |  | 3 | [35 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACS580-01-05A7-4 | R1 | 4.8 | 5.6 |  |  |  |  | 3 | [34 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [13 empty] | 1
ACS580-01-07A3-4 | R1 | 6 | 7.2 |  |  |  |  | 3 | [34 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [13 empty] | 1
ACS580-01-09A5-4 | R1 | 7.6 | 9.4 | [5 empty] | 3 | [33 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [12 empty] | 1
ACS580-01-12A7-4 | R1 | 11 | 12.6 | [5 empty] | 3 | [33 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [27 empty] | 1 | [35 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [13 empty] | 1
ACS580-01-018A-4 | R2 | 14 | 17 | [6 empty] | 3 | [34 empty] | 3 | [30 empty] | 3 | [23 empty] | 3 | [26 empty] | 1 | [33 empty] | x | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [12 empty] | 1
ACS580-01-026A-4 | R2 | 21 | 25 | [7 empty] | 3 | [33 empty] | 3 | [30 empty] | 3 | [23 empty] | 3 | [28 empty] | 1 | [31 empty] | x | 1 | [9 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [12 empty] | 1
ACS580-01-033A-4 | R3 | 27 | 32 | [8 empty] | 3 | [34 empty] | 3 | [29 empty] | 3 | [24 empty] | 3 | [28 empty] | 1 | [29 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [19 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [13 empty] | 1
ACS580-01-039A-4 | R3 | 34 | 38 | [9 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [28 empty] | 1 | [27 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [14 empty] | 1
ACS580-01-046A-4 | R3 | 40 | 45 | [10 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [25 empty] | 3 | [30 empty] | 1 | [25 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [13 empty] | 1
ACS580-01-062A-4 | R4 | 52 | 61 | [11 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [25 empty] | 3 | [36 empty] | 1 | [18 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [19 empty] | 1 | [15 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [7 empty] | 1 | [13 empty] | 1
ACS580-01-073A-4 | R4 | 65 | 72 | [12 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [34 empty] | 1 | [18 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [19 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [13 empty] | 1
ACS580-01-088A-4 | R5 | 77 | 87 | [12 empty] | 3 | [34 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [34 empty] | 1 | [17 empty] | x |  |  | 1 | [8 empty] | 1 | [10 empty] | 1 | [11 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [7 empty] | 1 | [13 empty] | 1
ACS580-01-106A-4 | R5 | 96 | 105 | [13 empty] | 3 | [38 empty] | 3 | [25 empty] | 3 | [27 empty] | 3 | [33 empty] | 1 | [16 empty] | x |  |  | 1 | [9 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [22 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [8 empty] | 1 | [12 empty] | 1
ACS580-01-145A-4 | R6 | 124 | 145 | [14 empty] | 3 | [37 empty] | 3 | [26 empty] | 3 | [27 empty] | 3 | [33 empty] | x | [5 empty] | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [22 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [12 empty] | 1
ACS580-01-169A-4 | R7 | 156 | 169 | [16 empty] | 3 | [38 empty] | 3 | [24 empty] | 3 | [27 empty] | 3 | [32 empty] | x | [5 empty] | 1 | [14 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [13 empty] | 1 | [23 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [11 empty] | 1
ACS580-01-206A-4 | R7 | 180 | 206 | [17 empty] | 3 | [38 empty] | 3 | [24 empty] | 3 | [28 empty] | 3 | [30 empty] | x | [9 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [13 empty] | 1 | [23 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [12 empty] | 1
ACS580-01-246A-4 | R8 | 240 | 246 | [18 empty] | 3 | [39 empty] | 3 | [23 empty] | 3 | [28 empty] | 3 | [29 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [16 empty] | 1 | [19 empty] | 2 | [9 empty] | 1 | [21 empty] | 1 | [12 empty] | 1
ACS580-01-293A-4 | R8 | 260 | 293 | [20 empty] | 3 | [42 empty] | 3 | [19 empty] | 3 | [28 empty] | 3 | [28 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [16 empty] | 1 | [21 empty] | 2 | [7 empty] | 1 | [22 empty] | 1 | [12 empty] | 1
ACS580-01-363A-4 | R9 | 361 | 363 | [21 empty] | 3 | [43 empty] | 3 | [18 empty] | 3 | [28 empty] | 3 | [27 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [17 empty] | 1 | [21 empty] | 2 | [6 empty] | 1 | [22 empty] | 1 | [11 empty] | 1
ACS580-01-430A-4 | R9 | 414 | 430 | [22 empty] | 3 | [44 empty] | 3 | [17 empty] | 3 | [28 empty] | 3 | [26 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1 | [21 empty] | 2 | [6 empty] | 1 | [22 empty] | 1 | [11 empty] | 1
ACS580-04-505A-4 | R10 | 483 | 505 | [36 empty] | x | [33 empty] | 3 | [15 empty] | 3 | [54 empty] | x | [12 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [38 empty] | 2 | [8 empty] | 1
ACS580-04-585A-4 | R10 | 573 | 585 | [36 empty] | x | [33 empty] | 3 | [16 empty] | 3 | [53 empty] | x | [13 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [39 empty] | 2 | [7 empty] | 1
ACS580-04-650A-4 | R10 | 623 | 650 | [36 empty] | x | [33 empty] | 3 | [16 empty] | 3 | [53 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [38 empty] | 2 | [7 empty] | 1
ACS580-04-725A-4 | R11 | 705 | 725 | [36 empty] | x | [51 empty] | 3 | [52 empty] | x | [14 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [38 empty] | 3 | [8 empty] | 1
ACS580-04-820A-4 | R11 | 807 | 820 | [36 empty] | x | [52 empty] | 3 | [51 empty] | x | [14 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [37 empty] | 3 | [8 empty] | 1
ACS580-04-880A-4 | R11 | 807 | 880 | [36 empty] | x | [52 empty] | 3 | [51 empty] | x | [14 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [37 empty] | 3 | [8 empty] | 1

## ACH580-01_04
|  |  |  | Main Cable |  | Main Fuses (gG) | [34 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [33 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [18 empty] | Main Fuses (UL) | [27 empty] | Miniature circuit breaker | [23 empty] | Moulded Case Circuit Breaker | [15 empty] | Mains Switch for gG fuse | [7 empty] | Mains Switch | [9 empty] | Mains Switch UL | [9 empty] | Main Contactor | [18 empty] | Braking Resistor | [19 empty] | Output Chokes (du/dt filters) | [15 empty] | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [34 empty] | aR Fuses(see footnotes) | [33 empty] | aR Fuses | [18 empty] | UL-class Fuses | [27 empty] | Miniature circuit breaker | [23 empty] | Tmax Moulded Case Circuit Breaker | [15 empty] | Switch Fuse | [7 empty] | Switch | [9 empty] | Switch UL | [9 empty] | Contactor | [18 empty] | Braking Resistor | [19 empty] | du/dt filters | [15 empty] | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | L-class | L-class | L-class | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21)
|  | I1N | I2cont.max |  |  | ABB: OFAF000H4 4A, 500V, 55A2s | ABB: OFAF000H6 6A, 500V, 110A2s | ABB: OFAF000H10 10A, 500V, 360A2s | ABB: OFAF000H16 16A, 500V, 740A2s | ABB: OFAF000H25 25A, 500V, 2,5kA2s | ABB: OFAF000H32 32A, 500V, 4kA2s | ABB: OFAF000H40 40A, 500V, 7,7A2s | ABB: OFAF000H50 50A, 500V, 16kA2s | ABB: OFAF000H63 63A, 500V, 20,1kA2s | ABB: OFAF000H80 80A, 500V, 37,5kA2s | ABB: OFAF000H100 100A, 500V, 65kASs | ABB: OFAF00H125 125A, 500V, 103kA2s | ABB: OFAF00H160 160A, 500V, 185kA2s | ABB: OFAF0H200 200A, 500V, 300kA2s | ABB: OFAF0H250 250A, 500V, 600kA2s | ABB: OFAF1H315 315A, 500V, 710kA2s | ABB: OFAF1H355 355A, 500V, 920kA2s | ABB: OFAF2H400 400A, 500V, 1000kA2s | ABB: OFAF2H425 425A, 500V, 1300kA2s | ABB: OFAF2H500 500A, 500V, 2000kA2s | ABB: OFAF3H630 630A, 500V, 2800kA2s | ABB: OFAA000GG16 16A, 690V, 1,2kA2s | ABB: OFAA000GG20 20A, 690V, 2,4kA2s | ABB: OFAA000GG25 25A, 690V, 4kA2s | ABB: OFAA000GG35 35A, 690V, 12kA2s | ABB: OFAA000GG50 50A, 690V, 24kA2s | ABB: OFAA000GG63 63A, 690V, 30kA2s | ABB: OFAA0GG80 16A, 690V, 51kA2s | ABB: OFAA0GG100 100A, 690V, 95kA2s | ABB: OFAA1GG160 160A, 690V, 240kA2s | ABB: OFAA1GG200 200A, 690V, 350kA2s | ABB: OFAA1GG250 250A, 690V, 700kA2s | ABB: OFAA2GG315 315A, 690V, 850kA2s | ABB: OFAA3GG400 400A, 690V, 1300kA2s | gG fuse is too slow for this drive | Bussmann: 170M1559 16A, 690V, 48A2s | Bussmann: 170M1560 20A, 690V, 78A2s | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1562 32A, 690V, 270A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1564 50A, 690V, 770A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2550A2s | Bussmann: 170M1567 100A, 690V, 4650A2s | Bussmann: 170M1568 125A, 690V, 8500A2s | Bussmann: 170M1569 160A, 690V, 16kA2s | Bussmann: 170M3813 125A, 690V, 3700A2s | Bussmann: 170M3814 160A, 690V, 7500A2s | Bussmann: 170M3815 200A, 690V, 15kA2s | Bussmann: 170M3816 250A, 690V, 28500A2s | Bussmann: 170M3817 315A, 690V, 46500A2s | Bussmann: 170M3818 350A, 690V, 68500A2s | Bussmann: 170M5808 400A, 690V, 74kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 145kA2s | Bussmann: 170M5811 550A, 690V, 190kA2s | Bussmann: 170M5812 630A, 690V, 275kA2s | Bussmann: 170M6810 630A, 690V, 220kA2s | Bussmann: 170M6810D 630A, 690V, 490 kA2s | Bussmann: 170M5813 700A, 690V, 405kA2s | Bussmann: 170M6811D 700A, 690V, 320 kA2s | Bussmann: 170M6812D 800A, 690V, 490 kA2s | Bussmann: 170M6813D 900A, 690V, 720 kA2s | Bussmann: 170M6814D 1000A, 690V, 985 kA2s | Bussmann: 170M6892D 1100A, 690V, 1400 kA2s | Bussmann: 170M8554D 1250A, 690V, 2150 kA2s | Bussmann: 170M8555D 1400A, 690V,2700 kA2s | Bussmann: 170M8556D 1500A, 690V,3350 kA2s | Bussmann: 170M8557D 1600A, 690V,4150 kA2s | Bussmann: 170M1311 25A, 690V, 0,130 kA2s | Bussmann: 170M1313 40A, 690V, 0,46 kA2s | Bussmann: 170M1315 63A, 690V, 1,45 kA2s | Bussmann: 170M1316 80A, 690V, 2,55 kA2s | Bussmann: 170M1417 100A, 690V, 4,65 kA2s | Bussmann: 170M1318 125A, 690V, 8,5 kA2s | Bussmann: 170M1319 160A, 690V, 16 kA2s | Bussmann: 170M3015 200A, 690V, 15 kA2s | Bussmann: 170M3016 250A, 690V, 28,5 kA2s | Bussmann: 170M3017 315A, 690V, 46,5 kA2s | Bussmann: 170M3018 350A, 690V, 68,5 kA2s | Bussmann: 170M5009 450A, 690V, 105 kA2s | Bussmann: 170M5010 500A, 690V, 145 kA2s | Bussmann: 170M5012 630A, 690V, 275 kA2s | Bussmann: 170M5013 700A, 690V, 405 kA2s | Bussmann: 170M6012 800A, 690V, 465 kA2s | Bussmann: 170M6014 1000A, 690V, 945 kA2s | Bussmann: 170M6016 1250A, 690V, 1950 kA2s | Bussmann: 170M6269 1600A, 690V, 3900 kA2s | Bussmann: JJS-3 3A, 600V | Bussmann: JJS-6 6A, 600V | Bussmann: JJS-10 10A, 600V | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-30 30A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-100 100A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-125 125A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-250 250A, 600V | Bussmann: JJS-300 300A, 600V | Bussmann: JJS-350 350A, 600V | Bussmann: JJS-400 400A, 600V | Bussmann: JJS-500 500A, 600V | Bussmann: JJS-600 600A, 600V | Ferraz: A4BY800 800A, 600V | Ferraz: A4BY900 900A, 600V | Ferraz: A4BY1000 1000A, 600V | ABB: S 203P-Z 10 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 10 (prospective SC current 20kA) | ABB: S 203P-Z 16 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 16 (prospective SC current 20kA) | ABB: S 203P-Z 20 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 20 (prospective SC current 20kA) | ABB: S 203P-Z 25 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 25 (prospective SC current 20kA) | ABB: S 203P-Z 32 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 32 (prospective SC current 12kA) | ABB: S 203P-Z 40 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 40 (prospective SC current 12kA) | ABB: S 203P-Z 50 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 50 (prospective SC current 12kA) | ABB: S 203 M/P-B/C 50 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 63 (prospective SC current 5kA) | ABB: S 803 S-B/C 6 (prospective SC current 10kA) | ABB: S 803 S-B/C 10 (prospective SC current 10kA) | ABB: S 803 S-B/C 13 (prospective SC current 10kA) | ABB: S 803 S-B/C 20 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 80 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 100 (prospective SC current 50kA, >500V 3kA) | ABB: S 803 S-B/C 125 (prospective SC current 10kA, >500V 3kA) | No miniature breaker for this drive. Select molded case breaker. | ABB: 1SDA067914R1 (XT2 L 160 Ekip LS/I In=10 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067915R1 (XT2 L 160 Ekip LS/I In=25 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067916R1 (XT2 L 160 Ekip LS/I In=63 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067917R1 (XT2 L 160 Ekip LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067918R1 (XT2 L 160 Ekip LS/I In=160 3p F F) Prospective SC current 65kA | ABB: 1SDA068555R1 (XT4 L 250 Ekip LS/I In=250 3p F F) Prospective SC current 65kA | ABB: 1SDA054069R1 (T4 L 250 PR221DS-LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054070R1 (T4 L 250 PR221DS-LS/I In=160 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054071R1 (T4 L 250 PR221DS-LS/I In=250 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054141R1 (T4 L 320 PR221DS-LS/I In=320 3p F F) Prospective SC current 65kA | ABB: 1SDA054365R1 (T5 L 400 PR221DS-LS/I In=400 3p F F) Prospective SC current 65kA | ABB: 1SDA054420R1 (T5 L 630 PR221DS-LS/I In=630 3p F F) Prospective SC current 65kA | ABB: 1SDA054412R1 (T5H 630 PR221DS-LS/I In=630 3p F F) | ABB: 1SDA069428R1 (T6V 800 PR221DS-LS/I In=800 3p F F) | ABB: 1SDA062770R1 (T7H 1000 PR231/P LS/I In=1000A 3p F F) | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OS400D12_ (1000V, 400A, DIN 0-2) | ABB: OS630D12_ (1000V, 630A, DIN 3) |  | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT1000E_ (1000V, 1000A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) | ABB: OT1200U_ (1000V, 1200A) | ABB: AF09-30-22-13 (25A,1000V 100-250V/50-60Hz) | ABB: AF12-30-22-13 (28A,1000V 100-250V/50-60Hz) | ABB: AF16-30-22-13 (30A,1000V 100-250V/50-60Hz) | ABB: AF26-30-22-13 (45A,1000V 100-250V/50-60Hz) | ABB: AF30-30-22-13 (50A,1000V 100-250V/50-60Hz) | ABB: AF52-30-22-13 (100A,1000V 100-250V/50-60Hz) | ABB: AF65-30-22-13 (115A,1000V 100-250V/50-60Hz) | ABB: AF75-30-22-70 (125A,1000V 100-250V/50-60Hz) | ABB: AF95-30-22-70 (145A,1000V 100-250V/50-60Hz) | ABB: AF110-30-22-70 (160A,1000V 100-250V/50-60Hz) | ABB: AF146-30-22-13 (250A,1000V 100-250V/50-60Hz) | ABB: AF185-30-22-70 (275A,1000V 100-250V/50-60Hz) | ABB: AF210-30-22-70 (350A,1000V 100-250V/50-60Hz) | ABB: AF265-30-22-13 (400A,1000V 100-250V/50-60Hz) | ABB: AF300-30-22-70 (500A,1000V 100-250V/50-60Hz) | ABB: AF400-30-22-70 (600A,1000V 100-250V/50-60Hz) | ABB: AF460-30-22-70 (700A,1000V 100-250V/50-60Hz) | ABB: AF580-30-22-70 (800A,1000V 100-250V/50-60Hz) | ABB: AF750-30-22-70 (1050A,1000V 100-250V/50-60Hz) | ABB Drives: JBR-01 | Danotherm: CBH 360 C T 406 210R | Danotherm: CBR-V 330 D T 406 78R UL | Danotherm: CBR-V 560 D HT 406 39R UL | Danotherm: CBT-H 560 D HT 406 19R | Danotherm: CBT-H 760 D HT 406 16R | BRK-D brake chopper with internal brake resistor | ABB Drives: SACE08RE44 | ABB Drives: SACE15RE22 | ABB Drives: SACE15RE13 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR80F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | ABB Drives: SAFUR210F575 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | ABB Drives: SAFUR210F575 | ABB Drives: NOCH0016-60 | ABB Drives: NOCH0030-60 | ABB Drives: NOCH0070-60 | ABB Drives: NOCH0120-60 | ABB Drives: FOCH0260-70 | ABB Drives: FOCH0320-50 | ABB Drives: FOCH0610-70 | ABB Drives: FOCH0875-70 | ABB Drives: NOCH0016-62 | ABB Drives: NOCH0030-62 | ABB Drives: NOCH0070-62 | ABB Drives: NOCH0120-62 | ABB Drives: NOCH0016-65 | ABB Drives: NOCH0030-65 | ABB Drives: NOCH0070-65 | ABB Drives: NOCH0120-65 | B84143V0006R231 | B84143V0007R231 | B84143V0012R231 | TDK: B84143V0016R229 | TDK: B84143V0038R231 | TDK: B84143V0043R231 | TDK: B84143V0064R231 | TDK: B84143V0077R231 | TDK: B84143V0091R231 | TDK: B84143V0145R231 | TDK: B84143V0209R231 | TDK: B84143V0249R231 | TDK: B84143V0390S229 | TDK: B84143V0004R229 +B84143Q0002R229 | TDK: B84143V0006R229 +B84143Q0002R229 | TDK: B84143V0011R229 +B84143Q0004R229 | TDK: B84143V0016R229 +B84143Q0006R229 | TDK: B84143V0025R229 +B84143Q0008R229 | TDK: B84143V0033R229 +B84143Q0008R229 | TDK: B84143V0050R229 +B84143Q0010R229 | TDK: B84143V0066R229 +B84143Q0010R229 | TDK: B84143V0095R229 +B84143Q0012R229 | TDK: B84143V0162S229 +B84143Q0014R229 | TDK: B84143V0230S229 +B84143Q0016R229 | TDK: B84143V0390S229 +B84143Q0018R229
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [34 empty] | Select aR Fuses | [53 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [30 empty] | *) Alternative option | *) Alternative option | *) Alternative option | [15 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | Connected in series | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | [5 empty] | Connected in series | (with code +D150) | (with code +D150) | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-659 brake chopper | + NBRA-658 brake chopper
UN = 200...240 V (200, 208, 220, 230, 240 V)-IEC Ratings-
ACH580-01-04A7-2 | R1 | 4.7 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACH580-01-06A7-2 | R1 | 6.7 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACH580-01-07A6-2 | R1 | 7.6 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACH580-01-012A-2 | R1 | 12 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACH580-01-018A-2 | R1 | 16.9 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACH580-01-025A-2 | R2 | 24.5 | [9 empty] | 3 | [34 empty] | 3 | [115 empty] | 1 | [7 empty] | 1
ACH580-01-032A-2 | R2 | 31.2 | [9 empty] | 3 | [34 empty] | 3 | [115 empty] | 1 | [8 empty] | 1
ACH580-01-047A-2 | R3 | 46.7 | [11 empty] | 3 | [33 empty] | 3 | [114 empty] | 1 | [8 empty] | 1
ACH580-01-060A-2 | R3 | 60 | [11 empty] | 3 | [33 empty] | 3 | [115 empty] | 1 | [8 empty] | 1
ACH580-01-089A-2 | R5 | 89 | [14 empty] | 3 | [36 empty] | 3 | [109 empty] | 1 | [8 empty] | 1
ACH580-01-115A-2 | R5 | 115 | [14 empty] | 3 | [36 empty] | 3 | [110 empty] | 1 | [8 empty] | 1
ACH580-01-144A-2 | R6 | 144 | [16 empty] | 3 | [36 empty] | 3 | [109 empty] | 1 | [7 empty] | 1
ACH580-01-171A-2 | R7 | 171 | [17 empty] | 3 | [38 empty] | 3 | [106 empty] | 1 | [8 empty] | 1
ACH580-01-213A-2 | R7 | 213 | [18 empty] | 3 | [38 empty] | 3 | [106 empty] | 1 | [7 empty] | 1
ACH580-01-276A-2 | R8 | 276 | [20 empty] | 3 | [39 empty] | 3 | [103 empty] | 1 | [8 empty] | 1
UN = 480 V (380, 400, 415, 440, 480 V)
ACH580-01-02A7-4 | R1 | 2.1 | 2.4 |  |  | 3 | [36 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACH580-01-03A4-4 | R1 | 3 | 3.3 |  |  |  | 3 | [35 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACH580-01-04A1-4 | R1 | 3.4 | 4 |  |  |  | 3 | [35 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACH580-01-05A7-4 | R1 | 4.8 | 5.6 |  |  |  |  | 3 | [34 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [13 empty] | 1
ACH580-01-07A3-4 | R1 | 6 | 7.2 |  |  |  |  | 3 | [34 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [13 empty] | 1
ACH580-01-09A5-4 | R1 | 7.6 | 9.4 | [5 empty] | 3 | [33 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [12 empty] | 1
ACH580-01-12A7-4 | R1 | 11 | 12.6 | [5 empty] | 3 | [33 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [27 empty] | 1 | [35 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [13 empty] | 1
ACH580-01-018A-4 | R2 | 14 | 17 | [6 empty] | 3 | [34 empty] | 3 | [30 empty] | 3 | [23 empty] | 3 | [26 empty] | 1 | [33 empty] | x | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [12 empty] | 1
ACH580-01-026A-4 | R2 | 21 | 25 | [7 empty] | 3 | [33 empty] | 3 | [30 empty] | 3 | [23 empty] | 3 | [28 empty] | 1 | [31 empty] | x | 1 | [9 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [12 empty] | 1
ACH580-01-033A-4 | R3 | 27 | 32 | [8 empty] | 3 | [34 empty] | 3 | [29 empty] | 3 | [24 empty] | 3 | [28 empty] | 1 | [29 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [19 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [13 empty] | 1
ACH580-01-039A-4 | R3 | 34 | 38 | [9 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [28 empty] | 1 | [27 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [14 empty] | 1
ACH580-01-046A-4 | R3 | 40 | 45 | [10 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [25 empty] | 3 | [30 empty] | 1 | [25 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [13 empty] | 1
ACH580-01-062A-4 | R4 | 52 | 61 | [11 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [25 empty] | 3 | [36 empty] | 1 | [18 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [19 empty] | 1 | [15 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [7 empty] | 1 | [13 empty] | 1
ACH580-01-073A-4 | R4 | 65 | 72 | [12 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [34 empty] | 1 | [18 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [19 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [13 empty] | 1
ACH580-01-088A-4 | R5 | 77 | 87 | [12 empty] | 3 | [34 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [34 empty] | 1 | [17 empty] | x |  |  | 1 | [8 empty] | 1 | [10 empty] | 1 | [11 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [7 empty] | 1 | [13 empty] | 1
ACH580-01-106A-4 | R5 | 96 | 105 | [13 empty] | 3 | [38 empty] | 3 | [25 empty] | 3 | [27 empty] | 3 | [33 empty] | 1 | [16 empty] | x |  |  | 1 | [9 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [22 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [8 empty] | 1 | [12 empty] | 1
ACH580-01-145A-4 | R6 | 124 | 145 | [14 empty] | 3 | [37 empty] | 3 | [26 empty] | 3 | [27 empty] | 3 | [33 empty] | x | [5 empty] | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [22 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [12 empty] | 1
ACH580-01-169A-4 | R7 | 156 | 169 | [16 empty] | 3 | [38 empty] | 3 | [24 empty] | 3 | [27 empty] | 3 | [32 empty] | x | [5 empty] | 1 | [14 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [13 empty] | 1 | [23 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [11 empty] | 1
ACH580-01-206A-4 | R7 | 180 | 206 | [17 empty] | 3 | [38 empty] | 3 | [24 empty] | 3 | [28 empty] | 3 | [30 empty] | x | [9 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [13 empty] | 1 | [23 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [12 empty] | 1
ACH580-01-246A-4 | R8 | 240 | 246 | [18 empty] | 3 | [39 empty] | 3 | [23 empty] | 3 | [28 empty] | 3 | [29 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [16 empty] | 1 | [19 empty] | 2 | [9 empty] | 1 | [21 empty] | 1 | [12 empty] | 1
ACH580-01-293A-4 | R8 | 260 | 293 | [20 empty] | 3 | [42 empty] | 3 | [19 empty] | 3 | [28 empty] | 3 | [28 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [16 empty] | 1 | [21 empty] | 2 | [7 empty] | 1 | [22 empty] | 1 | [12 empty] | 1
ACH580-01-363A-4 | R9 | 361 | 363 | [21 empty] | 3 | [43 empty] | 3 | [18 empty] | 3 | [28 empty] | 3 | [27 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [17 empty] | 1 | [21 empty] | 2 | [6 empty] | 1 | [22 empty] | 1 | [11 empty] | 1
ACH580-01-430A-4 | R9 | 414 | 430 | [22 empty] | 3 | [44 empty] | 3 | [17 empty] | 3 | [28 empty] | 3 | [26 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1 | [21 empty] | 2 | [6 empty] | 1 | [22 empty] | 1 | [11 empty] | 1
ACH580-04-505A-4 | R10 | 483 | 505 | [36 empty] | x | [33 empty] | 3 | [15 empty] | 3 | [54 empty] | x | [12 empty] | 1 | [18 empty] | 1 | [9 empty] | 1
ACH580-04-585A-4 | R10 | 573 | 585 | [36 empty] | x | [33 empty] | 3 | [16 empty] | 3 | [53 empty] | x | [13 empty] | 1 | [17 empty] | 1 | [9 empty] | 1
ACH580-04-650A-4 | R10 | 623 | 650 | [36 empty] | x | [33 empty] | 3 | [16 empty] | 3 | [53 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1
ACH580-04-725A-4 | R11 | 705 | 725 | [36 empty] | x | [51 empty] | 3 | [52 empty] | x | [14 empty] | 1 | [17 empty] | 1 | [9 empty] | 1
ACH580-04-820A-4 | R11 | 807 | 820 | [36 empty] | x | [52 empty] | 3 | [51 empty] | x | [14 empty] | 1 | [18 empty] | 1 | [9 empty] | 1
ACH580-04-880A-4 | R11 | 807 | 880 | [36 empty] | x | [52 empty] | 3 | [51 empty] | x | [14 empty] | 1 | [18 empty] | 1 | [9 empty] | 1

## ACQ580-01_04
|  |  |  | Main Cable |  | Main Fuses (gG) | [34 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [33 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [18 empty] | Main Fuses (UL) | [27 empty] | Miniature circuit breaker | [23 empty] | Moulded Case Circuit Breaker | [15 empty] | Mains Switch for gG fuse | [7 empty] | Mains Switch | [9 empty] | Mains Switch UL | [9 empty] | Main Contactor | [18 empty] | Braking Resistor | [19 empty] | Output Chokes (du/dt filters) | [15 empty] | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [34 empty] | aR Fuses(see footnotes) | [33 empty] | aR Fuses | [18 empty] | UL-class Fuses | [27 empty] | Miniature circuit breaker | [23 empty] | Tmax Moulded Case Circuit Breaker | [15 empty] | Switch Fuse | [7 empty] | Switch | [9 empty] | Switch UL | [9 empty] | Contactor | [18 empty] | Braking Resistor | [19 empty] | du/dt filters | [15 empty] | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | L-class | L-class | L-class | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | Braking Resistor | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters unprotected (IP00) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP22) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | du/dt filters protected (IP54) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21)
|  | I1N | I2cont.max |  |  | ABB: OFAF000H4 4A, 500V, 55A2s | ABB: OFAF000H6 6A, 500V, 110A2s | ABB: OFAF000H10 10A, 500V, 360A2s | ABB: OFAF000H16 16A, 500V, 740A2s | ABB: OFAF000H25 25A, 500V, 2,5kA2s | ABB: OFAF000H32 32A, 500V, 4kA2s | ABB: OFAF000H40 40A, 500V, 7,7A2s | ABB: OFAF000H50 50A, 500V, 16kA2s | ABB: OFAF000H63 63A, 500V, 20,1kA2s | ABB: OFAF000H80 80A, 500V, 37,5kA2s | ABB: OFAF000H100 100A, 500V, 65kASs | ABB: OFAF00H125 125A, 500V, 103kA2s | ABB: OFAF00H160 160A, 500V, 185kA2s | ABB: OFAF0H200 200A, 500V, 300kA2s | ABB: OFAF0H250 250A, 500V, 600kA2s | ABB: OFAF1H315 315A, 500V, 710kA2s | ABB: OFAF1H355 355A, 500V, 920kA2s | ABB: OFAF2H400 400A, 500V, 1000kA2s | ABB: OFAF2H425 425A, 500V, 1300kA2s | ABB: OFAF2H500 500A, 500V, 2000kA2s | ABB: OFAF3H630 630A, 500V, 2800kA2s | ABB: OFAA000GG16 16A, 690V, 1,2kA2s | ABB: OFAA000GG20 20A, 690V, 2,4kA2s | ABB: OFAA000GG25 25A, 690V, 4kA2s | ABB: OFAA000GG35 35A, 690V, 12kA2s | ABB: OFAA000GG50 50A, 690V, 24kA2s | ABB: OFAA000GG63 63A, 690V, 30kA2s | ABB: OFAA0GG80 16A, 690V, 51kA2s | ABB: OFAA0GG100 100A, 690V, 95kA2s | ABB: OFAA1GG160 160A, 690V, 240kA2s | ABB: OFAA1GG200 200A, 690V, 350kA2s | ABB: OFAA1GG250 250A, 690V, 700kA2s | ABB: OFAA2GG315 315A, 690V, 850kA2s | ABB: OFAA3GG400 400A, 690V, 1300kA2s | gG fuse is too slow for this drive | Bussmann: 170M1559 16A, 690V, 48A2s | Bussmann: 170M1560 20A, 690V, 78A2s | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1562 32A, 690V, 270A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1564 50A, 690V, 770A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2550A2s | Bussmann: 170M1567 100A, 690V, 4650A2s | Bussmann: 170M1568 125A, 690V, 8500A2s | Bussmann: 170M1569 160A, 690V, 16kA2s | Bussmann: 170M3813 125A, 690V, 3700A2s | Bussmann: 170M3814 160A, 690V, 7500A2s | Bussmann: 170M3815 200A, 690V, 15kA2s | Bussmann: 170M3816 250A, 690V, 28500A2s | Bussmann: 170M3817 315A, 690V, 46500A2s | Bussmann: 170M3818 350A, 690V, 68500A2s | Bussmann: 170M5808 400A, 690V, 74kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 145kA2s | Bussmann: 170M5811 550A, 690V, 190kA2s | Bussmann: 170M5812 630A, 690V, 275kA2s | Bussmann: 170M6810 630A, 690V, 220kA2s | Bussmann: 170M6810D 630A, 690V, 490 kA2s | Bussmann: 170M5813 700A, 690V, 405kA2s | Bussmann: 170M6811D 700A, 690V, 320 kA2s | Bussmann: 170M6812D 800A, 690V, 490 kA2s | Bussmann: 170M6813D 900A, 690V, 720 kA2s | Bussmann: 170M6814D 1000A, 690V, 985 kA2s | Bussmann: 170M6892D 1100A, 690V, 1400 kA2s | Bussmann: 170M8554D 1250A, 690V, 2150 kA2s | Bussmann: 170M8555D 1400A, 690V,2700 kA2s | Bussmann: 170M8556D 1500A, 690V,3350 kA2s | Bussmann: 170M8557D 1600A, 690V,4150 kA2s | Bussmann: 170M1311 25A, 690V, 0,130 kA2s | Bussmann: 170M1313 40A, 690V, 0,46 kA2s | Bussmann: 170M1315 63A, 690V, 1,45 kA2s | Bussmann: 170M1316 80A, 690V, 2,55 kA2s | Bussmann: 170M1417 100A, 690V, 4,65 kA2s | Bussmann: 170M1318 125A, 690V, 8,5 kA2s | Bussmann: 170M1319 160A, 690V, 16 kA2s | Bussmann: 170M3015 200A, 690V, 15 kA2s | Bussmann: 170M3016 250A, 690V, 28,5 kA2s | Bussmann: 170M3017 315A, 690V, 46,5 kA2s | Bussmann: 170M3018 350A, 690V, 68,5 kA2s | Bussmann: 170M5009 450A, 690V, 105 kA2s | Bussmann: 170M5010 500A, 690V, 145 kA2s | Bussmann: 170M5012 630A, 690V, 275 kA2s | Bussmann: 170M5013 700A, 690V, 405 kA2s | Bussmann: 170M6012 800A, 690V, 465 kA2s | Bussmann: 170M6014 1000A, 690V, 945 kA2s | Bussmann: 170M6016 1250A, 690V, 1950 kA2s | Bussmann: 170M6269 1600A, 690V, 3900 kA2s | Bussmann: JJS-3 3A, 600V | Bussmann: JJS-6 6A, 600V | Bussmann: JJS-10 10A, 600V | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-30 30A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-100 100A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-125 125A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-250 250A, 600V | Bussmann: JJS-300 300A, 600V | Bussmann: JJS-350 350A, 600V | Bussmann: JJS-400 400A, 600V | Bussmann: JJS-500 500A, 600V | Bussmann: JJS-600 600A, 600V | Ferraz: A4BY800 800A, 600V | Ferraz: A4BY900 900A, 600V | Ferraz: A4BY1000 1000A, 600V | ABB: S 203P-Z 10 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 10 (prospective SC current 20kA) | ABB: S 203P-Z 16 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 16 (prospective SC current 20kA) | ABB: S 203P-Z 20 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 20 (prospective SC current 20kA) | ABB: S 203P-Z 25 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 25 (prospective SC current 20kA) | ABB: S 203P-Z 32 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 32 (prospective SC current 12kA) | ABB: S 203P-Z 40 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 40 (prospective SC current 12kA) | ABB: S 203P-Z 50 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 50 (prospective SC current 12kA) | ABB: S 203 M/P-B/C 50 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 63 (prospective SC current 5kA) | ABB: S 803 S-B/C 6 (prospective SC current 10kA) | ABB: S 803 S-B/C 10 (prospective SC current 10kA) | ABB: S 803 S-B/C 13 (prospective SC current 10kA) | ABB: S 803 S-B/C 20 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 80 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 100 (prospective SC current 50kA, >500V 3kA) | ABB: S 803 S-B/C 125 (prospective SC current 10kA, >500V 3kA) | No miniature breaker for this drive. Select molded case breaker. | ABB: 1SDA067914R1 (XT2 L 160 Ekip LS/I In=10 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067915R1 (XT2 L 160 Ekip LS/I In=25 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067916R1 (XT2 L 160 Ekip LS/I In=63 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067917R1 (XT2 L 160 Ekip LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 18kA | ABB: 1SDA067918R1 (XT2 L 160 Ekip LS/I In=160 3p F F) Prospective SC current 65kA | ABB: 1SDA068555R1 (XT4 L 250 Ekip LS/I In=250 3p F F) Prospective SC current 65kA | ABB: 1SDA054069R1 (T4 L 250 PR221DS-LS/I In=100 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054070R1 (T4 L 250 PR221DS-LS/I In=160 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054071R1 (T4 L 250 PR221DS-LS/I In=250 3p F F) 500V: Prospective SC current 65kA >500V Prospective SC current 35kA | ABB: 1SDA054141R1 (T4 L 320 PR221DS-LS/I In=320 3p F F) Prospective SC current 65kA | ABB: 1SDA054365R1 (T5 L 400 PR221DS-LS/I In=400 3p F F) Prospective SC current 65kA | ABB: 1SDA054420R1 (T5 L 630 PR221DS-LS/I In=630 3p F F) Prospective SC current 65kA | ABB: 1SDA054412R1 (T5H 630 PR221DS-LS/I In=630 3p F F) | ABB: 1SDA069428R1 (T6V 800 PR221DS-LS/I In=800 3p F F) | ABB: 1SDA062770R1 (T7H 1000 PR231/P LS/I In=1000A 3p F F) | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OS400D12_ (1000V, 400A, DIN 0-2) | ABB: OS630D12_ (1000V, 630A, DIN 3) |  | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT1000E_ (1000V, 1000A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) | ABB: OT1200U_ (1000V, 1200A) | ABB: AF09-30-22-13 (25A,1000V 100-250V/50-60Hz) | ABB: AF12-30-22-13 (28A,1000V 100-250V/50-60Hz) | ABB: AF16-30-22-13 (30A,1000V 100-250V/50-60Hz) | ABB: AF26-30-22-13 (45A,1000V 100-250V/50-60Hz) | ABB: AF30-30-22-13 (50A,1000V 100-250V/50-60Hz) | ABB: AF52-30-22-13 (100A,1000V 100-250V/50-60Hz) | ABB: AF65-30-22-13 (115A,1000V 100-250V/50-60Hz) | ABB: AF75-30-22-70 (125A,1000V 100-250V/50-60Hz) | ABB: AF95-30-22-70 (145A,1000V 100-250V/50-60Hz) | ABB: AF110-30-22-70 (160A,1000V 100-250V/50-60Hz) | ABB: AF146-30-22-13 (250A,1000V 100-250V/50-60Hz) | ABB: AF185-30-22-70 (275A,1000V 100-250V/50-60Hz) | ABB: AF210-30-22-70 (350A,1000V 100-250V/50-60Hz) | ABB: AF265-30-22-13 (400A,1000V 100-250V/50-60Hz) | ABB: AF300-30-22-70 (500A,1000V 100-250V/50-60Hz) | ABB: AF400-30-22-70 (600A,1000V 100-250V/50-60Hz) | ABB: AF460-30-22-70 (700A,1000V 100-250V/50-60Hz) | ABB: AF580-30-22-70 (800A,1000V 100-250V/50-60Hz) | ABB: AF750-30-22-70 (1050A,1000V 100-250V/50-60Hz) | ABB Drives: JBR-01 | Danotherm: CBH 360 C T 406 210R | Danotherm: CBR-V 330 D T 406 78R UL | Danotherm: CBR-V 560 D HT 406 39R UL | Danotherm: CBT-H 560 D HT 406 19R | Danotherm: CBT-H 760 D HT 406 16R | BRK-D brake chopper with internal brake resistor | ABB Drives: SACE08RE44 | ABB Drives: SACE15RE22 | ABB Drives: SACE15RE13 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR90F575 | ABB Drives: SAFUR80F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | ABB Drives: SAFUR210F575 | ABB Drives: SAFUR125F500 | ABB Drives: SAFUR200F500 | ABB Drives: SAFUR210F575 | ABB Drives: NOCH0016-60 | ABB Drives: NOCH0030-60 | ABB Drives: NOCH0070-60 | ABB Drives: NOCH0120-60 | ABB Drives: FOCH0260-70 | ABB Drives: FOCH0320-50 | ABB Drives: FOCH0610-70 | ABB Drives: FOCH0875-70 | ABB Drives: NOCH0016-62 | ABB Drives: NOCH0030-62 | ABB Drives: NOCH0070-62 | ABB Drives: NOCH0120-62 | ABB Drives: NOCH0016-65 | ABB Drives: NOCH0030-65 | ABB Drives: NOCH0070-65 | ABB Drives: NOCH0120-65 | TDK: B84143V0006R231 | TDK: B84143V0007R231 | TDK: B84143V0012R231 | TDK: B84143V0016R229 | TDK: B84143V0038R231 | TDK: B84143V0043R231 | TDK: B84143V0064R231 | TDK: B84143V0077R231 | TDK: B84143V0091R231 | TDK: B84143V0145R231 | TDK: B84143V0209R231 | TDK: B84143V0249R231 | TDK: B84143V0390S229 | TDK: B84143V0004R229 +B84143Q0002R229 | TDK: B84143V0006R229 +B84143Q0002R229 | TDK: B84143V0011R229 +B84143Q0004R229 | B84143V0016R229 +B84143Q0006R229 | TDK: B84143V0025R229 +B84143Q0008R229 | TDK: B84143V0033R229 +B84143Q0008R229 | TDK: B84143V0050R229 +B84143Q0010R229 | TDK: B84143V0066R229 +B84143Q0010R229 | TDK: B84143V0095R229 +B84143Q0012R229 | TDK: B84143V0162S229 +B84143Q0014R229 | TDK: B84143V0230S229 +B84143Q0016R229 | TDK: B84143V0390S229 +B84143Q0018R229
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/116 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [34 empty] | Select aR Fuses | [53 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [30 empty] | *) Alternative option | *) Alternative option | *) Alternative option | [15 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | Connected in series | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | No external brake chopper needed | [5 empty] | Connected in series | (with code +D150) | (with code +D150) | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-658 brake chopper | + NBRA-659 brake chopper | + NBRA-658 brake chopper
UN = 200...240 V (200, 208, 220, 230, 240 V)-IEC Ratings-
ACQ580-01-04A7-2 | R1 | 4.7 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACQ580-01-06A7-2 | R1 | 6.7 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACQ580-01-07A6-2 | R1 | 7.6 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACQ580-01-012A-2 | R1 | 12 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACQ580-01-018A-2 | R1 | 16.9 | [7 empty] | 3 | [34 empty] | 3 | [116 empty] | 1 | [7 empty] | 1
ACQ580-01-025A-2 | R2 | 24.5 | [9 empty] | 3 | [34 empty] | 3 | [115 empty] | 1 | [7 empty] | 1
ACQ580-01-032A-2 | R2 | 31.2 | [9 empty] | 3 | [34 empty] | 3 | [115 empty] | 1 | [8 empty] | 1
ACQ580-01-047A-2 | R3 | 46.7 | [11 empty] | 3 | [33 empty] | 3 | [114 empty] | 1 | [8 empty] | 1
ACQ580-01-060A-2 | R3 | 60 | [11 empty] | 3 | [33 empty] | 3 | [115 empty] | 1 | [8 empty] | 1
ACQ580-01-089A-2 | R5 | 89 | [14 empty] | 3 | [36 empty] | 3 | [109 empty] | 1 | [8 empty] | 1
ACQ580-01-115A-2 | R5 | 115 | [14 empty] | 3 | [36 empty] | 3 | [110 empty] | 1 | [8 empty] | 1
ACQ580-01-144A-2 | R6 | 144 | [16 empty] | 3 | [36 empty] | 3 | [109 empty] | 1 | [7 empty] | 1
ACQ580-01-171A-2 | R7 | 171 | [17 empty] | 3 | [38 empty] | 3 | [106 empty] | 1 | [8 empty] | 1
ACQ580-01-213A-2 | R7 | 213 | [18 empty] | 3 | [38 empty] | 3 | [106 empty] | 1 | [7 empty] | 1
ACQ580-01-276A-2 | R8 | 276 | [20 empty] | 3 | [39 empty] | 3 | [103 empty] | 1 | [8 empty] | 1
UN = 480 V (380, 400, 415, 440, 480 V)
ACQ580-01-02A7-4 | R1 | 2.1 | 2.4 |  |  | 3 | [36 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACQ580-01-03A4-4 | R1 | 3 | 3.3 |  |  |  | 3 | [35 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACQ580-01-04A1-4 | R1 | 3.4 | 4 |  |  |  | 3 | [35 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [12 empty] | 1
ACQ580-01-05A7-4 | R1 | 4.8 | 5.6 |  |  |  |  | 3 | [34 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [19 empty] | 1 | [18 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 | [13 empty] | 1
ACQ580-01-07A3-4 | R1 | 6 | 7.2 |  |  |  |  | 3 | [34 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  |  |  |  | 1 | [13 empty] | 1
ACQ580-01-09A5-4 | R1 | 7.6 | 9.4 | [5 empty] | 3 | [33 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [25 empty] | 1 | [37 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [12 empty] | 1
ACQ580-01-12A7-4 | R1 | 11 | 12.6 | [5 empty] | 3 | [33 empty] | 3 | [31 empty] | 3 | [21 empty] | 3 | [27 empty] | 1 | [35 empty] | x | 1 | [7 empty] | 1 | [9 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [13 empty] | 1
ACQ580-01-018A-4 | R2 | 14 | 17 | [6 empty] | 3 | [34 empty] | 3 | [30 empty] | 3 | [23 empty] | 3 | [26 empty] | 1 | [33 empty] | x | 1 | [8 empty] | 1 | [9 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [12 empty] | 1
ACQ580-01-026A-4 | R2 | 21 | 25 | [7 empty] | 3 | [33 empty] | 3 | [30 empty] | 3 | [23 empty] | 3 | [28 empty] | 1 | [31 empty] | x | 1 | [9 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [12 empty] | 1
ACQ580-01-033A-4 | R3 | 27 | 32 | [8 empty] | 3 | [34 empty] | 3 | [29 empty] | 3 | [24 empty] | 3 | [28 empty] | 1 | [29 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [10 empty] | 1 | [19 empty] | 1 | [17 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [13 empty] | 1
ACQ580-01-039A-4 | R3 | 34 | 38 | [9 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [28 empty] | 1 | [27 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [5 empty] | 1 | [14 empty] | 1
ACQ580-01-046A-4 | R3 | 40 | 45 | [10 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [25 empty] | 3 | [30 empty] | 1 | [25 empty] | x |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [12 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [13 empty] | 1
ACQ580-01-062A-4 | R4 | 52 | 61 | [11 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [25 empty] | 3 | [36 empty] | 1 | [18 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [19 empty] | 1 | [15 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [7 empty] | 1 | [13 empty] | 1
ACQ580-01-073A-4 | R4 | 65 | 72 | [12 empty] | 3 | [33 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [34 empty] | 1 | [18 empty] | x |  |  | 1 | [8 empty] | 1 | [9 empty] | 1 | [11 empty] | 1 | [19 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [13 empty] | 1
ACQ580-01-088A-4 | R5 | 77 | 87 | [12 empty] | 3 | [34 empty] | 3 | [29 empty] | 3 | [26 empty] | 3 | [34 empty] | 1 | [17 empty] | x |  |  | 1 | [8 empty] | 1 | [10 empty] | 1 | [11 empty] | 1 | [18 empty] | 1 | [16 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [7 empty] | 1 | [13 empty] | 1
ACQ580-01-106A-4 | R5 | 96 | 105 | [13 empty] | 3 | [38 empty] | 3 | [25 empty] | 3 | [27 empty] | 3 | [33 empty] | 1 | [16 empty] | x |  |  | 1 | [9 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [22 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 |  |  |  | 1 | [8 empty] | 1 | [12 empty] | 1
ACQ580-01-145A-4 | R6 | 124 | 145 | [14 empty] | 3 | [37 empty] | 3 | [26 empty] | 3 | [27 empty] | 3 | [33 empty] | x | [5 empty] | 1 | [13 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [15 empty] | 1 | [22 empty] | 1 | [9 empty] | 1 | [20 empty] | 1 | [12 empty] | 1
ACQ580-01-169A-4 | R7 | 156 | 169 | [16 empty] | 3 | [38 empty] | 3 | [24 empty] | 3 | [27 empty] | 3 | [32 empty] | x | [5 empty] | 1 | [14 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [13 empty] | 1 | [23 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [11 empty] | 1
ACQ580-01-206A-4 | R7 | 180 | 206 | [17 empty] | 3 | [38 empty] | 3 | [24 empty] | 3 | [28 empty] | 3 | [30 empty] | x | [9 empty] | 1 | [11 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [13 empty] | 1 | [23 empty] | 1 | [8 empty] | 1 | [21 empty] | 1 | [12 empty] | 1
ACQ580-01-246A-4 | R8 | 240 | 246 | [18 empty] | 3 | [39 empty] | 3 | [23 empty] | 3 | [28 empty] | 3 | [29 empty] | x | [10 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [16 empty] | 1 | [19 empty] | 2 | [9 empty] | 1 | [21 empty] | 1 | [12 empty] | 1
ACQ580-01-293A-4 | R8 | 260 | 293 | [20 empty] | 3 | [42 empty] | 3 | [19 empty] | 3 | [28 empty] | 3 | [28 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [9 empty] | 1 | [16 empty] | 1 | [21 empty] | 2 | [7 empty] | 1 | [22 empty] | 1 | [12 empty] | 1
ACQ580-01-363A-4 | R9 | 361 | 363 | [21 empty] | 3 | [43 empty] | 3 | [18 empty] | 3 | [28 empty] | 3 | [27 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [7 empty] | 1 | [10 empty] | 1 | [17 empty] | 1 | [21 empty] | 2 | [6 empty] | 1 | [22 empty] | 1 | [11 empty] | 1
ACQ580-01-430A-4 | R9 | 414 | 430 | [22 empty] | 3 | [44 empty] | 3 | [17 empty] | 3 | [28 empty] | 3 | [26 empty] | x | [11 empty] | 1 | [10 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1 | [21 empty] | 2 | [6 empty] | 1 | [22 empty] | 1 | [11 empty] | 1
ACQ580-04-505A-4 | R10 | 483 | 505 | [36 empty] | x | [33 empty] | 3 | [15 empty] | 3 | [54 empty] | x | [12 empty] | 1 | [18 empty] | 1 | [9 empty] | 1
ACQ580-04-585A-4 | R10 | 573 | 585 | [36 empty] | x | [33 empty] | 3 | [16 empty] | 3 | [53 empty] | x | [13 empty] | 1 | [17 empty] | 1 | [9 empty] | 1
ACQ580-04-650A-4 | R10 | 623 | 650 | [36 empty] | x | [33 empty] | 3 | [16 empty] | 3 | [53 empty] | x | [13 empty] | 1 | [18 empty] | 1 | [9 empty] | 1
ACQ580-04-725A-4 | R11 | 705 | 725 | [36 empty] | x | [51 empty] | 3 | [52 empty] | x | [14 empty] | 1 | [17 empty] | 1 | [9 empty] | 1
ACQ580-04-820A-4 | R11 | 807 | 820 | [36 empty] | x | [52 empty] | 3 | [51 empty] | x | [14 empty] | 1 | [18 empty] | 1 | [9 empty] | 1
ACQ580-04-880A-4 | R11 | 807 | 880 | [36 empty] | x | [52 empty] | 3 | [51 empty] | x | [14 empty] | 1 | [18 empty] | 1 | [9 empty] | 1

## ACH580-31_34
[6 empty] | Main fuses (gG) | [8 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [14 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [23 empty] | Main Fuses (UL) | [19 empty] | Miniature circuit breaker | [28 empty] | Moulded case circuit breaker |  | Mains Switch for gG fuse |  |  |  |  | Mains Switch | [8 empty] | Mains Switch UL | [8 empty] | Main Contactor | [18 empty] | Output Chokes (du/dt filters) | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [8 empty] | aR Fuses (see footnotes) | [14 empty] | aR Fuses | [23 empty] | UL-class Fuses | [19 empty] | Miniature circuit breaker | [28 empty] | Tmax Moulded Case Circuit Breaker |  | Switch Fuse |  |  |  |  | Switch | [8 empty] | Switch UL | [8 empty] | Contactor | [18 empty] | du/dt filters | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | aR ; Flush end | aR ; Flush end | aR ; Flush end | aR ; Flush end | aR ; Flush end | aR ; Flush end | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | Braking Resistor | RCCB F 200 series | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21)
|  | I1N | I2cont.max |  |  | ABB: OFAF000H16 16A, 500V, 740A2s | ABB: OFAF000H25 25A, 500V, 2.5kA2s | ABB: OFAF000H32 32A, 500V, 4.0kA2s | ABB: OFAF000H40 40A, 500V, 7.7kA2s | ABB: OFAF000H50 50A, 500V, 16kA2s | ABB: OFAF000H63 63A, 500V, 20.1kA2s | ABB: OFAF000H80 80A, 500V, 37.5kA2s | ABB: OFAF000H100 100A, 500V, 65kA2s | gG fuse is too slow for this drive | Bussmann: 170M1558 10A, 690V, 27A2s | Bussmann: 170M1559 16A, 690V, 51A2s | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2700A2s | Bussmann: 170M1567 100A, 690V, 4950A2s | Bussmann: 170M1568 125A, 690V, 8250A2s | Bussmann: 170M1569 160A, 690V, 16.5kA2s | Bussmann: 170M1570 200A, 690V, 31kA2s | Bussmann: 170M3817 315A, 690V, 46.5kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 155kA2s | Bussmann: 170M5808 400A, 690V, 79kA2s | Bussmann: 170M5812 630A, 690V, 295kA2s | Bussmann: 170M1308 10A, 690V, 0,026 kA2s | Bussmann: 170M1309 16A, 690V, 0,048 kA2s | Bussmann: 170M1311 25A, 690V, 0,130 kA2s | Bussmann: 170M1312 32A, 690V, 0,27 kA2s | Bussmann: 170M1313 40A, 690V, 0,46 kA2s | Bussmann: 170M1314 50A, 690V, 0.77 kA2s | Bussmann: 170M1315 63A, 690V, 1,45 kA2s | Bussmann: 170M1316 80A, 690V, 2,55 kA2s | Bussmann: 170M1317 100A, 690V, 4,65 kA2s | Bussmann: 170M1318 125A, 690V, 8,5 kA2s | Bussmann: 170M1319 160A, 690V, 16 kA2s | Bussmann: 170M1320 200A, 690V, 28 kA2s | Bussmann: 170M2618 250A, 690V, 42 kA2s | Bussmann: 170M2619 315A, 690V, 68.5 kA2s | Bussmann: 170M3015 200A, 690V, 15 kA2s | Bussmann: 170M3016 250A, 690V, 28,5 kA2s | Bussmann: 170M3017 315A, 690V, 46,5 kA2s | Bussmann: 170M4410 315A, 690V, 42 kA2s | Bussmann: 170M5408 400A, 690V, 74 kA2s | Bussmann: 170M5410 500A, 690V, 145 kA2s | Bussmann: 170M6410 630A, 690V, 210 kA2s | Bussmann: 170M6411 700A, 690V, 300 kA2s | Bussmann: 170M6412 800A, 690V, 465 kA2s | Bussmann: 170M6414 1000A, 690V, 945 kA2s | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-300 300A, 600V | Bussmann: 170M5408 400A, 690V | Bussmann: 170M5410 500A, 690V | Bussmann: 170M6410 630A, 690V | Bussmann: 170M6411 700A, 690V | Bussmann: 170M6412 800A, 690V | Bussmann: 170M6414 1000A, 690V | ABB: S 203P-Z 10 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 10 (prospective SC current 25kA) | ABB: S 203P-Z 16 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 16 (prospective SC current 25kA) | ABB: S 203P-Z 20 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 20 (prospective SC current 25kA) | ABB: S 203P-Z 25 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 25 (prospective SC current 25kA) | ABB: S 203P-Z 32 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 32 (prospective SC current 15kA) | ABB: S 203P-Z 40 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 40 (prospective SC current 15kA) | ABB: S 203P-Z 50 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 50 (prospective SC current 15kA) | ABB: S 203 M/P-B/C 50 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 63 (prospective SC current 5kA) | ABB: S 803 S-B/C 6 (prospective SC current 10kA) | ABB: S 803 S-B/C 10 (prospective SC current 10kA) | ABB: S 803 S-B/C 13 (prospective SC current 10kA) | ABB: S 803 S-B/C 20 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 25 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 32 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 50 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 63 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 75 (prospective SC current 10kA) | ABB: S 803 S-B/C 80 (prospective SC current 16kA ) | ABB: S 803 S-B/C 100 (prospective SC current 25kA ) | ABB: S 803 S-B/C 125 (prospective SC current 50kA, >500V 3kA) | No miniature breaker for this drive. Select molded case breaker. | Not available yet | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) | ABB: AF09-30-22-13 (25A,1000V 100-250V/50-60Hz) | ABB: AF12-30-22-13 (28A,1000V 100-250V/50-60Hz) | ABB: AF16-30-22-13 (30A,1000V 100-250V/50-60Hz) | ABB: AF26-30-22-13 (45A,1000V 100-250V/50-60Hz) | ABB: AF30-30-22-13 (50A,1000V 100-250V/50-60Hz) | ABB: AF50-30-22-70 (100A,1000V 100-250V/50-60Hz) | ABB: AF63-30-22-70 (115A,1000V 100-250V/50-60Hz) | ABB: AF75-30-22-70 (125A,1000V 100-250V/50-60Hz) | ABB: AF95-30-22-70 (145A,1000V 100-250V/50-60Hz) | ABB: AF110-30-22-70 (160A,1000V 100-250V/50-60Hz) | ABB: AF146-30-22-13 (250A,1000V 100-250V/50-60Hz) | ABB: AF185-30-22-70 (275A,1000V 100-250V/50-60Hz) | ABB: AF210-30-22-70 (350A,1000V 100-250V/50-60Hz) | ABB: AF265-30-22-13 (400A,1000V 100-250V/50-60Hz) | ABB: AF300-30-22-70 (500A,1000V 100-250V/50-60Hz) | ABB: AF400-30-22-70 (600A,1000V 100-250V/50-60Hz) | ABB: AF460-30-22-70 (700A,1000V 100-250V/50-60Hz) | ABB: AF580-30-22-70 (800A,1000V 100-250V/50-60Hz) | ABB: AF750-30-22-70 (1050A,1000V 100-250V/50-60Hz) | ABB: NOCH0016-6X | ABB: NOCH0030-6X | ABB: NOCH0070-6X | ABB: NOCH0120-6X | ABB: FOCH0260-70 | ABB: FOCH0260-7X | ABB: FOCH0320-5x | ABB: FOCH-0610-70 |  |  | TDK: B84143V0012R231 | TDK: B84143V0016R229 | TDK: B84143V0038R231 | TDK: B84143V0043R231 | TDK: B84143V0064R231 | TDK: B84143V0077R231 | TDK: B84143V0091R231 | TDK: B84143V0145R231 | TDK: B84143V0209R231 | TDK: B84143V0011R229 +B84143Q0004R229 | TDK: B84143V0006R229 +B84143Q0002R229 | TDK: B84143V0011R229 +B84143Q0004R229 | TDK: B84143V0016R229 +B84143Q0006R229 | TDK: B84143V0025R229 +B84143Q0008R229 | TDK: B84143V0033R229 +B84143Q0008R229 | TDK: B84143V0050R229 +B84143Q0010R229 | TDK: B84143V0066R229 +B84143Q0010R229 | TDK: B84143V0095R229 +B84143Q0012R229 | TDK: B84143V0162S229 +B84143Q0014R229 | TDK: B84143V0230S229 +B84143Q0016R229 | TDK: B84143V0390S229 +B84143Q0018R229
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [8 empty] | Select aR Fuses | [39 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [42 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C
UN = 400 V (380, 400, 415 V)
ACH580-31-09A5-4 | R3 | 8 |  |  |  | 3 | [10 empty] | 3 | [14 empty] | 3 | [22 empty] | 3 | [19 empty] | 3 | [27 empty] | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACH580-31-12A7-4 | R3 | 10 |  |  |  | 3 | [10 empty] | 3 | [14 empty] | 3 | [22 empty] | 3 | [21 empty] | 3 | [25 empty] | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACH580-31-018A-4 | R3 | 14 |  |  |  |  | 3 | [10 empty] | 3 | [13 empty] | 3 | [24 empty] | 3 | [21 empty] | 3 | [23 empty] | x |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 | [19 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACH580-31-026A-4 | R3 | 20 | [5 empty] | 3 | [9 empty] | 3 | [14 empty] | 3 | [23 empty] | 3 | [23 empty] | 3 | [21 empty] | x |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [10 empty] | 1 | [10 empty] | 1
ACH580-31-033A-4 | R6 | 27 | [6 empty] | 3 | [9 empty] | 3 | [14 empty] | 3 | [25 empty] | 3 | [22 empty] | 3 | [19 empty] | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACH580-31-039A-4 | R6 | 33 | [7 empty] | 3 | [8 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [24 empty] | 3 | [17 empty] | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACH580-31-046A-4 | R6 | 40 | [8 empty] | 3 | [8 empty] | 3 | [16 empty] | 3 | [22 empty] | 3 | [26 empty] | 3 | [15 empty] | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1 | [10 empty] | 1 | [11 empty] | 1
ACH580-31-062A-4 | R6 | 51 | [9 empty] | 3 | [8 empty] | 3 | [15 empty] | 3 | [25 empty] | 3 | [35 empty] | 3 |  |  |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1
ACH580-31-073A-4 | R6 | 63 | [10 empty] | 3 | [8 empty] | 3 | [15 empty] | 3 | [24 empty] | 3 | [35 empty] | 3 |  |  |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [16 empty] | 1 | [10 empty] | 1 | [11 empty] | 1
ACH580-31-088A-4 | R6 | 76 | [10 empty] | 3 | [8 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [36 empty] | 3 |  |  | x |  |  |  | 1 | [6 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1
ACH580-31-106A-4 | R8 | 94 | [11 empty] | x | [8 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [38 empty] | x | [10 empty] | 1 | [8 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACH580-31-145A-4 | R8 | 128 | [11 empty] | x | [9 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [37 empty] | x | [10 empty] | 1 | [8 empty] | 1 | [40 empty] | 1 | [10 empty] | 1
ACH580-31-169A-4 | R8 | 154 | [11 empty] | x | [11 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [36 empty] | x | [11 empty] | 1 | [9 empty] | 1 | [39 empty] | 1 | [9 empty] | 1
ACH580-31-206A-4 | R8 | 188 | [11 empty] | x | [12 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [35 empty] | x | [11 empty] | 1 | [9 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACH580-34-246A-4 | R11 | 212 | [11 empty] | x | [33 empty] | 3 | [19 empty] | 3 | [34 empty] | x | [11 empty] | 1 | [9 empty] | 1
ACH580-34-293A-4 | R11 | 257 | [11 empty] | x | [34 empty] | 3 | [19 empty] | 3 | [33 empty] | x | [12 empty] | 1 | [8 empty] | 1
ACH580-34-365A-4 | R11 | 321 | [11 empty] | x | [35 empty] | 3 | [19 empty] | 3 | [32 empty] | x | [12 empty] | 1 | [9 empty] | 1
ACH580-34-442A-4 | R11 | 401 | [11 empty] | x | [36 empty] | 3 | [19 empty] | 3 | [31 empty] | x | [13 empty] | 1 | [8 empty] | 1
ACH580-34-505A-4 | R11 | 401 | [11 empty] | x | [37 empty] | 3 | [19 empty] | 3 | [30 empty] | x | [13 empty] | 1 | [8 empty] | 1
ACH580-34-585A-4 | R11 | 505 | [11 empty] | x | [38 empty] | 3 | [19 empty] | 3 | [29 empty] | x | [13 empty] | 1 | [8 empty] | 1
ACH580-34-650A-4 | R11 | 569 | [11 empty] | x | [38 empty] | 3 | [19 empty] | 3 | [29 empty] | x | [14 empty] | 1 | [8 empty] | 1
UN = 480 V (440, 460, 480 V) -NEC Ratings-
ACH580-31-07A6-4 | R3 | 7 | [12 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [19 empty] | 3 | [34 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1
ACH580-31-012A-4 | R3 | 9 | [13 empty] | 3 | [14 empty] | 3 | [23 empty] | 3 | [21 empty] | 3 | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1
ACH580-31-014A-4 | R3 | 12 | [14 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [21 empty] | 3 | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 | [19 empty] | 1
ACH580-31-023A-4 | R3 | 17 | [14 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [23 empty] | 3 | [29 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1
ACH580-31-027A-4 | R6 | 24 | [16 empty] | 3 | [15 empty] | 3 | [24 empty] | 3 | [22 empty] | 3 | [28 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1
ACH580-31-034A-4 | R6 | 29 | [16 empty] | 3 | [15 empty] | 3 | [24 empty] | 3 | [24 empty] | 3 | [26 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACH580-31-044A-4 | R6 | 34 | [16 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [26 empty] | 3 | [24 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACH580-31-052A-4 | R6 | 44 | [17 empty] | 3 | [16 empty] | 3 | [25 empty] | 3 | [35 empty] | 3 | [13 empty] | 1 | [7 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACH580-31-065A-4 | R6 | 54 | [18 empty] | 3 | [17 empty] | 3 | [23 empty] | 3 | [35 empty] | 3 | [13 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [16 empty] | 1
ACH580-31-077A-4 | R6 | 66 | [19 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [36 empty] | 3 | [13 empty] | 1 | [7 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACH580-31-096A-4 | R8 | 82 | [20 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [48 empty] | 1 | 1 | [8 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACH580-31-124A-4 | R8 | 111 | [22 empty] | 3 | [18 empty] | 3 | [20 empty] | 3 | [48 empty] | 1 | [8 empty] | 1 | [40 empty] | 1 | [10 empty] | 1
ACH580-31-156A-4 | R8 | 134 | [25 empty] | 3 | [16 empty] | 3 | [20 empty] | 3 | [47 empty] | 1 | [8 empty] | 1 | [41 empty] | 1 | [9 empty] | 1
ACH580-31-180A-4 | R8 | 163 | [26 empty] | 3 | [16 empty] | 3 | [20 empty] | 3 | [47 empty] | 1 | [9 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACH580-34-240A-4 | R11 | 209 | [44 empty] | 3 | [20 empty] | 3 | [46 empty] | 1 | [9 empty] | 1
ACH580-34-302A-4 | R11 | 258 | [45 empty] | 3 | [20 empty] | 3 | [46 empty] | 1 | [8 empty] | 1
ACH580-34-361A-4 | R11 | 307 | [46 empty] | 3 | [20 empty] | 3 | [45 empty] | 1 | [9 empty] | 1
ACH580-34-414A-4 | R11 | 363 | [47 empty] | 3 | [20 empty] | 3 | [45 empty] | 1 | [8 empty] | 1
ACH580-34-477A-4 | R11 | 418 | [48 empty] | 3 | [20 empty] | 3 | [44 empty] | 1 | [8 empty] | 1

## ACQ580-31_34
[6 empty] | Main fuses (gG) | [8 empty] | Main Fuses (aR) (BLADE style DIN 43620 ) | [14 empty] | Main Fuses (aR) (BOLTED tags DIN 43653 ) | [23 empty] | Main Fuses (UL) | [19 empty] | Miniature circuit breaker | [28 empty] | Moulded case circuit breaker |  | Mains Switch for gG fuse |  |  |  |  | Mains Switch | [8 empty] | Mains Switch UL | [8 empty] | Main Contactor | [18 empty] | Output Chokes (du/dt filters) | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
Type |  |  | Current ratings | Mains cable * |  | gG Fuses (see footnotes) | [8 empty] | aR Fuses (see footnotes) | [14 empty] | aR Fuses | [23 empty] | UL-class Fuses | [19 empty] | Miniature circuit breaker | [28 empty] | Tmax Moulded Case Circuit Breaker |  | Switch Fuse |  |  |  |  | Switch | [8 empty] | Switch UL | [8 empty] | Contactor | [18 empty] | du/dt filters | [7 empty] | Braking Resistor | Residual Current Device | Sine Filter
[6 empty] | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | gG Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | aR Fuses | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | T-class | aR ; Flush end | aR ; Flush end | aR ; Flush end | aR ; Flush end | aR ; Flush end | aR ; Flush end | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker | Miniature circuit breaker |  | Tmax Moulded Case Circuit Breaker |  | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch Fuse | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Switch-disconnector | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | Contactor | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | du/dt filters unprotected | Braking Resistor | RCCB F 200 series | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP00) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21) | Sine Filter (IP21)
|  | I1N | I2cont.max |  |  | ABB: OFAF000H16 16A, 500V, 740A2s | ABB: OFAF000H25 25A, 500V, 2.5kA2s | ABB: OFAF000H32 32A, 500V, 4.0kA2s | ABB: OFAF000H40 40A, 500V, 7.7kA2s | ABB: OFAF000H50 50A, 500V, 16kA2s | ABB: OFAF000H63 63A, 500V, 20.1kA2s | ABB: OFAF000H80 80A, 500V, 37.5kA2s | ABB: OFAF000H100 100A, 500V, 65kA2s | gG fuse is too slow for this drive | Bussmann: 170M1558 10A, 690V, 27A2s | Bussmann: 170M1559 16A, 690V, 51A2s | Bussmann: 170M1561 25A, 690V, 130A2s | Bussmann: 170M1563 40A, 690V, 460A2s | Bussmann: 170M1565 63A, 690V, 1450A2s | Bussmann: 170M1566 80A, 690V, 2700A2s | Bussmann: 170M1567 100A, 690V, 4950A2s | Bussmann: 170M1568 125A, 690V, 8250A2s | Bussmann: 170M1569 160A, 690V, 16.5kA2s | Bussmann: 170M1570 200A, 690V, 31kA2s | Bussmann: 170M3817 315A, 690V, 46.5kA2s | Bussmann: 170M5809 450A, 690V, 105kA2s | Bussmann: 170M5810 500A, 690V, 155kA2s | Bussmann: 170M5808 400A, 690V, 79kA2s | Bussmann: 170M5812 630A, 690V, 295kA2s | Bussmann: 170M1308 10A, 690V, 0,026 kA2s | Bussmann: 170M1309 16A, 690V, 0,048 kA2s | Bussmann: 170M1311 25A, 690V, 0,130 kA2s | Bussmann: 170M1312 32A, 690V, 0,27 kA2s | Bussmann: 170M1313 40A, 690V, 0,46 kA2s | Bussmann: 170M1314 50A, 690V, 0.77 kA2s | Bussmann: 170M1315 63A, 690V, 1,45 kA2s | Bussmann: 170M1316 80A, 690V, 2,55 kA2s | Bussmann: 170M1317 100A, 690V, 4,65 kA2s | Bussmann: 170M1318 125A, 690V, 8,5 kA2s | Bussmann: 170M1319 160A, 690V, 16 kA2s | Bussmann: 170M1320 200A, 690V, 28 kA2s | Bussmann: 170M2618 250A, 690V, 42 kA2s | Bussmann: 170M2619 315A, 690V, 68.5 kA2s | Bussmann: 170M3015 200A, 690V, 15 kA2s | Bussmann: 170M3016 250A, 690V, 28,5 kA2s | Bussmann: 170M3017 315A, 690V, 46,5 kA2s | Bussmann: 170M4410 315A, 690V, 42 kA2s | Bussmann: 170M5408 400A, 690V, 74 kA2s | Bussmann: 170M5410 500A, 690V, 145 kA2s | Bussmann: 170M6410 630A, 690V, 210 kA2s | Bussmann: 170M6411 700A, 690V, 300 kA2s | Bussmann: 170M6412 800A, 690V, 465 kA2s | Bussmann: 170M6414 1000A, 690V, 945 kA2s | Bussmann: JJS-15 15A, 600V | Bussmann: JJS-20 20A, 600V | Bussmann: JJS-25 25A, 600V | Bussmann: JJS-35 35A, 600V | Bussmann: JJS-40 40A, 600V | Bussmann: JJS-50 50A, 600V | Bussmann: JJS-60 60A, 600V | Bussmann: JJS-80 80A, 600V | Bussmann: JJS-90 90A, 600V | Bussmann: JJS-110 110A, 600V | Bussmann: JJS-150 150A, 600V | Bussmann: JJS-200 200A, 600V | Bussmann: JJS-225 225A, 600V | Bussmann: JJS-300 300A, 600V | Bussmann: 170M5408 400A, 690V | Bussmann: 170M5410 500A, 690V | Bussmann: 170M6410 630A, 690V | Bussmann: 170M6411 700A, 690V | Bussmann: 170M6412 800A, 690V | Bussmann: 170M6414 1000A, 690V | ABB: S 203P-Z 10 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 10 (prospective SC current 25kA) | ABB: S 203P-Z 16 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 16 (prospective SC current 25kA) | ABB: S 203P-Z 20 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 20 (prospective SC current 25kA) | ABB: S 203P-Z 25 (prospective SC current 25kA) | ABB: S 203P-B/C/Z 25 (prospective SC current 25kA) | ABB: S 203P-Z 32 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 32 (prospective SC current 15kA) | ABB: S 203P-Z 40 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 40 (prospective SC current 15kA) | ABB: S 203P-Z 50 (prospective SC current 15kA) | ABB: S 203P-B/C/Z 50 (prospective SC current 15kA) | ABB: S 203 M/P-B/C 50 (prospective SC current 5kA) | ABB: S 203 M/P-B/C 63 (prospective SC current 5kA) | ABB: S 803 S-B/C 6 (prospective SC current 10kA) | ABB: S 803 S-B/C 10 (prospective SC current 10kA) | ABB: S 803 S-B/C 13 (prospective SC current 10kA) | ABB: S 803 S-B/C 20 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 25 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 32 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 50 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 63 (prospective SC current 10kA, >500V 4kA) | ABB: S 803 S-B/C 75 (prospective SC current 10kA) | ABB: S 803 S-B/C 80 (prospective SC current 16kA ) | ABB: S 803 S-B/C 100 (prospective SC current 25kA ) | ABB: S 803 S-B/C 125 (prospective SC current 50kA, >500V 3kA) | No miniature breaker for this drive. Select molded case breaker. | Not available yet | No Moulded case circuit breaker for this drive. Select miniature circuit breaker. | ABB: OS32GD_ (1000V,32A,DIN 000) | ABB: OS63GD_ (1000V,63A,DIN 000) | ABB: OS125GD_ (1000V, 125A, DIN 000,00) | ABB: OS160GD_ (1000V, 160A, DIN 000,00) | ABB: OS250D12_ (1000V, 250A, DIN 0-1) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT160EV_ (1000V, 160A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400E_ (1000V, 400A) | ABB: OT630E_ (1000V, 630A) | ABB: OT800E_ (1000V, 800A) | ABB: OT16F3_ (750V,16A) | ABB: OT25F3_ (750V,25A) | ABB: OT63F3_ (750V, 63A) | ABB: OT100F_ (750V, 100A) | ABB: OT200U_ (1000V, 200A) | ABB: OT250E_ (1000V, 250A) | ABB: OT400U_ (1000V, 400A) | ABB: OT600U_ (1000V, 600A) | ABB: OT800U_ (1000V, 800A) | ABB: AF09-30-22-13 (25A,1000V 100-250V/50-60Hz) | ABB: AF12-30-22-13 (28A,1000V 100-250V/50-60Hz) | ABB: AF16-30-22-13 (30A,1000V 100-250V/50-60Hz) | ABB: AF26-30-22-13 (45A,1000V 100-250V/50-60Hz) | ABB: AF30-30-22-13 (50A,1000V 100-250V/50-60Hz) | ABB: AF50-30-22-70 (100A,1000V 100-250V/50-60Hz) | ABB: AF63-30-22-70 (115A,1000V 100-250V/50-60Hz) | ABB: AF75-30-22-70 (125A,1000V 100-250V/50-60Hz) | ABB: AF95-30-22-70 (145A,1000V 100-250V/50-60Hz) | ABB: AF110-30-22-70 (160A,1000V 100-250V/50-60Hz) | ABB: AF146-30-22-13 (250A,1000V 100-250V/50-60Hz) | ABB: AF185-30-22-70 (275A,1000V 100-250V/50-60Hz) | ABB: AF210-30-22-70 (350A,1000V 100-250V/50-60Hz) | ABB: AF265-30-22-13 (400A,1000V 100-250V/50-60Hz) | ABB: AF300-30-22-70 (500A,1000V 100-250V/50-60Hz) | ABB: AF400-30-22-70 (600A,1000V 100-250V/50-60Hz) | ABB: AF460-30-22-70 (700A,1000V 100-250V/50-60Hz) | ABB: AF580-30-22-70 (800A,1000V 100-250V/50-60Hz) | ABB: AF750-30-22-70 (1050A,1000V 100-250V/50-60Hz) | ABB: NOCH0016-6X | ABB: NOCH0030-6X | ABB: NOCH0070-6X | ABB: NOCH0120-6X | ABB: FOCH0260-70 | ABB: FOCH0260-7X | ABB: FOCH0320-5x | ABB: FOCH-0610-70 |  |  | TDK: B84143V0012R231 | TDK: B84143V0016R229 | TDK: B84143V0038R231 | TDK: B84143V0043R231 | TDK: B84143V0064R231 | TDK: B84143V0077R231 | TDK: B84143V0091R231 | TDK: B84143V0145R231 | TDK: B84143V0209R231 | TDK: B84143V0011R229 +B84143Q0004R229 | TDK: B84143V0006R229 +B84143Q0002R229 | TDK: B84143V0011R229 +B84143Q0004R229 | TDK: B84143V0016R229 +B84143Q0006R229 | TDK: B84143V0025R229 +B84143Q0008R229 | TDK: B84143V0033R229 +B84143Q0008R229 | TDK: B84143V0050R229 +B84143Q0010R229 | TDK: B84143V0066R229 +B84143Q0010R229 | TDK: B84143V0095R229 +B84143Q0012R229 | TDK: B84143V0162S229 +B84143Q0014R229 | TDK: B84143V0230S229 +B84143Q0016R229 | TDK: B84143V0390S229 +B84143Q0018R229
| Frame |  |  |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 |  |  | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115 | 230/115
[5 empty] | Part number -> | [8 empty] | Select aR Fuses | [39 empty] | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | UN = 440....480 V | [42 empty] | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | Fuses are not included. | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C | ≤40 °C
UN = 400 V (380, 400, 415 V)
ACQ580-31-09A5-4 | R3 | 8 |  |  |  | 3 | [10 empty] | 3 | [14 empty] | 3 | [22 empty] | 3 | [19 empty] | 3 | [27 empty] | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACQ580-31-12A7-4 | R3 | 10 |  |  |  | 3 | [10 empty] | 3 | [14 empty] | 3 | [22 empty] | 3 | [21 empty] | 3 | [25 empty] | x |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACQ580-31-018A-4 | R3 | 14 |  |  |  |  | 3 | [10 empty] | 3 | [13 empty] | 3 | [24 empty] | 3 | [21 empty] | 3 | [23 empty] | x |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 | [19 empty] | 1 | [9 empty] | 1 | [10 empty] | 1
ACQ580-31-026A-4 | R3 | 20 | [5 empty] | 3 | [9 empty] | 3 | [14 empty] | 3 | [23 empty] | 3 | [23 empty] | 3 | [21 empty] | x |  |  | 1 |  |  |  |  | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1 | [10 empty] | 1 | [10 empty] | 1
ACQ580-31-033A-4 | R6 | 27 | [6 empty] | 3 | [9 empty] | 3 | [14 empty] | 3 | [25 empty] | 3 | [22 empty] | 3 | [19 empty] | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1 | [9 empty] | 1 | [11 empty] | 1
ACQ580-31-039A-4 | R6 | 33 | [7 empty] | 3 | [8 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [24 empty] | 3 | [17 empty] | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1 | [9 empty] | 1 | [12 empty] | 1
ACQ580-31-046A-4 | R6 | 40 | [8 empty] | 3 | [8 empty] | 3 | [16 empty] | 3 | [22 empty] | 3 | [26 empty] | 3 | [15 empty] | x |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1 | [10 empty] | 1 | [11 empty] | 1
ACQ580-31-062A-4 | R6 | 51 | [9 empty] | 3 | [8 empty] | 3 | [15 empty] | 3 | [25 empty] | 3 | [35 empty] | 3 |  |  |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1
ACQ580-31-073A-4 | R6 | 63 | [10 empty] | 3 | [8 empty] | 3 | [15 empty] | 3 | [24 empty] | 3 | [35 empty] | 3 |  |  |  | x |  |  |  | 1 | [5 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [16 empty] | 1 | [10 empty] | 1 | [11 empty] | 1
ACQ580-31-088A-4 | R6 | 76 | [10 empty] | 3 | [8 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [36 empty] | 3 |  |  | x |  |  |  | 1 | [6 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [15 empty] | 1 | [11 empty] | 1 | [11 empty] | 1
ACQ580-31-106A-4 | R8 | 94 | [11 empty] | x | [8 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [38 empty] | x | [10 empty] | 1 | [8 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACQ580-31-145A-4 | R8 | 128 | [11 empty] | x | [9 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [37 empty] | x | [10 empty] | 1 | [8 empty] | 1 | [40 empty] | 1 | [10 empty] | 1
ACQ580-31-169A-4 | R8 | 154 | [11 empty] | x | [11 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [36 empty] | x | [11 empty] | 1 | [9 empty] | 1 | [39 empty] | 1 | [9 empty] | 1
ACQ580-31-206A-4 | R8 | 188 | [11 empty] | x | [12 empty] | 3 | [15 empty] | 3 | [23 empty] | 3 | [35 empty] | x | [11 empty] | 1 | [9 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACQ580-34-246A-4 | R11 | 212 | [11 empty] | x | [33 empty] | 3 | [19 empty] | 3 | [34 empty] | x | [11 empty] | 1 | [9 empty] | 1
ACQ580-34-293A-4 | R11 | 257 | [11 empty] | x | [34 empty] | 3 | [19 empty] | 3 | [33 empty] | x | [12 empty] | 1 | [8 empty] | 1
ACQ580-34-365A-4 | R11 | 321 | [11 empty] | x | [35 empty] | 3 | [19 empty] | 3 | [32 empty] | x | [12 empty] | 1 | [9 empty] | 1
ACQ580-34-442A-4 | R11 | 401 | [11 empty] | x | [36 empty] | 3 | [19 empty] | 3 | [31 empty] | x | [13 empty] | 1 | [8 empty] | 1
ACQ580-34-505A-4 | R11 | 401 | [11 empty] | x | [37 empty] | 3 | [19 empty] | 3 | [30 empty] | x | [13 empty] | 1 | [8 empty] | 1
ACQ580-34-585A-4 | R11 | 505 | [11 empty] | x | [38 empty] | 3 | [19 empty] | 3 | [29 empty] | x | [13 empty] | 1 | [8 empty] | 1
ACQ580-34-650A-4 | R11 | 569 | [11 empty] | x | [38 empty] | 3 | [19 empty] | 3 | [29 empty] | x | [14 empty] | 1 | [8 empty] | 1
UN = 480 V (440, 460, 480 V) -NEC Ratings-
ACQ580-31-07A6-4 | R3 | 7 | [12 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [19 empty] | 3 | [34 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1
ACQ580-31-012A-4 | R3 | 9 | [13 empty] | 3 | [14 empty] | 3 | [23 empty] | 3 | [21 empty] | 3 | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1
ACQ580-31-014A-4 | R3 | 12 | [14 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [21 empty] | 3 | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 | [19 empty] | 1
ACQ580-31-023A-4 | R3 | 17 | [14 empty] | 3 | [14 empty] | 3 | [24 empty] | 3 | [23 empty] | 3 | [29 empty] | 1 | [8 empty] | 1 | [8 empty] | 1 | [18 empty] | 1
ACQ580-31-027A-4 | R6 | 24 | [16 empty] | 3 | [15 empty] | 3 | [24 empty] | 3 | [22 empty] | 3 | [28 empty] | 1 | [8 empty] | 1 | [9 empty] | 1 | [17 empty] | 1
ACQ580-31-034A-4 | R6 | 29 | [16 empty] | 3 | [15 empty] | 3 | [24 empty] | 3 | [24 empty] | 3 | [26 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACQ580-31-044A-4 | R6 | 34 | [16 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [26 empty] | 3 | [24 empty] | 1 | [8 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACQ580-31-052A-4 | R6 | 44 | [17 empty] | 3 | [16 empty] | 3 | [25 empty] | 3 | [35 empty] | 3 | [13 empty] | 1 | [7 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACQ580-31-065A-4 | R6 | 54 | [18 empty] | 3 | [17 empty] | 3 | [23 empty] | 3 | [35 empty] | 3 | [13 empty] | 1 | [8 empty] | 1 | [10 empty] | 1 | [16 empty] | 1
ACQ580-31-077A-4 | R6 | 66 | [19 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [36 empty] | 3 | [13 empty] | 1 | [7 empty] | 1 | [11 empty] | 1 | [15 empty] | 1
ACQ580-31-096A-4 | R8 | 82 | [20 empty] | 3 | [16 empty] | 3 | [23 empty] | 3 | [48 empty] | 1 | 1 | [8 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACQ580-31-124A-4 | R8 | 111 | [22 empty] | 3 | [18 empty] | 3 | [20 empty] | 3 | [48 empty] | 1 | [8 empty] | 1 | [40 empty] | 1 | [10 empty] | 1
ACQ580-31-156A-4 | R8 | 134 | [25 empty] | 3 | [16 empty] | 3 | [20 empty] | 3 | [47 empty] | 1 | [8 empty] | 1 | [41 empty] | 1 | [9 empty] | 1
ACQ580-31-180A-4 | R8 | 163 | [26 empty] | 3 | [16 empty] | 3 | [20 empty] | 3 | [47 empty] | 1 | [9 empty] | 1 | [39 empty] | 1 | [10 empty] | 1
ACQ580-34-240A-4 | R11 | 209 | [44 empty] | 3 | [20 empty] | 3 | [46 empty] | 1 | [9 empty] | 1
ACQ580-34-302A-4 | R11 | 258 | [45 empty] | 3 | [20 empty] | 3 | [46 empty] | 1 | [8 empty] | 1
ACQ580-34-361A-4 | R11 | 307 | [46 empty] | 3 | [20 empty] | 3 | [45 empty] | 1 | [9 empty] | 1
ACQ580-34-414A-4 | R11 | 363 | [47 empty] | 3 | [20 empty] | 3 | [45 empty] | 1 | [8 empty] | 1
ACQ580-34-477A-4 | R11 | 418 | [48 empty] | 3 | [20 empty] | 3 | [44 empty] | 1 | [8 empty] | 1