Specification Toolbox 2.0

ABB i-bus KNX in Office Buildings

Functional Specification – Premium

Table of Contents

1.	General Requirements	4

1.1.	System Description	5

1.2.	Bus System Control Devices	5

1.3.	Control Panel (Distribution Board)	5

1.4.	General Controlling Concept	5

1.5.	KNX Control Elements	5

2.	Office Building – Premium Configuration	6

2.1.	Lighting Control	6

2.2.	HVAC Control	8

2.3.	Blind/Curtain/Shutter Control	8

2.4.	KNX Bus Control Elements	8

2.5.	Touch Screen Device	8

2.6.	Metering	9

3.	Control Devices – System Components	10

3.1.	KNX Power Supply with Enhanced Diagnostics (320 mA/640 mA)	10

3.2.	Line Coupler	11

3.3.	IP Router	12

3.4.	IP Router Advanced	13

4.	Control Devices – Switching and Dimming	14

4.1.	Switch Actuator 16/20 AX	14

4.2.	Switch Actuator 16/20 AX with Current Detection	15

4.3.	Universal Dim Actuator	16

4.4.	Switch/Dim Actuator 16 A	18

4.5.	DALI Gateway with Group Control	19

4.6.	DALI Light Controller	20

4.7.	Light Sensor	21

5.	Control Devices – Curtain and Blind Control	22

5.1.	Blind/Curtain/Shutter Control Actuator with Travel Detection and Manual Operation	22

5.2.	Shutter Control Unit	23

5.3.	KNX Weather System	24

5.4.	KNX Weather Station	25

6.	Control Devices – HVAC	26

6.1.	Room Thermostat Fan Coil with Display	26

6.2.	Standard Room Thermostat with Display	27

6.3.	Multi-Function Room Thermostat with Display and Control Elements	29

6.4.	Valve Drive Actuator	31

6.5.	Thermoelectric Valve Drive	32

6.6.	Blower Actuator 6 A	33

6.7.	Fan Coil Actuator PWM	34

6.8.	Fan Coil Actuator 0-10V	35

6.9.	Air Quality Sensor (CO2 Sensor) for Fan Control	36

7.	Control Devices – Operation	37

7.1.	Binary Input Contact Scanning	37

7.2.	Multi-Function Control Element with Rockers	38

7.3.	Touch Screen Device	39

7.4.	Presence Detector	40

7.5.	Presence Detector Premium	41

7.6.	Radio Time Switch	43

8.	Control Devices – Metering and Load Management	44

8.1.	Meter Interface Module	44

8.2.	Energy Actuator	45

8.3.	Energy Module	47

# General Requirements

The Intelligent Building Control System shall be designed and developed in accordance with the multi-vendor KNX standard and also in conformity to the following standards:

European Standard (CENELEC EN 50090 and CEN EN 13321-1)

International Standard (ISO/IEC 14543-3)

Chinese Standard (GB/T 20965)

US Standard (ANSI/ASHRAE 135)

Systems which are single vendor based and run on proprietary protocols shall not be accepted. The system shall ensure that devices from different manufacturers are interoperable and compatible thus providing a future proof and flexible installation.

The system should cover commercial control requirements of one or more applications, such as lighting, HVAC, shading, etc.

The system shall be completely decentralized and programmable. Each device will have its own intelligence. 
The parameters are configured using PC or notebook computer located anywhere in the system topology. Systems using centralized controllers or processors will not be accepted. In case of power failure all the configuration and status information have to be stored and retained in a non-volatile storage. This data shall be pushed back to the device once electrical current is back. System with additional built-in or external battery that needs to be changed periodically for information storage shall not be accepted.

The communication cable that links all the devices shall have data and power residing on the same medium. It shall also be possible to lay the cable along the power mains. Systems requiring different communication cables for signal transmission and control power between the devices are not acceptable.

The bus connection terminal of all the devices should have 4 bus connection possibilities for looping or branching of bus cable. The bus cable shall be laid in the building in all possible configurations, i.e. linear, star or tree architecture similar to the power mains. Systems requiring fixed wiring configurations shall not be acceptable. It is thereby possible to disconnect the devices without interrupting the bus line. Systems requiring special tools for crimping, lagging or special installation connectors, e.g. RJ45 bus connections, shall not be acceptable.

Online programming of any device of the system should be possible without affecting the other devices on the system as well as offline programming prior to dispatching of the material to site. In the event of failure of a device in one line, only the control functions controlled by that device shall be affected and all other devices shall continue to operate normally.

Each device shall operate via the 21…30 V DC made available on the KNX bus line. The power supply unit should deliver a 640 mA/320 mA/160 mA version depending upon the bus network density.

The system shall communicate through CSMA/CA with parity checks in order to avoid collision in the bus thereby increasing the system flexibility and bandwidth allocation. Systems which work on polling or master-slave configurations shall not be accepted.

## System Description

The Intelligent Building Control system shall be programmed to provide the following applications:

The control system will provide the aesthetic and energy management control of the lighting in each of the designated areas. This includes switching and dimming of lighting in combination with constant light control where applicable. Additionally, lighting shall be controlled dependent on outside brightness level in combination with automatic shading.

Automatic shutter, blind and curtatin control to provide shading dependent on sun position

HVAC control

Metering and load control

Operation via pre-defined scenarios and time schedules

The system will be fully configurable and software based. No centralized processors or memory storage devices shall be required. It shall be able to interface to BMS by mode of high level interface, such as OPC server. The system shall provide the flexibility to ensure that it can be easily altered or added with new functions in the future without the need of reconfiguration or rewiring.

## Bus System Control Devices

Dedicated integrated KNX controllers shall be provided in individual rooms for controlling lighting, HVAC, blinds, etc. The controllers shall have decentralized intelligence and shall be independent of any centralized controllers/software. For each application, such as lighting/blinds/HVAC control, dedicated controllers or channels need to be used.

## Control Panel (Distribution Board)

There shall be a dedicated Control Panel for the control of one storey, for example. The control panel shall house the system devices and the related control equipment and protection devices depending on the number of circuits being controlled. This is to ensure that the power wiring between the control panel and the controlled loads is kept short.

## General Controlling Concept

Manual operation shall be reduced to a minimum. All major functions like lighting, shading and HVAC control shall be operated automatically by the bus system. Nevertheless, local and manual operation shall be considered wherever a manual override of the automatic control is required. This shall be possible via a local operation with bus control elements and/or touch panels located at operation points where a huge number of loads have to be controlled. 
To allow a quick and comfortable operation according to several use cases, predefined lighting/blinds/HVAC scenes shall be planned to allow an efficient control for the staff. These shall be accessible via rockers of the bus control elements or via a touch panel, where applicable. Furthermore, to reduce energy consumption in low frequent times (e.g. at night), presence detectors shall be used to provide the full lighting level only if it is needed. Time-scheduled operation shall be considered as well, wherever applicable.

A control of the building shall also be possible by centralized PC visualization software connectable to the bus (e.g. via LAN interface) allowing a comprehensive control of the building. It shall also feature a predefined time-based control for setting the lighting/blinds/HVAC system to predefined states dependent on the daytime. Furthermore, a local operation by the operator shall be possible by graphical display, e.g. showing the entire building based on floor plans or individual room plans (optional).

## KNX Control Elements

KNX control elements shall be used to control various loads and scenes in the building. They shall include a bus coupler as part of the delivery, if applicable. The control elements shall be appropriately designed and located wherever necessary. All control elements shall be connected to the bus system. Furthermore, a touch screen control device connected to the bus system shall be available in order to allow the control of the building from a single control station.

# Office Building – Premium Configuration

## Lighting Control

The bus-based lighting control solution shall allow the following control types:

### Switching of Lighting

Switchable lighting circuits shall be controlled via a switch actuator consisting of relays to switch several channels on/off. The switch actuator shall allow status feedback messages in order to monitor the response of the connected relay.

Specialized switch actuators with current detection shall be used to monitor the electrical state of a connected lighting load. By means of current threshold values, alarm messages shall be triggered if a certain current value is exceeded or undercut.

### Dimming of Lighting

Dimmable lighting circuits shall be controlled via appropriate actuators/gateways. There shall be three different dimming possibilities dependent on the used actuator which is connected to the bus system:

Universal dim actuators: Load is directly connected to the dimmer; incandescent lamps, low voltage halogen lamps (on conventional or electronic transformers) or 230 V halogen lamps can be operated. Outputs automatically recognize the connected load. Additionally, the operating mode can be selected manually.

1…10 V switch/dim actuator: Dimming control is achieved via 1…10 V ballasts connected to the appropriate outputs of the switch/dim actuator. Switching on/off the light is done via floating contacts controlling the mains power supply of the 1…10 V ballast.

DALI Gateway: The dimming control system shall be based on DALI (Digital Addressable Lighting Interface) according to the technical standard IEC 62 386 in combination with KNX. To control DALI equipment, such as ballasts, transformers, LED converters, etc., a KNX/DALI Gateway shall be used. DALI allows the addressing of 64 ballasts which can be freely assigned to 16 DALI lighting control groups. The DALI control line can be installed together with the mains cable (e.g. by using a 5 wire standard cable). Functionalities achieved by DALI: light scenes, day light control, feedback regarding the connected DALI equipment (e.g. lamp or ballast failure), light scenes, etc.

### Daylight-Dependent Control

A daylight-dependent control uses the available daylight to save operating and energy costs. To implement the control, an outside brightness sensor is mounted at the exterior of the building measuring the outside brightness value. The brightness sensor shall be a part of the weather system.

After a certain outside brightness value is reached, lighting circuits shall be switched off as required by the operator, according to definable threshold values. In case of dimmable lighting circuits the lighting can be dimmed to a predefined lower brightness value in order to save energy.

### Constant Light Control

Optimum lighting conditions in buildings can be realized economically with the constant lighting control of the bus system which shall be implemented in the office areas. It can be used to regulate the actual brightness in the rooms. The brightness in the room is measured and the main causes of interference are detected, e.g. darkness due to shutters or partial shading due to buildings directly opposite the window. An almost perfect level of brightness is therefore achieved in the room without external influences.

Therefore an internal brightness sensor mountable at the ceiling of the appropriate room along with dimmable lighting circuits is required.

A manual override of the constant lighting control shall be available, if applicable, via appropriate bus control elements.

### Time-Based and Occupancy-Dependent Control

For further automation, the lighting shall be controlled via predefined time schedules according to the usage of the building. These shall be defined via touch panels, visualization or a Building Management System. Lighting circuits can be either switched off, or in case of dimmable circuits, set to a specified light value (e.g. 30 %) to allow a basic lighting coverage.

An occupancy-dependent control is a control form that uses motion or presence detectors. It detects the presence of persons in the building or in external areas and switches the corresponding lighting on or off. If dimmable lighting circuits are used, the light value can be reduced to a certain level (e.g. 30 %), if no presence is detected. Presence detection can be also combined with constant lighting control to further increase energy efficient lighting.

## HVAC Control

KNX shall be used for room-oriented temperature control or individual room temperature control. By detecting the actual temperature value and specifying a respective temperature setpoint with a control algorithm, the thermostat sends a control value to the actuator. This actuator controls a heating or cooling unit that changes the room temperature. 
The prerequisite is a water-based heating and cooling system. The following control types shall be available:

Heating radiator control with electrothermal or electromotor valve drive

Fan coil unit control

Blower/Fans

The room temperature controller shall be fully integrated into the Intelligent Building Control system in order to control the shutter/blind system as well. If a room is unoccupied, the blinds can be driven down in cooling operation to prevent heating of the room due to sun radiance. In heating operation (e.g. during wintertime) the blinds shall be driven up in order to support a cost-efficient heating of the room.

The HVAC control system shall be interfaced to presence detectors, if applicable. Therefore, the presence detectors used for controlling lighting shall control the heating/cooling setpoint as well. If the room is not occupied, the setpoint value can be decreased (heating operation) in order to reduce the energy consumption.

Windows shall be equipped with magnetic reed contacts in order to set the heating/cooling control system to a standby mode when a window is opened. In the standby mode the setpoint is decreased in heating operation, during cooling operation the setpoint shall be increased.

## Blind/Curtain/Shutter Control

Blind and curtain control shall be possible via the bus control elements. Motors are interfaced to the appropriate actuators. Furthermore, the integration into scenes shall be possible. The system shall also be capable of integrating values of the Weather Station in order to allow automatic control dependent on outside brightness level/sun position. Additionally, a reaction to wind alarms shall be integrated. Furthermore, an interaction with the room temperature controller shall be possible.

There shall be an automatic control mode which can be enabled, e.g. via a superordinate visualization system/BMS/touch screen device. The control mode allows automated shading dependent on the current sun position and shall furthermore include the functions of anti-glare protection and daylight redirection. Shadow objects in front of facades shall be taken also into consideration. For this operation mode, a KNX Weather Station as defined in 5.4 is required allowing to connect separate outside brighntess sensors for each facade direction. A manual override shall be available via bus control elements or appropriate touch panels.

## KNX Bus Control Elements

Bus control elements shall be used to control various building applications , such as lighting control including dimming, curtain and blind control, room temperature control. The local operation with bus control elements shall be only applicable if a manual override of the automatic control is required.

## Touch Screen Device

- The touch screen device shall provide a comprehensive control of the building applications. Therefore, it shall have a capacitive and colored touch screen TFT display allowing the control of lighting, blinds/curtains and further facilities, as well as displaying the status of weather values, for example. The touch screen device shall also be used to define time-based scenarios which can be easily adjusted by the end user directly on the device. A presence simulation which records the typical use of the building’s functions shall be also available.

## Metering

The Intelligent Building Control system shall be capable of providing metering values to any displaying facility in order to have a transparent view on energy consumption in the building. Metering values shall be transmitted for further evaluation to the visualization system or the Building Management System via proper Gateway.

In order to measure the power consumption directly at the switched circuits, for enhancing transparency, specialized switch actuators with an inbuilt metering feature for each channel shall be used.

If the measurement of energy consumption is required, e.g. for the main feeder circuits, there shall also be the possibility to connect meters via a proper IR Gateway/interface to the bus system. This is applicable for circuits with higher rated currents. If a low current rating is sufficient, an energy module directly connected to the bus system shall be used.

# Control Devices – System Components

## KNX Power Supply with Enhanced Diagnostics (320 mA/640 mA)

Produces and monitors the KNX system voltage

With diagnostic function via KNX or ABB i-bus® Tool

The voltage output is short-circuit- and overload-proof. The LEDs indicate the bus current consumption and the status of the line or device.

Diagnostic functions via KNX: Bus voltage UN, bus current I, bus current I > rated current IN, overload I > Imax, trigger bus reset

Supply voltage: US 85…265 V AC, 50/60 Hz

KNX voltage output: 1 line with integrated choke

Rated voltage: UN 30 V DC +1/-2 V, SELV

Power consumption:

< 30 W (320 mA)

< 55 W (640 mA)

Nominal power loss:

< 2.5 W (320 mA)

< 4 W (640 mA)

Output voltage: 30 V DC +1/-2 V, SELV

Nominal current: 320 mA/640 mA, short-circuit-proof

Sustained short-circuit current:

< 0.8 A (320 mA)

< 1.4 A (640 mA)

Mains failure back-up time: 200 ms

Rated current: IN 320 mA or 640 mA

Connection:

Bus connection: Bus connection terminal

Supply connection: Screw terminals

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 modules at 18 mm

Manufacturer: ABB

Product type (dependent on current): SV/S 30.320.2.1, SV/S 30.640.5.1

## Line Coupler

The Line Coupler electrically isolates lines/areas from one another. With an activated filter table, it only allows data telegrams which are intended for bus devices on other lines. The device can be parameterized as a line or area coupler as well as a line repeater using ETS software. With ETS version 4.1.2 or higher, the entire group address range (main group 0…13 and 14…31) can be filtered.

Operating and display elements:

LED, green: ON

LED, yellow: Main line

LED, yellow: Line

Connection:

Main line: Bus connection terminal

Line: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 2 modules at 18 mm

Manufacturer: ABB

Product type: LK/S 4.2

## IP Router

The IP Router connects the KNX bus with the Ethernet network. The device uses the KNXnet/IP protocol for communication (Routing and Tunneling). It can be used as a fast line and area coupler and can utilize the local network (LAN) for fast exchange of telegrams between the lines/areas. KNX devices can be programmed via the LAN using ETS. The IP address can be fixed or can be received from a DHCP server. The power supply range is from 10…30 V DC.

Supply voltage: 10...30 V DC

Display elements:

LED green: Operating mode display

LED yellow: Network connection indicator

LED yellow: KNX telegram traffic indicator

Connection:

Plug-in terminal

RJ45 socket

Bus connection terminal

Interfaces:

1 x KNX

1 x LAN

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 2 modules at 18 mm

Manufacturer: ABB

Product type: IPR/S 2.1

## IP Router Advanced

The IP Interface connects the KNX bus with the Ethernet network.The device uses the KNXnet/IP protocol for communication (Routing and Tunneling).

Auxiliary voltage: 12 ... 30 V DC (+10% / -15%) or PoE (IEEE 802.3 af class 1)

Relocated RJ45 socket for better radius of bend

KNX devices can be programmed via the LAN using ETS

Visualizations can send and receive telegrams via the tunneling servers

The IP address can be fix or can be received from a DHCP server

5 tunneling servers available

8k filter table available (main groups 0...31)

Standard multicast communication can be switched to unicast. In this case up to 10 ABB IPR/S3.1.1 can communicate via unicast

Supports bus monitor and group monitor

Diagnosis and commissioning tool available (incl. firmware update)

Power dissipation: Max. 1,8 W

Display elements:

LED green: Operating mode display

LED yellow: LAN/LINK

LED yellow: KNX telegram

Housing: Halogen free

Connections:

LAN: Plug-in terminal, RJ45 socket

KNX: Bus connection terminal

Interfaces:

1 x KNX

1 x LAN

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Mounting position: As required

Width: 2 modules at 18 mm

Manufacturer: ABB

Product type: IPR/S 3.1.1

# Control Devices – Switching and Dimming

## Switch Actuator 16/20 AX

Uses potential-free contacts to independently switch 2, 4, 8 or 12 electrical loads via KNX

Manual operation and display of the switching status. No separate voltage supply necessary. Especially suitable for switching from loads with high surge current, such as lighting with compensatory capacitor or fluorescent lighting loads according to IEC/EN 60 669.

With only one application program the following functions for each output can be set separately:

Current recognition, current value sending and reaction to current threshold values

Time functions, on/off delay

Staircase lighting function with preliminary warning and changeable staircase lighting time

Recall scenes/presets over 8-bit/1-bit commands

Logic functions AND, OR, XOR

Status response

Forced control and safety function

Reaction to threshold values

Control of electrothermal valve drives (continuous controller)

Selection of default position on bus voltage failure and recovery

Inversion of outputs

Parameterization of single outputs can be exchanged or copied

Outputs: 2-12 potential-free floating contacts

Rated current: 16/20 AX - C-Load (50/60 Hz)

Switching capacity:

According to IEC/EN 60 947-4-1: 
16/20 A/AC1 (16 A actuator); 16 A/AC3 (on 230/400 V AC, 16 A actuator)

According to IEC/EN 60 669: 
16/20 AX (16 A actuator), max. capacitive load 200 μF

Operation: Actuating levers for displaying the switch position and manual operation

Connection:

Load side: Screw terminals with combination head screws for lines, 0.2…6.0 mm² unifilar

KNX: Screwless bus connector

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 1 module at 18 mm per output channel

Manufacturer: ABB

Product type (dependent on number of channels): SA/S 2.16.5.1, SA/S 4.16.5.1, SA/S 8.16.5.1, SA/S 12.16.5.1

## Switch Actuator 16/20 AX with Current Detection

Uses potential-free contacts to independently switch 2, 4, 8 or 12 electrical loads via KNX

With integrated load current detection and without separate supply voltage

Manual operation and display of the switching status. Especially suitable for switching from loads with high surge current, such as lighting with compensatory capacitor or fluorescent lighting loads according to IEC/EN 60 669.

With only one application program the following functions for each output can be set separately:

Current recognition, current value sending and reaction to current threshold values

Detected current can be sent on KNX via 2-byte (counter value) or 4-byte (float value) object

Time functions, on/off delay

Staircase lighting function with preliminary warning and changeable staircase lighting time

Recall scenes/presets over 8-bit/1-bit commands

Logic functions AND, OR, XOR

Status response

Forced control and safety function

Reaction to threshold values

Control of electrothermal valve drives (continuous controller)

Selection of default position on bus voltage failure and recovery

Inversion of outputs

Parameterization of single outputs can be exchanged or copied

Outputs: 2-12 potential-free floating contacts

Rated current: 16/20 AX - C-Load (50/60 Hz)

Switching capacity:

According to IEC/EN 60 947-4-1: 
16/20 A/AC1 (16 A actuator); 16 A/AC3 (on 230/400 V AC, 16 A actuator)

According to IEC/EN 60 669: 
16/20 AX (16 A actuator), max. capacitive load 200 μF

Operation: Actuating levers for displaying the switch position and manual operation

Connection:

Load side: Screw terminals with combination head screws for lines, 0.2…6.0 mm² unifilar

KNX: Screwless bus connector

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 1 module at 18 mm per output channel

Manufacturer: ABB

Product type (dependent on number of channels): SA/S 2.16.6.1, SA/S 4.16.6.1, SA/S 8.16.6.1, SA/S 12.16.6.1

## Universal Dim Actuator

KNX multichannel universal dimming actuator for controlling incandescent lamps, 230 V incandescent halogen lamps, low-voltage halogen lamps with conventional or electronic transformers, and dimmable energy-saving halogen lamps

For dimmable retrofit LED lamps (LEDi)

Parallel switching of channels for increasing the loads through wire bridges possible

The outputs can be switched parallel in any combination

Outputs automatically recognize the connected load

In addition, the operating mode can be selected manually, with local operation.

Status indication via LED

The following applications are provided for the outputs:

Switching

Dimming

Value

Error message

Enable object

Light scene actuator

Sequence actuator

Staircase lighting

Delay

Preset

Cyclical telegram

Flashing

Logics (AND, OR, XOR, XNOR, NAND, NOR)

GATE

Min/max value transducers

Set value/hysteresis

PWM inverter

Priority

Power supply: 230 V AC ± 10 %, 50/60 Hz

Connection:

Outputs: Screw terminals, 0.2…6.0 mm²

Multiple-wire: 0.5…2.5 mm²

KNX: Bus connection terminal control element: Manual operation of ON brighter/Off darker and channel selection

Display elements: Outputs status indication via LED

Outputs: 4 or 6

Rated power: Max. 210 W/VA, 315 W/VA, 600 W/VA per channel (dependent on used dim actuator type)

Operating temperature range: -5° C to + 45° C

Protection: Electronic short-circuit and overload protection

Mounting: 35 mm mounting rail, IEC/EN 60715

Width: 8 or 12 modules at 18 mm (dependent on rated power)

Manufacturer: ABB

Prodcut type (dependent on number of channels and rated power): 
6197/12-101-500, 6197/13-101-500, 6197/14-101-500, 6197/15-101-500

## Switch/Dim Actuator 16 A

Device for switching and dimming of 2/4/8 independent groups of luminaries with electronic ballasts, dimmers or transformers with 1…10 V control input. The dimming control per outputs carried out with two control wires. Maximum control load per channel is 100 mA. The Switch/Dim Actuator needs only KNX bus voltage for normal function. 
With 2/4/8 potential-free relays the supply voltage of the ballasts and consequently the luminaries can be switched on and off over KNX or manually without any auxiliary supply. Contact position is displayed.

The following functions can be set separately for each channel:

Switching and dimming of lighting

Feedback of switching state and brightness value

Different adjustable dimming speeds for dimming and setting brightness

Adjustable upper and lower dimming limits

Recall and set of up to 18 light scenes (8-bit commands) per channel

4 presets (1-bit commands) per channel

Integration in constant lighting control (“slave mode”)

Forced operation with higher priority

Staircase lighting function with adjustable staircase lighting time

Warning before switching off

Disable function to prevent unauthorized operation

Characteristic curve adjustment to adapt ballast brightness characteristic

Outputs (channels):

2/4/8, ﬂoating contacts for switching power supply of ballasts

2/4/8, control channel 1…10 V passive

Nominal voltage: 230/440 V AC

Switching capacity:

- 16 A/AC1 (ohmic load, IEC/EN 60 947)

- 10 AX (fluorescent lighting load, IEC/EN 60 669)

Control current max.: 100 mA per channel

Connection:

Outputs: Screw terminals

Bus connection: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4/6/8 modules at 18 mm

Manufacturer: ABB

Product type (dependent on number of channels): SD/S 2.16.1, SD/S 4.16.1, SD/S 8.16.1

## DALI Gateway with Group Control

The group-oriented KNX DALI Gateway (DALI = Digital Addressable Lighting Interface) is used for controlling DALI equipment (ballasts, transformers, LED converters, etc. using the DALI interface to IEC/EN 62 386/60 929) via KNX.

Up to 64 DALI devices can be connected to a DALI output. The 64 DALI devices can be individually addressed and allocated as required in up to 16 lighting groups. Overlapping groups are possible. Control using KNX is implemented exclusively via 16 lighting groups. Furthermore, setting of 14 light scenes is possible which can be recalled or stored via 8-bit or 1-bit scene telegrams. The lighting group can be integrated into a lighting control using slave mode. Furthermore, a staircase lighting function and a sequencer mode are available for the programming of running lights and color effects without additional logic or timer modules.

The 64 DALI devices of the DALI output can also be read or controlled together in broadcast mode. Information relating to a lamp and ballast fault is available individually for a lamp group or for a DALI device. Error messages can be inhibited on the KNX allowing the Gateway to operate together with emergency lighting systems, which disconnect the DALI from the Gateway during emergency lighting tests.

Programming of the DG/S 1.16.1 is implemented with the Engineering Tool Software (ETS).

Manual switching of all DALI devices with a test button on the device is possible.

Additionally, the correct operating voltage of the Gateway and the fault state of the DALI devices are indicated via two status LEDs. The brightness value (0…100 %) of the ballast (power-on level) after ballast operating voltage recovery is programmable.

The DALI address assignment is implemented automatically on the Gateway. It can however be suppressed by a parameter in the application program.

Readdressing of the DALI device and the assignment of the 64 DALI devices into 16 lighting groups is implemented in an ETS independent software tool (ABB i-bus® Tool), so that for example, a facility manager without ETS knowledge is capable of exchanging and reassigning DALI devices, should maintenance be required. Furthermore, the fault states of the individual DALI devices and/or lighting groups are represented graphically with this tool.

The DALI power source for the 64 DALI devices is integrated into the Gateway.

Output DALI: Output for max. 64 DALI devices

Operating voltage: 85…265 V AC, 45…65 Hz, 110…240 V DC

Connection:

Outputs: Screw terminal

Bus connection: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 modules at 18 mm

Manufacturer: ABB

Product type: DG/S 1.16.1

## DALI Light Controller

Device for switching and dimming of 16 independent lighting groups with electronic DALI ballasts (DALI = Digital Addressable Lighting Interface to IEC/EN 62 386/60 929). The device can be used not just as a KNX DALI Gateway, but also as a Lighting Controller for constant lighting control in conjunction with a Light Sensor.

The device shall feature the following funtions:

64 DALI devices can be individually assigned to 16 lighting groups.

Switching and dimming of 16 lighting groups

8 of the 16 lighting groups can be applied individually in conjunction with a Light Sensor LF/U 2.1 to control the brightness in closed rooms.

Feedback of the switching state and the brightness per lighting group

Adjustable dimming speeds and brightness thresholds

Recall and store up to 14 light scenes (8-bit or 1-bit commands)

Slave operation of lighting groups controlled internally or externally via communication object

One offset brightness per control circuit, for example, to control a second lighting strip (slave) with differing brightness

Staircase lighting function (incl. warning and basis brightness)

Staircase lighting function can be combined with constant lighting control

DALI characteristic adjustment to adjust the DALI adjustment range to KNX

Signalling of lamp and ballast faults for a lighting group

Coded lamp and ballast fault information for each DALI device

Inhibit of error messages via KNX communication object

Fluorescent lamp burn-in function by lighting group

Fixed DALI ballast brightness after ballast voltage recovery (power-on level) can be adjusted.

Switching and dimming of 16 lighting groups via manual operation on the device

ETS-independent DALI commissioning tool used to assign DALI devices to desired lighting groups and to put the lighting control into operation. The error state of the DALI devices is also displayed with the tool.

Output: 1 DALI output with integrated DALI current source for max. 64 DALI devices

Operating voltage: 85…265 V AC, 45...65 Hz, 110...240 V DC

Inputs: 8, for light sensor

Control operating range:

Lighting control in 200...1,200 Lux range

Optimised typically for 500 Lux

Connection:

Screw terminals

Bus connection: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 6 modules at 18 mm

Manufacturer: ABB

Product type: DLR/S 8.16.1M

## Light Sensor

The light sensor is used to measure the brightness level in rooms. When combined with the light controller LR/S x.16.1 (x =2 or 4) the light sensor is used for constant light control. It is connected to the light controller with a twin-core MSR cable (SELV) and connection terminals (supplied). The light sensor is mounted in a standard installation box in the ceiling. A cover-plate (white) is supplied.

Type of protection: IP 20, IEC/EN 60 529

Mounting: Flush-mounted

Dimensions (Ø x H) 54 mm x 20 mm (without light pipe and cover)

Manufacturer: ABB

Product type: LF/U 2.1

# Control Devices – Curtain and Blind Control

## Blind/Curtain/Shutter Control Actuator with Travel Detection and Manual Operation

To control up to 2/4/8 independent blind and roller shutter drives or ventilation flaps (230 V AC)

Automatic travel detection via identification of end positions for each channel

Manual operation and displaying LEDs for each channel

Mutually mechanically interlocked outputs

Power supply only via KNX bus voltage

Software functionality:

Copy and change channels

Time-delayed switching of drives

Sending and switching delay after bus voltage recovery

Request status values via object

Limited number of telegrams

Preferred position on bus voltage failure, recovery, programming and reset

Disable/enable manual operation, deactivation by time

Travel detection (automatically or triggered by object) or manual setting of travel times

Safety function (3 x wind alarm, rain alarm, frost alarm with cyclical monitoring, block and forced operation) and reaction on reset of safety function

Direct commands available for UP/DOWN, STOP/Slat Adjustment

Move to position height/slat 0…255

Move to/set preset position 1…4 and 8-bit scene

Dead times of blind/shutter adjustable

Tensioning function available (for awning and flap adjustment)

Limited travel range (adjustable for direct and/or automatic commands)

Change on direction and delay times for drives adjustable

Automatic sun protection (position height/slat at sun) and sun tracking

Heating/cooling automatic with overheat control

Status messages: Height/slat 0…255, upper/lower end position, operability, automatic, status information (2-byte, including motor error), controlling ventilation flaps, switch mode with staircase lighting function

Outputs: 2/4/8 (2 relay outputs UP/DOWN for each channel)

Power consumption: < 250 mW

Operating voltage: 21…30 V DC

UN rated voltage: Max. 230 V AC, 45…65 Hz

IN rated current: Max. 6 A

Operating and displaying elements: 2 LEDs and push-buttons for each channel

Connection:

Outputs: Screw terminals (combination heads)

KNX: Screwless bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 or 8 modules at 18 mm

Manufacturer: ABB

Product type (dependent on number of channels): JRA/S 2.230.5.1, JRA/S 4.230.5.1, JRA/S 8.230.5.1

## Shutter Control Unit

The shutter control unit controls shutter actuators with dazzle protection and daylight control functions via the KNX. 
The sun’s position is constantly calculated and updated and then logically combined with a threshold value for the sun’s intensity, so that the venetian blind is only moved into the calculated position if the sun is really shining. The shadow effect of shade generators (e.g. buildings opposite) is taken into account. Up to 200 windows or window groups can be activated individually.

Connection: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 2 modules at 18 mm

Manufacturer: ABB

Product type (dependent on number of channels): JSB/S 1.1

## KNX Weather System

A weather system shall comprise of 2 units:

Weather Sensor: The Weather Sensor is used with the Weather Unit installed in KNX systems. The Weather Sensor allows the measurement of wind, brightness in three directions, rain incl. heating, temperatures, GPS-based date and time. The integrated power supply of the Weather Unit directly supplies power to the Weather Sensor.

Weather Unit: The Weather Sensor is connected to the Weather Unit. The Weather Unit collects and elaborates data from the Weather Sensor. The Weather Sensor provides data on wind speed, brightness in three directions, twilight, rain, temperature, as well as information about day/night, date and time. The Weather Sensor is directly supplied with power through the integrated power supply. A temperature sensor, type PT1000 is connectable.

The Weather Unit and the Weather Sensor are synchronized. An additional heat transformer is not required.

Blinds and sunblinds (awnings) can be retracted in the event of strong wind, or skylights and fanlights can be closed when it starts to rain.

Functions of the application program:

The weather system is time-synchronized, with options for summer/winter schedules.

The Weather Sensor records wind velocity (0...24.0 m/s), rain and brightness in three directions (left, right and center), (0...999 Lux), twilight, temperatures (-30...+ 50 °C), date and time (GPS radio receiver). It only functions in combination with the Weather Unit.

Measured value for the unit: Adjustable as 1-bit values or 2-byte values depending on the type

Threshold: 2 per sensor, each with upper and lower limit

Logical functions: AND/OR, inversion, each with 4 inputs

Memory: 4 memories, 24 values per memory can be stored according to FiFo principle

Weather Sensor:

Connection:

- 1, 2 power supply: 2-pole, 1 plug-in terminals each for solid conductors 0.4 to 1.5 mm Ø, color: black

- A, B data communication: 2-pole, 4 plug-in terminals each for solid conductors 0.6 to 0.8 mm Ø, 
color: white/yellow

Type of protection: IP 44, IEC/EN 60 529

Mounting: Wall mounted

Dimensions (H x W x D): 109 mm x 121 mm x 227 mm

Manufacturer: ABB

Product type: WES/A 3.1

Weather Unit:

Power supply: 85...265 V AC, 50/60 Hz, 110…240 V DC

Output: Voltage supply, data communication

Input: Temperature sensor (PT1000)

Connection: Screw terminals

Tightening torque: Max. 0.6 Nm

KNX: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 modules at 18 mm

Manufacturer: ABB

Product type: WZ/S 1.3.1.2

## KNX Weather Station

The Weather Station allows the detection and processing of four output signals. All conventional sensors, e.g. wind velocity sensor, wind direction sensor, rain sensor, rainfall sensor, brightness sensor, pyranometer (light intensity), twilight sensor, air pressure sensor, humidity sensor and temperature sensor, can be connected. An integrated power supply unit provides the sensors with 24 V DC voltage.

Functions of the application program:

Sensor output: Freely adjustable sensor output signals

Measured value: Can be represented as 1-bit, 1-byte, 2-byte or 4-byte value

Filtering: Generation of average via 4/16/64 measurements

Threshold value: 2 per input, each with upper and lower limit

Calculation: Comparison/arithmetic functions, generation of average

Logic functions: AND/OR, inversion, each with 4 inputs

Mains voltage: 85...265 V AC, 50/60 Hz

Inputs:

4 sensor signals in accordance with IEC/EN 60 381

Connection of sensor output signals: 0…1 V, 0…5 V, 0…10 V, 1…10 V, 0…20 mA, 4…20 mA, 
0…1,000 ohm, PT100, PT1000, KT/KTY, user-defined input and floating contact

Output:

1 auxiliary voltage output to supply the sensors

Nominal voltage: 24 V DC

Nominal current: 300 mA, over the entire mains voltage

Connection:

Screw terminals

Bus connection: Via bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 modules at 18 mm

Manufacturer: ABB

Product type: WS/S 4.1.1.2

# Control Devices – HVAC

## Room Thermostat Fan Coil with Display

KNX fan coil room temperature controller with display

Surface-mounted with integrated KNX bus coupler

LCD and 5 operating buttons

Used for single-room temperature control in heating and air-conditioning technology

The controller is a constant ambient temperature controller for fan convectors (fan coils) in 2-pipe and 4-pipe systems and conventional heating or cooling systems.

Adjusting range: 10…28 °C

The ambient temperature controller works in both heating and cooling mode.

The fan stage can also be selected manually via a button:

OFF/Stage

1/Stage

2/Stage

3/Automatic

Functions:

Comfort, standby, night, frost protection, and heat protection modes

Actuation of fan convectors (fan coil) in two-pipe and four-pipe systems

Actuation of two-point, PWN, or constantly regulated heating and cooling systems

Control and display elements:

One LCD for displaying temperatures, operating modes, fan stages, and fault messages

One push-button for manually turning the device on and off

One push-button for the selection of the fan stage:

OFF/Stage

1/Stage

2/Stage

3/Automatic

One push-button for increasing the set temperature

One push-button for reducing the set temperature

One push-button for switching the temperature unit between Celsius and Fahrenheit

Connections:

KNX line: DP screw/clamp terminals

Inputs:

Measuring range: Temperature: 0 °C to 50 °C

Type of protection: IP 20, IEC/EN 60 529

Temperature range: -5 °C to 45 °C

Mounting: Surface-mounting directly onto the wall and all common flush-mounted socket outlets

Dimensions (H x W x D): 81 mm x 81 mm x 20 mm

Manufacturer: ABB

Product type: 6138/11

## Standard Room Thermostat with Display

For single-room temperature control in heating and air-conditioning technology

With illuminated display for showing the actual room temperature and external actual-value default

Comfort, standby, night operation or frost/heat protection operation can be selected via KNX. The set values can be parameterized.

Display of the operation statuses with symbols

Display of the date and time is possible

The controller is a constant room temperature controller for ventilator convectors (fan coils) in 2-pipe and 4-pipe systems and conventional heating or cooling systems.

The fan stage can be switched manually or in automatic mode.

Setpoint adjustment using upper switch cover is possible.

Comfort/standby switchover using lower switch cover is possible.

The control output can optionally emit a continuous (PI control) or switching position signal (2-point or PWM).

Support of KNX functions through innovative LED-color concept (yellow = lighting, blue = blind, orange = RTC, magenta = scene and white = neutral/no function assigned) or standard illumination red/green

Color and function of the LED can be changed via ETS.

Removal protection is possible with screw-on installation.

With a maximum of 10 logic channels (logic gate, time delay, sequences, etc.). The logic functions of the channel can be freely selected.

For flush-mounted bus coupler

The following functions are provided for the application module:

Inputs: Switching, Continuous, Heating, Cooling, Time, Date

Outputs: Fan control, Light scene actuator, Sequence actuator, Staircase lighting, Delay, Preset, Cyclical telegram, Flashing, Logics (AND, OR, XOR, XNOR, NAND, NOR), GATE, Min/max value transducers, Set value/hysteresis, PWM inverter, Priority

Room thermostat:

Connection:

- Power supply: 10-pole multi-point connector

Control element: Switch contacts left/right for selecting setpoint and mode of operation

Display elements: LCD showing operation modes

Type of protection: IP 20, IEC/EN 60 529

Temperature range: -5 °C to 45 °C

Dimensions (L x W x D): 63 mm x 63 mm

Manufacturer: ABB

Product type: 6128/28

Bus coupler:

For combining the installation bus KNX and the different application modules

For installation in surface-mounted or flush-mounted boxes

Connection:

- KNX line: Bus connection terminal

Rated voltage: 24 V

Outputs:

- Rated current: 24 mA

Type of protection: IP 20, IEC/EN 60 529

Temperature range: -5 °C to 45 °C

Dimensions (L x W x D): 50 mm x 45 mm x 23 mm

Manufacturer: ABB

Product type: 6120/12

## Multi-Function Room Thermostat with Display and Control Elements

For single-room temperature control in heating and air-conditioning technology

With illuminated display for showing the actual room temperature

With external actual-value default

Comfort, standby, night operation or frost/heat protection operation can be selected via KNX. The set values can be parameterized.

Display of the operation statuses with symbols

Display of the date and time is possible

The controller is a constant room temperature controller for ventilator convectors (fan coils) in 2-pipe and 4-pipe systems and conventional heating or cooling systems.

The fan stage can be switched manually or in automatic mode.

Setpoint adjustment using upper switch cover is possible.

Comfort/standby switchover using lower switch cover is possible.

The control output can optionally emit a continuous (PI control) or switching position signal (2-point or PWM).

For transmitting switching, push-button, dimming and blind commands to KNX actuator

Support of KNX functions through innovative LED-color concept (yellow = lighting, blue = blind, orange = RTC, magenta = scene and white = neutral/no function assigned) or standard illumination red/green

Color and function of the LEDs can be changed via ETS.

Removal protection is possible with screw-on installation.

With a maximum of 10 logic channels (logic gate, time delay, sequences, etc.). The logic functions of the channel can be freely selected.

For flush-mounted bus coupler

The following functions are provided for the application module:

Inputs: LED

Outputs: Switching, Dimming, Blinds, Value, Push-button, Light scene extension unit, Step switch, Short/long operation, RTC operating mode switchover, Push-button switching, Push-button dimming, Push-button blind, Push-button value sender, Push-button step-type switch, Push-button multiple functions (max. 5 channels), Push-button value sender, 2 objects, Light scene actuator, Sequence actuator, Staircase lighting, Delay, Preset, Cyclical telegram, Flashing, Logics (AND, OR, XOR, XNOR, NAND, NOR), GATE, Min/max value transducers, Set value/hysteresis, PWM inverter, Priority, Continuous, Heating, Cooling, Fan control

Room thermostat:

Connection:

- Power supply: 10-pole multi-point connector

Control element: Switch contacts left/right, also for selecting setpoint and mode of operation

Display elements: LCD showing operation mode, temperature, time and date

Type of protection: IP 20, IEC/EN 60 529

Temperature range: -5 °C to 45 °C

Dimensions (L x W x D): 63 mm x 63 mm

Manufacturer: ABB

Product type: 6128/28

Bus coupler:

For combining the installation bus KNX and the different application modules

For installation in surface-mounted or flush-mounted boxes

Connection:

- KNX line: Bus connection terminal

Rated voltage: 24 V

Outputs:

- Rated current: 24 mA

Type of protection: IP 20, IEC/EN 60 529

Temperature range: -5 °C to 45 °C

Dimensions (L x W x D): 50 mm x 45 mm x 23 mm

Manufacturer: ABB

Product type: 6120/12

## Valve Drive Actuator

To control thermoelectric valve drives (24…230 V AC) in heating/cooling systems via 6/12 independent semiconductor outputs

General device functions:

Supply via bus voltage

Protection against overload and short-circuit

Manual operating keys and displaying LEDs for each channel

Block/enable manual operation, deactivation after time and status

Copy and exchange channels

Cyclical monitoring of the device

Sending and switching delay after bus voltage recovery

Request status values

Limited number of telegrams

Software functionality for each channel:

Reaction on bus voltage recovery

Status message overload/short-circuit

Selection of valve drive (normally closed/normally open)

Control of outputs: Switching (1-bit) or continuous (1-byte, pulse width modulation)

Status message control value (1-bit or 1-byte)

Cyclic monitoring of control value (room temperature controller)

Preferred position and status message at controller fault

Security functions: Blocking and forced operation

Valve purge: Activation via object, adjustable duration, cyclic purge and status

Characteristic curve correction

Status byte

Outputs: 6/12 semiconductor outputs

Power consumption KNX: < 250 mW

Operating voltage: 21…30 V DC via KNX

UN rated voltage: Max. 24…230 V AC, 45…65 Hz

IN rated current: Max. 160 mA

Operating and displaying elements:

LED and push-button (ON/OFF) for each channel

LED overload/short-circuit and push-button reset

Connection:

Outputs: Screw terminals with combination head screws

KNX: Screwless bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 or 8 modules at 18 mm

Manufacturer: ABB

Product type (dependent on number of channels): VAA/S 6.230.2.1, VAA/S 12.230.2.1

## Thermoelectric Valve Drive

The thermoelectric valve drive is used to open and close valves in heating, cooling and air conditioning systems.

The snap-on mounting on valves or in heating circuit distributors will be established by valve adapters.

Version normally closed (NC)

Voltage supply: 230 V AC, 50/60 Hz

Type of protection: IP 54, IEC/EN 60 529

Protection class: II

Mounting: Snap-on mounting in all installation positions

Connection cable: Pluggable, 2 x 0.75 mm², 1m

Display elements: Function display

Housing: White, RAL 9003

Dimensions: 60 mm x 44 mm x 49 mm

Manufacturer: ABB

Product type: TSA/K 230.2

## Blower Actuator 6 A

The Blower Actuator switches one or two 1- to 3-speed fan/s, controlled via KNX, by means of floating contacts.

Switching of one/two multi-level resistive, inductive or capacitive loads

Contacts of the fan connection with common foot point

Second fan connection alternatively as 3 switching outputs (2-fold version only)

One/two additional floating switching output

Speed switching or changeover switching can be parameterized

Direct selection of fan speed

Increase and decrease fan speed

Control fan speed via up to 2 control values

Control value selection by switchover or maximum selection

Threshold value with hysteresis for fan speeds

Forced operation

Limitation

Selection of fan speed on bus voltage failure

Selection of fan speed on bus voltage recovery

Start-up behavior can be parameterized

Switchover pause between fan speeds can be parameterized

Fan run-on can be individually parameterized for every speed

Control value monitoring can be parameterized

Switching output can be parameterized as N/O contact or N/C contact

Switching output with staircase lighting function

Status feedback

Reaction of outputs on bus voltage failure can be parameterized

Reaction of outputs on bus voltage recovery can be parameterized

Sending delay after bus voltage recovery

"In Operation" object (cyclic alive signal)

Outputs:

1-fold device: 4 (3+1)

2-fold device: 8 (2 x 3 + 2 x 1)

Rated current per output: 6 AX (250/440 V AC)

Max. power consumption of device: 1.5 W (1-fold), 2 W (2-fold)

Switching capacity:

- To IEC/EN 60 947-4-1: 6 A/AC3

- To IEC/EN 60 669: 6 AX

- Max. capacitive load: 140 µF

- Max. peak inrush current (150 µs): 400 A

Connection:

Screw terminals with universal head screw

KNX: Screwless bus connection terminal

Load circuit: For 0.2…6.0 mm² cables

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 4 or 6 modules at 18 mm

Manufacturer: ABB

Product type (dependent on number of channels): FCL/S 1.6.1.1, FCL/S 2.6.1.1

## Fan Coil Actuator PWM

Fan Coil Actuator for the usage with KNX bus. It controls via toggle switch and switch control up to three fan speeds. The fan speeds are locked against each other. With electronic outputs, the actuator controls 2 electromotor or 4 electrothermal valves for cooling and heating circuit loops. A further potential-free output is available, e.g. for an additional electrical heater. Furthermore, 3 inputs are available, for contactable temperature sensors or potential-free contacts.

Manual operation:

All contacts, inputs and outputs can be operated manually.

Commissioning without KNX:

Manual operation is optionally possible by connecting an auxiliary voltage to the bus connection terminal (separate KNX  device).

Fan speeds: 3, locked against each other

Nominal current: 6 A

Valve outputs: 4

Electronic: 0.5 A

Additional contact: 1

Nominal current: 20 AX (16 A C-Load, AC3)

Inputs: 3

Connection:

Screw terminal with combination head screws

Torque: Max. 0.6 Nm

KNX: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 6 modules at 18 mm

Manufacturer: ABB

Product type: FCA/S 1.1.1.2 (without manual operation), FCA/S 1.1.2.2 (with manual operation)

## Fan Coil Actuator 0-10V

Fan Coil Actuator for the usage with KNX bus. It controls via toggle switch and switch control up to three fan speeds. The fan speeds are locked against each other. With analog outputs, the actuator controls 2 motor-driven valves for cooling and heating circuits loops. A further potential-free output is available, e.g. for an additional electrical heater. Furthermore, 3 inputs are available, for contactable temperature sensors or potential-free contacts.

Manual operation:

All contacts, inputs and outputs can be operated manually.

Commissioning without KNX:

Manual operation is optionally possible by connecting an auxiliary voltage to the bus connection terminal (separate KNX  device)

Fan speeds: 3, locked against each other

Nominal current: 6 A

Valve outputs: 2

Analog: 0…10 V

Additional contact: 1

Nominal current: 20 AX (16 A C-Load, AC3)

Input: 3

Connection:

Screw terminal with combination head screws

Torque: Max. 0.6 Nm

KNX: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 6 modules at 18 mm

Manufacturer: ABB

Product type: FCA/S 1.2.1.2 (without manual operation), FCA/S 1.2.2.2 (with manual operation)

## Air Quality Sensor (CO2 Sensor) for Fan Control

The Air Quality Sensor (CO2 sensor) accurately measures the CO2 concentration, humidity and temperature in a room.

Three independent thresholds can be set for the CO2 concentration and the relative humidity in addition to a threshold for the temperature. Exceeding or under-running the thresholds can trigger a response.

Disable object for every threshold. Measured variables can be transmitted directly on the bus. Communication object “Ventilation” is used for RPM control or as a position indicatior for the ventilation flaps.

Maintenance-free sensor

The sensor is powered via the bus.

CO2:

Measuring range: 300…9,999 ppm

Threshold setting range: 500…2,550 ppm

Display by a colored LED

Relative humidity:

Measuring range: 1…100 %

Linear measuring range: 20…80 %

Display by a colored LED

Temperature:

Measuring range: 0…40 °C

Wall-mounted housing: 74 mm x 74 mm x 30.8 mm

Manufacturer: ABB

Product type: LGS/A 1.1

# Control Devices – Operation

## Binary Input Contact Scanning

The device for coupling potential-free (floating) contacts with an internally generated scanning voltage to the ABB i-bus® KNX. The status of the inputs is displayed by 4/8 yellow LEDs. The device makes possible the capture of a total of 4/8 individual input signals. Each channel of the device has a manual input key. These keys are used to operate the inputs manually. The device is powered via the KNX and does not require an additional auxiliary voltage supply.

The bus connection is made through a bus connecting terminal.

Functions of the application program:

Switching and dimming of lighting (also for 1-button operation)

Operation of shutters and blinds (also for 1-button operation)

Sending of arbitrary values, e.g. temperature value

Control and storing of light scenes

Operation of different consumers by repeated actuation

Counting from impulses and actuations

Reading out of technical contacts

Inputs: 4/8 individual

Scanning voltage: 35 V, pulsed

Scanning current: 0.1 mA

Display elements: 4/8 LEDs display status of the inputs

Manual operation: All inputs can be operated individually and manually

Connection:

Inputs: Slotted head screw terminals, for 0.2 to 4 mm² single core conductors

Bus connection: Screwless bus connection terminal

Tightening torque: Max. 0.6 Nm

Type of protection: IP 20, IEC/EN 60 529

Mounting: 35 mm mounting rail, IEC/EN 60 715

Width: 2 or 4 modules at 18 mm

Manufacturer: ABB

Product type (dependent on number of channels): BE/S 4.20.2.1, BE/S 8.20.2.1

## Multi-Function Control Element with Rockers

- For transmitting switching, push-button, value, dimming and blind commands to a KNX actuator

- Support of KNX functions through innovative LED-color concept (yellow = lighting, blue = blind, orange = RTC, magenta = scene and white = neutral/no function assigned) or standard illumination red/green

- Color and function of the LEDs can be changed via ETS.

- Removal protection is possible with screw-on installation.

- With a maximum of 10 logic channels (logic gate, time delay, sequences, etc.). The logic functions of the channel can be freely selected.

- The following functions are provided for the application module:

- Connection:

  - Inputs: LED

  - Outputs: Switching, Dimming, Blinds, Value, Push-button, Light scene extension unit, Step switch, Short/long operation, RTC operating mode switchover, Push-button switching, Push-button dimming, Push-button blind, Push-button value sender, Push-button step-type switch, Push-button multiple functions (max. 5 channels), Push-button value sender, 2 objects, Light scene actuator, Sequence actuator, Staircase lighting, Delay, Preset, Cyclical telegram, Flashing, Logics (AND, OR, XOR, XNOR, NAND, NOR), GATE, Min/max value transducers, Set value/hysteresis, PWM inverter, Priority

- Control element:

  - Power supply: 10-pole multi-point connector

  - Control element: Rocker switch left/right

  - Display elements: Two LED per rocker via separate communication object for status (Red/Green/OFF) or orientation light

  - Type of protection: IP 20, IEC/EN 60 529

  - Temperature range: -5 °C to 45 °C

  - Dimensions (L x W x D): 63 mm x 63 mm

  - Manufacturer: ABB

  - Product type (dependent on number of rockers): 6125/02, 6126/02, 6127/02

- Bus coupler:

  - For combining the installation bus KNX and the different application modules

  - For installation in surface-mounted or flush-mounted boxes

  - Connection:

- KNX line: Bus connection terminal

  - Rated voltage: 24 V

  - Outputs:

- Rated current: 24 mA

  - Type of protection: IP 20, IEC/EN 60 529

  - Temperature range: -5 °C to 45 °C

  - Dimensions (L x W x D): 50 mm x 45 mm x 23 mm

  - Manufacturer: ABB

  - Product type: 6120/12

## Touch Screen Device

KNX touch display

Presentation and operation of up to 210 KNX standard functions. Including light scene function, macro recorder, presence simulation and timed programmes

Integrated single-room thermostat

Operated via IR mobile remote control

Can be used via integrated logic as signalling station with acoustic feedback

Freely definable menu structure

Backlit LCD graphics display

Page layout with 8 symbols, or 5 or 10 touch surfaces

Actuating multimedia devices

Touch surfaces can be labelled (text or user-defined symbols)

Setting-up operation of the device via SD card or via bus

Touch Display:

Connections:

Power supply: 2 screw/plug terminals, up to 2.5 mm²

KNX line: Screw/clamp terminal up to 1.5 mm²

Rated voltage: 230 V DC

Rated frequency: 50 Hz

Control element: Freely programmable touch surfaces

Display elements: TFT Touch Display 320 x 240 pixels

Rated power: 12 W

Type of protection: IP 20, IEC/EN 60 529

Temperature range: 0 °C to 45 °C

Dimensions (L x W x D): 179.9 mm x 214.8 mm x 69 mm

Mounting depth: 60 mm

Manufacturer: ABB

Product type: 6136/100

Design Styling Frame:

The design styling frame allows the SMARTtouch Panel to be connected flush to the wall.

Black glass and chrome

Dimensions (L x W x D): 184.6 mm x 218 mm x 9 mm

Manufacturer: ABB

Product type: 6136/10

Flush-mounted installation box:

For flush-mounted and hollow-wall installation of the control panel

Dimensions (L x W x D): 163.5 mm x 199 mm x 60 mm

Mounting depth: 60 mm

Manufacturer: ABB

Product type: 6136/UP

## Presence Detector

- With integrated bus coupler

- Targeted for connection and disconnection of light bands depending on the room brightness

- Applicable as presence or movement detector

- Control also possible depending on movement

- Constant light switch with up to 2 independet channels

- Constant light switch with max. 2 outputs for brightness-dependent switching of two light bands in the room

- Detector operation with 2 power off stages

- Detector operation with integrated monitoring function

- Configurable as master or slave

- Configurable operating modes: Automatic, automatic activation or deactivation

- Activation text can be changed using an external communication object

- Switch-off delay can be changed using an external communication object

- Ceiling mounting in false ceilings with spring clamps or in solid ceilings in surface-mounting boxes 6131/29-xxx(-500)

- 4 PIR sensors, integrated brightness sensor

- The device can be updated through the bus

- The presence detector is not suited for alarm indications in VdS-compliant alarm systems.

- Detection range (for mounting height 2.5 m, 3 m and 4 m): circular

  - Seated persons Ø: Max. 5 m (8 m), max. 6.5 m (10 m), and max. 9 m (14 m)

  - Walking persons Ø: Max. 6.5 m (10 m), max. 8 m (12 m), and max. 10.5 m (16 m)

- Visible height: 16 mm (23 mm)

- Inputs: External brightness sensor, external movement

- Outputs: Movement detector, constant light switch

- Power supply: Via KNX
KNX line: Bus connection terminal

- Type of protection: IP 20, IEC/EN 60 529

- Temperature range: -5 °C to 45 °C

- Brightness limit value: 1…1,000 Lux

- Dimensions (L x W x D): 80 mm x 80 mm x 45 mm (91 mm x 91 mm x 45 mm)

- Mounting depth: 29 mm (22 mm)

- Mounting height: 2…4 m

- Manufacturer: ABB

- Product type: 6131/20, 6131/30

## Presence Detector Premium

- With integrated bus coupler

- Targeted for connection and disconnection of light bands depending on the room brightness

- Applicable as presence or movement detector

- Control also possible depending on movement

Constant light switch with up to 4 independent channels

Constant light switch with max. 2 outputs for brightness-dependent switching of two light bands in the room

Detector operation with 2 power off stages

Detector operation with integrated monitoring function

2 channels configurable as constant light controllers

Constant light controller with a maximum of 2 outputs for brightness-dependent control of two light rows in the room

Constant light controller with 2-stage deactivation function

1 channel configured as HVAC application with switching-on delay and sensitivity setting

Integrated object room temperature controller

10 freely programmable IR channels (blue and/or white)

Including 5 logic channels (logic gates, gates, delay and staircase lighting)

Configurable as master or slave

Activation text can be changed using an external communication object.

Switch-off delay can be changed using an external communication object.

Ceiling mounting in false ceilings with spring clamps or in solid ceilings in surface-mounting boxes

4 PIR sensors, integrated brightness sensor

The device can be updated through the bus.

The presence detector is not suited for alarm indications in VdS-compliant alarm systems.

Detection range (for mounting height 2.5 m, 3 m and 4 m): circular

Seated persons Ø: Max. 5 m (8 m), max. 6.5 m (10 m), and max. 9 m (14 m)

Walking persons Ø: Max. 6.5 m (10 m), max. 8 m (12 m), and max. 10.5 m (16 m)

The programming button can be activated with the IR transmitter 6010-25 (-500).

Visible height: 16 mm (23 mm)

Inputs: External brightness sensor, external movement

Outputs: Movement detector, HVAC, constant light switch, constant light controller

Connections:

Power supply: via KNX

KNX line: Bus connection terminal

Type of protection: IP 20, IEC/EN 60 529

Temperature range: -5 °C to 45 °C

Brightness limit value: 1…1,000 Lux

Dimensions (L x W x D): 80 mm x 80 mm x 45 mm (91 mm x 91 mm x 45 mm)

Mounting depth: 29 mm (22 mm)

Mounting height: 2…4 m

Manufacturer: ABB

Product type: 6131/21, 6131/31

## Radio Time Switch

The Radio Time Switch sends current time and date on the bus. The time can be optionally received via a DCF or GPS antenna. Furthermore, the device can be used to easily adjust the time programs.

Functions:

800 memory locations

Astronomical function with automatic calculation of sunrise and sunset times

Operation on the device with display backlight

Programming of the time programs on a PC

Transfer of time programs via memory card or via the KNX bus

Automatic summer/winter time changeover

Holiday and random programs

Protection against unauthorized access (PIN)

8 years power reserve (lithium backup battery)

Number of channels: 8

Supply voltage: 110…240 V AC, 50/60 Hz

Connection: Screw-less terminals

Mounting: 35 mm mounting rail, IEC/EN 60 715

Manufacturer: ABB

Product type: FW/S 8.2.1

- Control Devices – Metering and Load Management

## Meter Interface Module

- This device receives data and values from energy meters and converts them into system telegrams used for visualization, energy monitoring, billing, cost allocation and optimization. Suitable for ABB Electricity Meters of A/B series.

- Application areas: This device is a comfortable and economic energy management device, and can thus be part of green building solutions. No separate approvals required for installation and usage.

- Functions of the application program:

  - IR communication is automatically established by supplying bus voltage

  - Send/reset power fail counter and switch tariff via bus

  - Status byte available for: Internal or hardware error, IR communication error, no voltage or overvoltage, current out of specification, negative power, installation error or end value for active/reactive register is reached

  - Energy values import: Active energy, Reactive energy, Active energy tariff 1…4, Total Reactive energy tariff 1…4, Total Active energy resettable energy register (OD1365)

  - Energy values export: Active energy, Reactive energy, Active energy tariff 1…4, Total

  - Reactive energy tariff 1…4

  - Instrument values used:

- Active, Reactive and Apparent Power (L1, L2, L3, Total)

- Voltage (L1-N, L2-N, L3-N) and (L1-L2, L2-L3, L1-L3)

- Current (L1, L2, L3, N) , Quadrant andFrequency

- Power factor, Phase Angle Power and Voltage, Phase Angle Current (L1, L2, L3, Total)

- Other values used: Transformer ratio (CT and VT), Power fail counter, Tariffs Status information

- Power supply: 21…30 V DC via bus

- Connection:

  - Bus connection: Bus connecting terminal

  - Interface: Infrared port

- Display: LEDs for status and telegrams

- Type of protection: IP 20, IEC/EN 60 529

- Mounting: 35 mm mounting rail, IEC/EN 60 715

- Width: 2 modules at 18 mm

- Manufacturer: ABB

- Product type: ZS/S 1.1

## Energy Actuator

- Switch Actuator that records the energy consumption of the connected electrical load (Main Meters and Intermediate Meters available). Consumption per output and total consumption. Measures active power, current, voltage, apparent power, power factor, crest factor and frequency. Outputs can be switched depending on thresholds, meter readings and time. All values are available on KNX. Uses potential-free contacts to independently switch 3 electrical loads via KNX. Manual operation and display of the switching status. Especially suitable for switching of loads with high surge current, such as lighting with compensatory capacitor or fluorescent lighting loads according to IEC/EN 60 669.

- Software (ABB i-bus® Tool) is available for diagnostic purposes (commissioning) and is used to display the measured values and the status objects.

- Additional functions:

  - Load Control (Master/Slave system)

  - Time functions, on/off delay

  - Staircase lighting with preliminary warning and changeable duration

  - Recall scenes over 8-bit commands

  - Logical functions AND, OR, XOR, GATE

  - Forced operation and safety functions

  - Reaction to threshold values

  - Selection of default position on bus voltage failure and recovery

  - The parameterization of single outputs can be exchanged or copied

- Outputs: 3 potential-free floating contacts

  - Rated voltage: 250/440 V AC (50/60 Hz)

  - Rated current: 16/20 AX - C-Load

  - Switching capacity

- According to IEC/EN 60 947-4-1: 16/20 A/AC1; 16 A/AC3 (at 230/400 V AC)

- According to IEC/EN 60 669: 16/20 AX, max. capacitive load 200 μF

- Active consumption/Active Power:

  - Measuring range: 5.7 W…4,600 W (UN = 230 V)

  - Measuring range: 2.8 W…2,300 W (UN = 115 V)

  - Accuracy (250…500 mA): ± 6 % measuring value

  - Accuracy (500 mA…5 A): ± 3 % measuring value

  - Accuracy (5 A…20 A): ± 2 % measuring value

  - Starting current: 25 mA

- Current:

  - Measuring range (AC): 0.025…20 A

  - Accuracy: ± 1 % of actual value and ± 10 mA

- Voltage:

  - Measuring range (AC): 95…265 V

  - Accuracy: ± 1 % of actual value

- Frequency:

  - Measuring range: 45…65 Hz

  - Accuracy: ± 1 % of actual value

- Operation: 2 actuating levers for displaying the switch position and manual operation

- Connection: Screw terminals with combination head screws

  - Load side: For lines 0.2 to 6.0 mm² unifilar

  - KNX: Screwless bus connector

- Type of protection: IP 20, IEC/EN 60 529

- Mounting: 35 mm mounting rail, IEC/EN 60 715

- Width: 4 Modules at 18 mm

- Manufacturer: ABB

- Type: SE/S 3.16.1

## Energy Module

- KNX device with recording of the energy consumption (Watt hours) in the end circuit (main and intermediate meter). Consumption per phase and total. Detection of current, voltage, active power, apparent power, crest factor, power factor and frequency. Reaction (warning message) to thresholds, meter readings and time. All values can be transferred to KNX. Load control (master functionality). No switching functionality available.

- The parameterization of individual inputs can be exchanged or copied into other inputs.

- Software (ABB i-bus® Tool) is available for diagnostic purposes (commissioning) and is used to display the measured values and the status objects.

- Inputs: 3 floating contacts

- Rated voltage: 250/440 V AC (50/60 Hz)

- Rated current: 16/20 A

- Measuring range:

  - Active consumption/active power:

- 5.7 W…4,600 W (Un  = 230 V)

- 2.8 W…2,300 W (Un = 115 V)

  - Current (AC): 0.025…20 A

  - Voltage (AC): 95…265 V

  - Frequency: 45…65 Hz

- Accuracy:

  - Active consumption/active power (250…500 mA): ± 6 % of actual value

  - Active consumption/active power (500 mA… 5 A): ± 3 % of actual value

  - Active consumption/active power (5…20 A): ± 2 % of actual value

  - Current (0.025…20 A): ± 1 % of actual value and ±10 mA

  - Voltage (95…265 V): ± 1 % of actual value

  - Frequency (45…65 Hz): ± 1 % of actual value

- Starting current: 25 mA

- Connection:

  - Load circuit:

- Screw terminal with universal head screw

- For 0.2 to 6.0 mm² single core conductors

  - KNX: Screwless bus connection terminal

- Type of protection: IP 20, IEC/EN 60 529

- Mounting: 35 mm mounting rail, IEC/EN 60 715

- Width: 4 modules at 18 mm

- Manufacturer: ABB

- Product type: EM/S 3.16.1

Order number 2CDC500111N0202

Note:

The information in this Document contains best practice solutions to prescribe KNX installations in a specific application segment, but is of an exemplary nature only. The information may not represent the exact functional requirements with regard to specific local electrical installation requirements. Please note the Document also does not include the specification of legally required primary electrical protection devices i.e., circuit breakers, earth fault devices, etc., as these are highly dependent on national installation regulations.

We reserve the right to make technical changes or modify the contents of the Document without prior notice. ABB does not accept any responsibility whatsoever for potential errors or possible lack of information in the Document.

We reserve all rights in the Document and in the subject matter and illustrations contained therein. Any reproduction, disclosure to third parties or utilization of its contents – in whole or in parts – is forbidden without prior written consent of ABB AG.

©Copyright 2015 ABB. All rights reserved.

Warranty, Liability:

The user shall be solely responsible for the use of the content of this Document.

ABB shall be under no warranty whatsoever. ABB's liability in connection with the Document, irrespective of the legal ground, shall be excluded. The exclusion of liability shall not apply in the case of intention or gross negligence. The present declaration shall be governed by and construed in accordance with the laws of Switzerland under exclusion of its conflict of law rules and of the Vienna Convention on the International Sale of Goods (CISG).

Further information and local contacts:

www.abb.com/knx