Sample Specification for ACS850 Module Adjustable Speed Drives

Rated from 1.5 to 600HP; 230 or 460Vac

# GENERAL

## DESCRIPTION

This specification describes a complete Adjustable Speed AC Drive (ASD) used to control the speed and torque of NEMA design B induction motors.

The ASD manufacturer shall supply the ASD and all necessary controls as herein specified.

The ASD shall be manufactured by a company with at least twenty (20) years experience in the production of this type of equipment.

## QUALITY ASSURANCE

- The ASD manufacturing facility shall be ISO 9001 and ISO 14001 certified.

All printed circuit boards shall be completely tested before being assembled into the complete ASD. The ASD shall be subjected to a functional test and load test. The load test shall be at full rated load, or cycled load.

The ASD manufacturer shall have an analysis laboratory to evaluate the failure of any component.

## QUALIFICATIONS

- The ASD shall meet the following specifications

UL 508A and/or 508C - Underwriter's Laboratory. The ASD shall be UL listed and carry the UL mark.

CAN/CSA-C22 No. 14-M91 - Canadian Standards Association. The ASD shall be C-UL or CSA listed and carry the appropriate mark.

The ASD shall comply with the following European Union’s CE directives. The ASD shall carry CE mark.

EMC Low Voltage Directive EN 50178, 61800-5-1 and EN 60204-1

EMC Directive IEC 61800-3 category C2 and C3 with appropriate optional equipment

Machinery Directive 98/37 EC

Acceptable manufacturers

- ABB Inc. ACS850 series of AC ASDs

- ASD manufacturer must design, manufacture, quality control and life cycle manage all products offered on this project.

- ASD vendors that brand label products manufactured by others shall not be allowed.

## SUBMITTALS

- The Submittals shall include the following information:

- Outline Dimensions and Weight.

Customer connection and power wiring diagrams.

Complete technical product description including a complete list of options provided.

# DESIGN

## DESCRIPTION

- The ASD shall be solid state AC to AC inverter controlled device utilizing the latest isolated gate bipolar transistor (IGBT) technology.  The ASD shall utilize Direct Torque Control (DTC) as the primary motor control, employing an inner loop torque control strategy that mathematically determines the optimal motor torque and flux every 25 microseconds.  The ASD must also provide an optional motor control operational mode for scalar of V/Hz operation.

- The benefits that the motor control DTC shall make available for the operation of a NEMA design B induction motor shall be:

- Steady state speed accuracy within 1/10th the slip without an encoder, for process repeatability.

- 100% motor torque from zero speed available for acceleration with the ASD continuous current rating equal to or greater then the motor full load amp rating.

- At and below 90% speed, 100% torque is achievable even with 10% low line voltage.

- Ability to limit torque to protect the mechanical system with a common single torque setting above and below field weakening.

- Ability to provide torque in % of motor shaft torque (with in +/- 4% linearity) on the ASD control panel, analog output or via field bus of actual.

- Quiet motor operation for audibly friendly working environment in comparison to other low voltage PWM solutions utilizing a carrier frequency.

- Have available the ability to operate in open loop torque control, with an ability to switch between speed and torque control on the fly with the change of state to a digital input.

- Have an ability to share load or speed between two or more induction AC motors connected to the same system, when those motors are controlled by separate ASDs.

## RATINGS

- The ASD shall be rated to operate from 3-phase power at 230 VAC +10/-15% / 380 VAC to 500 VAC +10/-15%. The over- and under-voltage trip levels shall be automatically adjusted based on line voltage. The overvoltage trip level shall be a minimum of 70Vdc over nominal DC bus voltage, and the undervoltage trip level shall be a minimum 50Vdc under the nominal DC bus voltage.

The ASD shall be rated to operate at the following environmental operating conditions: ambient temperature 0 to 40(C continuous. ASDs that can operate at 40( C intermittently (during a 24 hour period) are not acceptable and must be oversized. Altitude 0 to 3300 feet above sea level without derating, less than 95% humidity, non-condensing.

The ASD shall be offered from 1.5 HP to 600 HP in similar construction and operation, using the same technology.

The ASD shall be rated to operate from input power from 48Hz to 63Hz.

Output voltage and current ratings shall match the adjustable frequency operating requirements of standard NEMA design A or NEMA design B motors.

The Light Duty overload current capacity shall be 110% of rated current for one (1) minute out of five (5) minutes.

The Heavy Duty overload current capacity shall be 150% of rated current for one (1) minute out of five (5) minutes.

The ASD efficiency shall be 98% or better of the full rated capability of the ASD at full speed and load.

## CONSTRUCTION

- All models shall provide a complete, ready-to-install solution.

The latest, most efficient IGBT power technology shall be used. This technology shall be used for all power and voltage ranges offered by the manufacturer.

The ASD shall offer microprocessor based control logic that is isolated from power circuitry.

The ASD shall use the same main control board for all ratings.

Control connections shall remain consistent for all power ratings.

Power connections on drives 1.5 to 10 HP shall be plug-in type

Drives from 1.5 to 60 HP shall have line connections on the top and motor connections on the bottom

All drive parameters, firmware and user programming shall be stored on a removable memory unit which can be moved to a replacement drive should that become necessary.  Once the memory block has been moved, the new drive shall start up and run without having to re-commission that drive.  The memory module shall also be capable of storing a backup set of drive parameters.

Module ASDs shall be available from 1.5 to 600HP and have the following features:

- Offered in UL Type Open construction for installation in an enclosure

- Support zero clearance left and right side installation through 200HP

- Provide as optional a control panel mounted on the front of the ASD through 200HP

- Include conformal coated circuit boards as standard

- Include integrated internal AC line reactor or DC choke above 10HP

- Offer option internally mounted braking chopper for use in dynamic braking

Desired optional features shall be furnished by the ASD manufacturer and shall also be available as field installable kits as an alternative. All optional features shall carry all of the necessary certifications as described in Section 1.03. Field installed kits shall not affect the ASD’s certification.

## OPERATOR INTERFACE

- The ASD shall be equipped with a front mounted operator control panel consisting of a four- (4) line by 20-character back-lit alphanumeric LCD display and a keypad with keys for Start/Stop, Local/Remote, Help, and have a minimum of two smart keys which change operation depending on what is being displayed.

- The control panel shall be removable, capable of remote mounting and allow for uploading and downloading of parameter settings as an aid for start-up of multiple ASDs.

The display of the control panel shall have the following features:

- The LCD display shall have contrast adjustment provisions to optimize viewing at angle.

All parameter names, fault messages, warnings and other information shall be displayed in complete American English words or standard American English abbreviations to allow the user to understand what is being displayed without the use of a manual or cross-reference table.

Additional languages including French, Spanish, German, Italian, Danish, Swedish, Russian and Turkish shall be selectable.

During normal operation, one (1) line of the control panel shall display the speed reference, and run/stop forward/reverse and local/remote status. The remaining three (3) lines of the display shall be programmable to display the values of any three (3) operating parameters. The selection shall include at least the following values:

- Speed/torque in percent (%), RPM or user-scaled units

Output frequency, voltage, current and torque

Power and kilowatt hours

Heatsink temperature and DC bus voltage

Status of discrete inputs and outputs

Values of analog input and output signals

Values of PID controller reference, feedback and error signals

The control panel shall be used for local control, for setting all parameters, and for stepping through the displays and menus.

Parameter setting shall be descriptive down to the bit level having descriptions in English (or other chosen language) of each bit that is to be programmed.

A copy function to upload and store parameter settings from an ASD and download stored parameter settings to the same ASD or to a PC shall exist.

The control panel shall display a log of the last ten faults detected, including real time stamp and pertinent drive information recorded at the time of the fault.

The control panel shall display a list of parameters different from default, and a list of the last twenty parameters that were changed by the user.

The drive parameter list shall be able to be backed up in the control panel and in the PC.

An intelligent start-up assistant shall be provided as standard. The Start-up routine will guide the user through all necessary adjustments to optimize operation.

- The Start-Up routine shall include “plug and produce” operation, which automatically recognizes the addition of options and fieldbus adapters and provides the necessary adjustment assistance.

The Start-Up routine shall prompt the user for Motor Nameplate Data including power, speed, voltage, frequency and current.

An auto-tune function shall identify the optimal motor tuning parameters for typical applications.

An auto-tune function shall also be available to tune the PID speed regulator loop. Manual adjustments shall also be allowed.

A selection of at least four (4) preprogrammed application macro parameter sets shall be provided to minimize the number of parameter adjustments required during start-up. Macros offered shall include Factory Default, Hand/Auto, Sequential Control, and Torque Control. A selection of two (2) user defined macros shall are also be available.

Selection shall be offered for both 2-wire and 3-wire Start/Stop control.

## PROTECTIVE FEATURES

- For each programmed warning and fault protection function, the ASD shall display a message in complete English words or Standard English abbreviations.

The ASD shall include internal MOV’s for phase to phase and phase to ground line voltage transient protection.

Output short circuit and ground fault protection rated for 100,000 amps shall be provided per UL508C.

Motor phase loss protection shall be provided.

The ASD shall provide electronic motor overload protection qualified per UL508C.

Protection shall be provided for AC line or DC bus overvoltage at 135% of maximum rated voltage or undervoltage at 75% of min. rated voltage.

The ASD shall protect itself against input phase loss.

A power loss ride through feature shall allow the ASD to remain fully operational after losing power as long as kinetic energy can be recovered from the rotating mass of the motor and load.

Stall protection shall be programmable to provide a warning or stop the ASD after the motor has operated above a programmed torque level for a programmed time limit.

Underload protection shall be programmable to provide a warning or stop the ASD after the motor has operated below a selected underload curve for a programmed time limit.

Over-temperature protection shall provide a warning if the power module temperature is less than 5(C below the over-temperature trip level.

Input terminals shall be provided for connecting a motor thermistor (PTC, PT100, or KTY84 type) to the ASD’s protective monitoring circuitry. An input shall also be programmable to monitor an external relay or switch contact.

## CONTROL INPUTS AND OUTPUTS

- Safe Torque Off:  through the use of redundant and non-processor based control complying with SIL3 (Safety Integrity Levels) as per IEC 61508 shall be a standard feature.  Implementation of “Safe Torque Off” shall be accomplished without the need for a safety relay or safety PLC.

- Discrete Inputs

- Minimum of six (6) discrete inputs shall be provided.

A minimum of six (6) of the inputs shall be independently programmable by function selection (e.g., run enable = DI2, fault reset = DI6, etc.) and by digital input selection (e.g., DI2 = run enable; DI6 = fault reset, etc.)

Inputs shall be designed for use with either the ASD’s internal 24 VDC supply or a customer supplied external 24 VDC supply.

Discrete Outputs

- Minimum of three (3) form C relay contact outputs shall be provided

- All relay outputs shall be independently programmable by function and by digital output selection to activate with at least 30 function selections including:

- Operating conditions such as drive ready, drive running, reversed and at set speed

- General warning and fault conditions

- Adjustable supervision limit indications based on programmed values of operating speed, speed reference, current, torque and PID feedback.

- Relay contacts shall be rated to switch 2 Amps at 24 VDC or 115/230 VAC.

Discrete Input/Outputs

- Minimum of two (2) signals shall be configurable as either inputs or outputs

- When configured as inputs, they shall have the same features as listed above for “discrete inputs.”

- When configured as outputs:

- Activate with at least 30 function selections as listed above for relay outputs

- Shall be rated to switch 200 milliamps at 24 VDC.

- When configured as an input, at least one (1) digital input shall be configurable as a frequency input accepting a square wave from 3 – 32 kHz at 24 VDC

- When configured as an output, at least one (1) digital output shall be configurable as a frequency output capable of switching from 3 – 32 kHz at 24VDC.

Analog Inputs

- Minimum of two (2) analog inputs shall be provided:

- Must support bi-polar voltage input or current input

Resolution of analog inputs must be at least 11bit total resolution

Inputs shall be independently programmable to accept signals including speed / frequency reference, torque reference or set point, PID set point and PID feedback / actual.

A differential input isolation amplifier shall be provided for each input.

Analog input signal processing functions shall include scaling adjustments and adjustable filtering.

If the input reference signal is lost, the ASD shall be programmable to signal this condition via a keypad warning, relay output and/or over the serial communications bus.  If the signal is lost, the ASD shall give the user the option of the following:

- Stop and display a fault

Run at a programmable preset speed and display an alarm

Hold the ASD speed based on the last good reference received and display an alarm

When inputs are used as speed references, reference signal processing shall include increase/decrease floating point control and control of speed and direction using a “joystick” reference signal.  Two (2) analog inputs shall be programmable to form a reference by addition, subtraction, multiplication, minimum selection or maximum selection.

Analog Outputs

- Minimum of two (2) 0 / 4-20 mA analog outputs shall be provided.

Outputs shall be independently programmable to provide signals proportional to output function selections including output speed, frequency, voltage, current and power.

## SERIAL COMMUNICATIONS

- The ASD shall be capable of communicating with other ASDs or controllers via a serial communications link. A variety of communications interface modules for the typical overriding control systems shall be available.

Interface modules shall be available for a wide selection of protocols including but not limited to:

- Modbus RTU

- Ethernet/IP

- Modbus TCP

- DeviceNet

- Profibus DP

- Canbus

Interface modules shall mount directly to the ASD control board to minimize interference and provide maximum throughput.

I/O shall be accessible through the serial communications adapter. Serial communication capabilities shall include, but not be limited to:

- Run-Stop control

Hand-Off-Auto Control

Speed Adjustment

PID (proportional/integral/derivative) control adjustments

Current Limit

Accel/Decel time adjustments

The ASD shall have the capability of allowing the overriding controller to monitor feedback such as process variable feedback, output speed/frequency, current (in amps), % torque, power (kW), kilowatt hours (resettable), operating hours (resettable), relay outputs, and diagnostic warning and fault information.

A connection shall also be provided for personal computer interface. Software shall be available for ASD setup, diagnostic analysis, monitoring and control.  The software shall provide real time graphical displays of ASD performance.

## CONTROL FUNCTIONS AND ADJUSTMENTS

- Output frequency shall be adjustable between 0Hz and 500Hz. Operation above motor nameplate shall require programming changes to prevent inadvertent high-speed operation.

Stop mode selections shall include coast to stop and ramp to stop.

The ASD shall be capable of controlling deceleration of a load without generating an overvoltage fault caused by excessive regenerated energy. Overvoltage control on deceleration shall extend the ramp time beyond the programmed value to keep the amount of regenerated energy below the point that causes overvoltage trip.

The ASD shall be capable of starting into a rotating motor with or without existing magnetic flux on the motor regardless of the motor direction. From the time the start signal is given to the ASD to the time the ASD has control of the motor shall not exceed two (2) seconds. Once the ASD has control of the motor it will than accelerate or decelerate the motor to the active reference speed without tripping or faulting or causing component damage to the ASD.

The ASD shall have the ability to automatically restart after an overcurrent, overvoltage, undervoltage, or loss of input signal protective trip. The number of restart attempts, trial time, and time between reset attempts shall be programmable.

Control functions shall include two (2) sets of acceleration and deceleration ramp time adjustments with linear and an s-curve ramp time selection.

Speed control functions shall include:

- Adjustable min/max speed limits.

Selection of up to seven (7) preset speed settings for external speed control.

Three sets of critical speed lockout adjustments.

A built-in PID controller to control a process variable such as pressure, flow or fluid level.

Functions shall include energy (flux) optimization for optimizing energy efficiency and limit the audible noise produced by the motor by providing the optimum magnetic flux for any given speed / load operating point.

The ASD shall be capable of sensing a loss of load (broken belt / broken coupling) and signal the loss of load condition. The ASD shall be programmable to signal this condition via a keypad warning, relay output and/or over the serial communications bus. Relay output shall include programmable time delays that will allow for ASD acceleration from zero speed without signaling a false underload condition.

Three (3) programmable critical frequency lockout ranges shall be provided to prevent the ASD from operating the load continuously at an unstable speed.

The ASD shall offer software to select the ASDs action in the event of a loss of the primary speed reference.

The ASD shall have programming blocks capable of more than twenty (20) different functions. These blocks shall be connectable to ASD’s actual signals and functions allowing the user to tailor the ASD to the specific application requirements without additional hardware. These blocks shall be programmable through the use of programming software for a PC.

# OPTIONS

## ASD control panel mounting on separate enclosure or cabinet door

## Dynamic braking chopper with 100% continuous duty internally mounted in ASD enclosure.  (Resistor mounted externally.)

## Second environnent EMC / RFI filter

## First environment EMC / RFI filter (1.5 – 200 HP)

## Input and Output extension modules

- Analog input and output expansion

- Digital input and output expansion

- Speed and position feedback for TTL incremental encoder and for HTL encoder

- Speed and position feedback for resolver interface

- Fieldbus communication modules (protocols);

- DeviceNet

- EtherNet / IP

- ModBus TCP

- ModBus RTU

- ProfiBus DP

- CANopen

# EXECUTION

## INSTALLATION

- The ASD manufacturer shall provide adequate drawings and instruction material to facilitate installation of the ASD by qualified electrical and mechanical personnel employed by others.

## PRODUCT SUPPORT

- Factory trained application engineering and service personnel that are thoroughly familiar with the ASD products offered shall be locally available at both the specifying and installation locations.

- A 24/365 technical support line shall be available on a toll-free-line.

## WARRANTY

- Standard Warranty shall be 12 months from the date of start-up or 24 months from the date of shipment. The warranty shall include all parts and on-site labor.

- There shall be 24/365 support available on a toll-free-line.