## Legend
Introduction
DOCUMENT INFORMATION
This document contains all the information regarding the Ekip Signalling Modbus TCP accessory module, available with an Ethernet network and the Modbus TCP communication protocol.
All the information are managed in 2 sheets: - Map: list of all the registers and addresses available. - Tables: list of tables not reported in the "Map" sheet.
NOTE: all the changes are reported in the "Revision History" sheet.
For all the information necessary to manage the Modbus TCP communication protocol, and to read information from the module, program parameters, and execute commands, refer to the ABB document 1SDH001140R0001 and to the proper standard documentation.
Application Note
PROGRAMMING SESSION
The writing of all the parameters in RW configuration, except for the Commands, must be managed with a programmaing session: 1. Command Start programming session (command 4) 2. Writing of paramater 1 3. Writing of parameter 2 ... N. Wring of paramater N N+1. Command Stop programming session (command 6)
Acronyms and Abbreviations
Measure units | Meaning
A | Ampere
V | Volt
Data Type | Meaning
CHAR | Ascii character
U8 | Unsigned 8 bit
U16 | Unsigned 16 bit
U32 | Unsigned 32 bit
S8 | Signed 8 bit
S16 | Signed 16 bit
S32 | Signed 32 bit
General | Meaning
d.c. | Don't care
Th | Threshold
CB | Circuit Breaker

## Revision History
Release | Date | Description
A | 2016-10-10 | First version
B | 2017-06-08 | - Changed the register "Output State" DEC address 1951 to "Command Output State - Physical", reduced the register bits to 3 - Added the registers "Output States - Physical" and "Logical", DEC addresses 1952 and 1953 - Changed the addresses of the registers "Number of activations of Output 1…10", DEC addresses 1976…1985

## Map
Registers & Parameters Name | Modbus Address (DEC) | Modbus Address (HEX) | CAN Index (HEX) | Data Type | Number of registers | Bitfield | Units | Multiplier | Range | Access | Stored Volatile | Description | 03 | 04 | 06 | 16 | 72 - 03 | 72 - 06 | 72 - 16 | N° of object | Type
Commands | 0 | 0000 | 2000 |  | 2 |  |  |  |  | RW | V | Actions toward the device |  | X |  | X |  |  |  | 1 | 32
Command type | 0 | 0000 | 1 | U32 | 1 |  |  |  | Commands List | RW | V | Write here the desired command | X | X |  | X
Command parameter | 1 | 0001 |  |  | 1 |  |  |  | Commands List | RW | V | Optional parameter | X | X |  | X
Programming Fail error code | 30 | 001E | 5002 |  | 1 |  |  |  |  | R | V | Result of device programming phase |  | X | [5 empty] | 1 | 16
Programming Fail error code | 30 | 001E | 1 | E16 | 1 |  |  |  | 0 ÷ 65535 | R | V | Code of error occured during programming |  | X
Command result | 40 | 0028 | 5003 |  | 1 |  |  |  |  | R | V | Result of command received from remote |  | X | [5 empty] | 1 | 16
Command result | 40 | 0028 | 1 | U16 | 1 |  |  |  | 0 ÷ 5 | R | V | 0 = OK, 1 = PROCESSING, 2 = OPEN_FAILED, 3 = CLOSED_FAILED, 4 = RESET_FAILED, 5 = SPRINGS_CHARGE_FAILED |  | X
Application Status | 50 | 0032 | 5004 |  | 1 |  |  |  |  | R | V | Actual status of the device |  | X | [5 empty] | 1 | 16
Application Status Word | 50 | 0032 | 1 | U16 | 1 | B |  |  | Bit Field | R | V |  |  | X
Operational Mode |  | 0000 | 1 | U16 |  | 0..2 |  |  | 0..7 | R | V | 0 = Initializing, 1 = Single CB supervisor 2 = Five CBs supervisor, 3 = FW Update 4 = Free I/O |  | X
Autotest Procedure status |  | 0000 | 1 | U16 |  | 3 |  |  | 0..1 | R | V | 0 = No autotest, 1 = Autotest running |  | X
Wink |  | 0000 | 1 | U16 |  | 4 |  |  | 0..1 | R | V | 0 = Normal status, 1 = Wink status active |  | X
Device Information | 500 | 01F4 | 2014 |  | 8 |  |  |  |  | R | S | Read Only information about the device |  | X | [5 empty] | 1 | 16
Slave ID | 500 | 01F4 | 1 | U16 | 8 |  |  |  | 0 ÷ 65535 | R | S | Slave device identifier = 28 (0x1C) |  | X
Serial Number | 536 | 0218 | 7006 |  | 8 |  |  |  |  | R | S | Read Only information about the device |  | X | [5 empty] | 8 | 16
Serial Number | 536 | 0218 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | R | S | ASCII Chars for serial number |  | X
CB Information | 600 | 0258 | 7115 |  | 16 |  |  |  |  | RW | S | Programmablle information about the connected CB |  | X | X | X |  |  |  | 16 | 16
CB Serial Number | 600 | 0258 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | ASCII Chars for CB serial number |  | X | X | X
CB Name | 608 | 0260 | 2 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | ASCII Chars for CB name/identifier |  | X | X | X
Tag Name | 628 | 0274 | 700A |  | 10 |  |  |  |  | RW | S | Programmable information about the device |  | X | X | X |  |  |  | 10 | 16
Tag Name | 628 | 0274 | 1 | CHAR | 5 |  |  |  | 10 ASCII Chars | RW | S | ASCII Chars for tag name |  | X | X | X
User Data | 633 | 0279 | 2 | CHAR | 5 |  |  |  | 10 ASCII Chars | RW | S | ASCII Chars for user data |  | X | X | X
CB Selection | 650 | 028A | 700B |  | 1 |  |  |  |  | RW | S | Device configuration, CB type |  | X | X | X |  |  |  | 1 | 16
CB Selection | 650 | 028A | 1 | U16 | 1 |  |  |  | 0 ÷ 10 | RW | S | Type of connected CB and command circuit: 0 = Generic CB, 1 = Isomax S1-S2 2 = Isomax S3, 3 = Isomax S4-S5 4 = Isomax S6-S7, 5 = Reserved 6 = Tmax T1-T2-T3 5 wires, 7 = Tmax T4-T5-T6 8 = Tmax T7- Emax X1, 9 = Emax E1..E6 10 = Emax2 |  | X | X | X
Information A | 700 | 02BC | 5005 |  | 5 |  |  |  |  | R | S | Read Only information about the device |  | X | [5 empty] | 5 | 16
SW Version | 700 | 02BC | 1 | U16 | 1 |  |  |  | MAJOR.minor (MSB.LSB) | R | S | Version of the running software |  | X
Boot SW Version | 701 | 02BD | 2 | U16 | 1 |  |  |  | MAJOR.minor (MSB.LSB) | R | S | Version of the Boot software |  | X
HW Version | 702 | 02BE | 3 | U16 | 1 |  |  |  | MAJOR.minor (MSB.LSB) | R | S | Version of the HW |  | X
Status Word | 703 | 02BF | 4 | U16 | 1 | B |  |  |  | R | S |  |  | X
CRC Error |  | 0000 |  |  |  | 0 |  |  | 0=CRC ok; 1=CRC error | R | V | CRC error condition (calculated for the application program portion) |  | X
CRC Calculated |  | 0000 |  |  |  | 1 |  |  | 0=CRC calculation in progress; 1=1st calculation done | R | V | CRC calculation completed: CRC error field is valid |  | X
Calculated CRC | 704 | 02C0 | 6 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | V | Calculated Code-area CRC |  | X
Dates | 800 | 0320 | 700E |  | 4 |  |  |  |  | RW | S | Meaningful dates |  | X | X | X |  |  |  | 4 | 16
Date Of CB Installation seconds low | 800 | 0320 | 1 | U16 | 1 |  |  |  | 0 ÷ 65535 | RW | S | Seconds from 00:00:00 31 december 1999 |  | X | X | X
Date Of CB Installation seconds high | 801 | 0321 | 2 | U16 | 1 |  |  |  | 0 ÷ 65535 | RW | S |  |  | X | X | X
Date Of Test seconds low | 802 | 0322 | 3 | U16 | 1 |  |  |  | 0 ÷ 65535 | RW | S | Seconds from 00:00:00 31 december 1999 |  | X | X | X
Date Of Test seconds high | 803 | 0323 | 4 | U16 | 1 |  |  |  | 0 ÷ 65535 | RW | S |  |  | X | X | X
Digital Inputs configuration | 1400 | 0578 | 7100 |  | 22 |  |  |  |  | RW | S | Input lines parameters |  | X | X | X |  |  |  | 22 | 16
Input 1 Configuration | 1400 | 0578 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 1 Filter Time | 1401 | 0579 | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 2 Configuration | 1402 | 057A | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 2 Filter Time | 1403 | 057B | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 3 Configuration | 1404 | 057C | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
CB supervisor: Active open Five CBs / Free I/O: Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 3 Filter Time | 1405 | 057D | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 4 Configuration | 1406 | 057E | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 4 Filter Time | 1407 | 057F | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 5 Configuration | 1408 | 0580 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 5 Filter Time | 1409 | 0581 | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 6 Configuration | 1410 | 0582 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
CB supervisor: Active open Five CBs / Free I/O: Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 6 Filter Time | 1411 | 0583 | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 7 Configuration | 1412 | 0584 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 7 Filter Time | 1413 | 0585 | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 8 Configuration | 1414 | 0586 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 8 Filter Time | 1415 | 0587 | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 9 Configuration | 1416 | 0588 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 9 Filter Time | 1417 | 0589 | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 10 Configuration | 1418 | 058A | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 10 Filter Time | 1419 | 058B | 1 | U16 | 1 |  | ms |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Input 11 Configuration | 1420 | 058C | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Input configuration bits |  | X | X | X
Active closed | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Active open; 1: Active closed |  | X | X | X
Input 11 Filter Time | 1421 | 058D | 1 | U16 | 1 |  |  |  | 0 ÷ 10000 | RW | S | Input persistency time before changing state |  | X | X | X
Digital Outputs configuration | 1500 | 05DC | 7101 |  | 20 |  |  |  |  | RW | S | Output lines parameters |  | X | X | X |  |  |  | 20 | 16
Output 1 Configuration | 1500 | 05DC | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T01 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Five CBs: Not latched Free I/O: Latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 1 Duration | 1501 | 05DD | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T01 pulse duration if not latched |  | X | X | X
Output 2 Configuration | 1502 | 05DE | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T02 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Five CBs: Not latched Free I/O: Latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 2 Duration | 1503 | 05DF | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T02 pulse duration if not latched |  | X | X | X
Output 3 Configuration | 1504 | 05E0 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T03 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Five CBs: Not latched Free I/O: Latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 3 Duration | 1505 | 05E1 | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T03 pulse duration if not latched |  | X | X | X
Output 4 Configuration | 1506 | 05E2 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T04 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 4 Duration | 1507 | 05E3 | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T04 pulse duration if not latched |  | X | X | X
Output 5 Configuration | 1508 | 05E4 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T05 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 5 Duration | 1509 | 05E5 | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T05 pulse duration if not latched |  | X | X | X
Output 6 Configuration | 1510 | 05E6 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T06 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 6 Duration | 1511 | 05E7 | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T06 pulse duration if not latched |  | X | X | X
Output 7 Configuration | 1512 | 05E8 | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T07 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 7 Duration | 1513 | 05E9 | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T07 pulse duration if not latched |  | X | X | X
Output 8 Configuration | 1514 | 05EA | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T08 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 8 Duration | 1515 | 05EB | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T08 pulse duration if not latched |  | X | X | X
Output 9 Configuration | 1516 | 05EC | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T09 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 9 Duration | 1517 | 05ED | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T09 pulse duration if not latched |  | X | X | X
Output 10 Configuration | 1518 | 05EE | 1 | U16 | 1 | B |  |  | Bit Field | RW | S | Output O T10 configuration bits |  | X | X | X
Normally open | [5 empty] | 0 |  |  | 0..1 | RW | S | 0: Normally open; 1: Normally closed |  | X | X | X
CB supervisor / Free I/O: Latched Five CBs: Not latched | [5 empty] | 1 |  |  | 0..1 | RW | S | 0: Not latched; 1: Latched |  | X | X | X
Output 10 Duration | 1519 | 05EF | 1 | U16 | 1 |  | ms | x10 | 1 ÷ 1000 | RW | S | Output O T10 pulse duration if not latched |  | X | X | X
Blink Led Info | 1560 | 0618 | 7002 |  | 1 |  |  |  |  | RW | S | Read Only information about the device |  | X | X | X |  |  |  | 1 | 16
Led Alive | 1560 | 0618 | 1 | U16 | 1 |  |  |  | 0..1 | RW | S | Led alive info (0 = power, 1 = blink) |  | X | X | X
CB Serial Numbers | 1600 | 0640 | 7116 |  | 40 |  |  |  |  | RW | S | Multiple CB serial numbers |  | X | X | X |  |  |  | 40 | 16
CB 1 Serial Number | 1600 | 0640 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | Serial number of CB 1 in multi CB operational mode |  | X | X | X
CB 2 Serial Number | 1608 | 0648 | 2 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | Serial number of CB 2 in multi CB operational mode |  | X | X | X
CB 3 Serial Number | 1616 | 0650 | 3 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | Serial number of CB 3 in multi CB operational mode |  | X | X | X
CB 4 Serial Number | 1624 | 0658 | 4 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | Serial number of CB 4 in multi CB operational mode |  | X | X | X
CB 5 Serial Number | 1632 | 0660 | 5 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | Serial number of CB 5 in multi CB operational mode |  | X | X | X
IO Tag Names 0..4 | 1650 | 0672 | 7117 |  | 40 |  |  |  |  | RW | S | Input Tag Names |  | X | X | X |  |  |  | 40 | 16
Input 1 Tag Name | 1600 | 0640 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 1 |  | X | X | X
Input 2 Tag Name | 1658 | 067A | 2 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 2 |  | X | X | X
Input 3 Tag Name | 1666 | 0682 | 3 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 3 |  | X | X | X
Input 4 Tag Name | 1674 | 068A | 4 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 4 |  | X | X | X
Input 5 Tag Name | 1682 | 0692 | 5 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 5 |  | X | X | X
IO Tag Names 5..9 | 1700 | 06A4 | 7118 |  | 40 |  |  |  |  | RW | S | Input Tag Names |  | X | X | X |  |  |  | 40 | 16
Input 6 Tag Name | 1700 | 06A4 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 6 |  | X | X | X
Input 7 Tag Name | 1708 | 06AC | 2 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 7 |  | X | X | X
Input 8 Tag Name | 1716 | 06B4 | 3 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 8 |  | X | X | X
Input 9 Tag Name | 1724 | 06BC | 4 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 9 |  | X | X | X
Input 10 Tag Name | 1732 | 06C4 | 5 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 10 |  | X | X | X
IO Tag Names 10..14 | 1750 | 06D6 | 7119 |  | 40 |  |  |  |  | RW | S | Input and Ouput Tag Names |  | X | X | X |  |  |  | 40 | 16
Input 11 Tag Name | 1750 | 06D6 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Input 11 |  | X | X | X
Output 1 Tag Name | 1758 | 06DE | 2 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 01 |  | X | X | X
Output 2 Tag Name | 1766 | 06E6 | 3 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 02 |  | X | X | X
Output 3 Tag Name | 1774 | 06EE | 4 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 03 |  | X | X | X
Output 4 Tag Name | 1782 | 06F6 | 5 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 04 |  | X | X | X
IO Tag Names 15..20 | 1800 | 0708 | 7120 |  | 48 |  |  |  |  | RW | S | Ouput Tag Names |  | X | X | X |  |  |  | 48 | 16
Output 5 Tag Name | 1800 | 0708 | 1 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 05 |  | X | X | X
Output 6 Tag Name | 1808 | 0710 | 2 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 06 |  | X | X | X
Output 7 Tag Name | 1816 | 0718 | 3 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 07 |  | X | X | X
Output 8 Tag Name | 1824 | 0720 | 4 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 08 |  | X | X | X
Output 9 Tag Name | 1832 | 0728 | 5 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 09 |  | X | X | X
Output 10 Tag Name | 1840 | 0730 | 6 | CHAR | 8 |  |  |  | 16 ASCII Chars | RW | S | TAG Name for Output T 10 |  | X | X | X
Input / Output State | 1950 | 079E | 6450 |  | 2 |  |  |  |  | R | V | Status of each digital Input and each digital Output |  | X | [5 empty] | 2 | 16
Input State | 1950 | 079E | 1 | U16 | 1 | B |  |  | Bit Field | R | V | Input States |  | X
Free Input 1 State / CB Springs charged | [5 empty] | 0 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active / Springs are charged |  | X
Free Input 2 State / Protection Tripped | [5 empty] | 1 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active / Protection has Tripped |  | X
Free Input 3 State / CB Connected | [5 empty] | 2 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active / CB is Connected |  | X
Free Input 4 State / CB Closed | [5 empty] | 3 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active / CB is Closed |  | X
Free Input 5 State / CB Tripped | [5 empty] | 4 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active / CB is Tripped |  | X
Free Input 6 State / Remote Status | [5 empty] | 5 |  |  | 0..1 | R | V | 0: Input inactive / Local; 1: Input active / Remote |  | X
Free Input 7 State | [5 empty] | 6 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active |  | X
Free Input 8 State | [5 empty] | 7 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active |  | X
Free Input 9 State | [5 empty] | 8 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active |  | X
Free Input 10 State | [5 empty] | 9 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active |  | X
Free Input 11 State | [5 empty] | 10 |  |  | 0..1 | R | V | 0: Input inactive; 1: Input active |  | X
Command Output State - Physical | 1951 | 079F | 1 | U16 | 1 | B |  |  | Bit Field | R | V | Output States |  | X
Open Command State | [5 empty] | 0 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Close Command State | [5 empty] | 1 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Reset Command State | [5 empty] | 2 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output State - Physical | 1952 | 07A0 | 1 | U16 | 1 | B |  |  | Bit Field | R | V | Output States |  | X
Output 1 State | [5 empty] | 0 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 2 State | [5 empty] | 1 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 3 State | [5 empty] | 2 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 4 State | [5 empty] | 3 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 5 State | [5 empty] | 4 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 6 State | [5 empty] | 5 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 7 State | [5 empty] | 6 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 8 State | [5 empty] | 7 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 9 State | [5 empty] | 8 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 10 State | [5 empty] | 9 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output State - Logical | 1953 | 07A1 | 1 | U16 | 1 | B |  |  | Bit Field | R | V | Output States |  | X
Output 1 State | [5 empty] | 0 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 2 State | [5 empty] | 1 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 3 State | [5 empty] | 2 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 4 State | [5 empty] | 3 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 5 State | [5 empty] | 4 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 6 State | [5 empty] | 5 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 7 State | [5 empty] | 6 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 8 State | [5 empty] | 7 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 9 State | [5 empty] | 8 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Output 10 State | [5 empty] | 9 |  |  | 0..1 | R | V | 0: Output inactive; 1: Output active |  | X
Statistics | 1960 | 07A8 | 6460 |  | 26 |  |  |  |  | R | S | Device collected statistics about I/O |  | X | [5 empty] | 26 | 16
Number of activations of Input 1 | 1960 | 07A8 | 1 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 2 | 1961 | 07A9 | 2 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 3 | 1962 | 07AA | 3 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 4 | 1963 | 07AB | 4 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 5 | 1964 | 07AC | 5 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 6 | 1965 | 07AD | 6 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 7 | 1966 | 07AE | 7 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 8 | 1967 | 07AF | 8 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 9 | 1968 | 07B0 | 9 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 10 | 1969 | 07B1 | 10 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Input 11 | 1970 | 07B2 | 11 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Open commands from Remote | 1971 | 07B3 | 12 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of Open commands received from remote |  | X
Open commands from Local | 1972 | 07B4 | 13 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of Open commands executed locally |  | X
Number of Open commands | 1973 | 07B5 | 14 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of received Open commands |  | X
Number of Close commands | 1974 | 07B6 | 15 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of received Closed commands |  | X
Number of Reset commands | 1975 | 07B7 | 16 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of received Reset commands |  | X
Number of activations of Output 4 | 1976 | 07B8 | 17 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 5 | 1977 | 07B9 | 18 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 6 | 1978 | 07BA | 19 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 7 | 1979 | 07BB | 20 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 8 | 1980 | 07BC | 21 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 9 | 1981 | 07BD | 22 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 10 | 1982 | 07BE | 23 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 1 | 1983 | 07BF | 24 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 2 | 1984 | 07C0 | 25 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Number of activations of Output 3 | 1985 | 07C1 | 26 | U16 | 1 |  |  |  | 0 ÷ 65535 | R | S | Number of transitions from inactive to active status |  | X
Network parameters | 2000 | 07D0 | 6509 |  | 12 |  |  |  |  | R | V | Dynamic network settings |  | X | [5 empty] | 6 | 16
Ip address | 2000 | 07D0 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | R | V | Ip address |  | X
Network Mask | 2002 | 07D2 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | R | V | Network Mask |  | X
Gateway Address | 2004 | 07D4 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | R | V | Gateway Address |  | X
Connected Client 1 | 2006 | 07D6 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | R | V | Ip address of first Modbus TCP Client connected |  | X
Connected Client 2 | 2008 | 07D8 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | R | V | Ip address of second Modbus TCP Client connected |  | X
Connected Client 3 | 2010 | 07DA | 1 | U32 | 2 |  |  |  | 0..2^32-1 | R | V | Ip address of third Modbus TCP Client connected |  | X
Eth Settings | 2100 | 0834 | 650F |  | 8 |  |  |  |  | RW | S | Static network settings |  | X |  | X |  |  |  | 4 | 32
Static Ip address | 2100 | 0834 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | RW | S | Static Ip address |  | X |  | X
Static Network Mask | 2102 | 0836 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | RW | S | Static Network Mask |  | X |  | X
Static Gateway Address | 2104 | 0838 | 1 | U32 | 2 |  |  |  | 0..2^32-1 | RW | S | Static Gateway Address |  | X |  | X
Configuration | 2106 | 083A | 1 | U32 | 2 | B |  |  | Bit Field | RW | S | Configuration |  | X |  | X
Use Static IP | [5 empty] | 0 |  |  | 0..1 | RW | S | 0 = Don't use static address; 1 = Latched |  | X |  | X
Enable IEEE 1588 | [5 empty] | 1 |  |  | 0..1 | RW | S | 0 = Disable; 1 = Enable |  | X |  | X
IEEE 1588 master role | [5 empty] | 2 |  |  | 0..1 | RW | S | 0 = Disable; 1 = Enable |  | X |  | X
Modbus TCP | [5 empty] | 3 |  |  | 0..1 | RW | S | 0 = Ekip Com HTTP Server; 1 = Ekip COM Modbus/TCP |  | X |  | X
Disable Gratuitous ARP | [5 empty] | 4 |  |  | 0..1 | RW | S | 0 = Gratuitous ARP enabled; 1 = Gratuitous ARP disabled |  | X |  | X
Password required | [5 empty] | 5 |  |  | 0..1 | RW | S | 0 = Password not required; 1 = Password required |  | X |  | X
Local State | [5 empty] | 6 |  |  | 0..1 | RW | S | 0 = Remote; 1 = Local |  | X |  | X
Check Spring | [5 empty] | 7 |  |  | 0..1 | RW | S | 0 = Springs check disabled; 1 = Springs check enabled |  | X |  | X
NOT USED | [5 empty] | 8 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 9 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 10 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 11 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 12 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 13 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 14 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 15 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 16 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 17 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 18 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 19 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 20 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 21 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 22 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 23 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 24 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 25 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 26 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 27 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 28 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 29 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 30 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
NOT USED | [5 empty] | 31 |  |  | 0..1 | RW | S | NOT USED |  | X |  | X
Mac Address | 2150 | 0866 | 6550 |  | 3 |  |  |  |  | R | S | Unique device address |  | X | [5 empty] | 1 | 48
Mac Address | 2150 | 0866 | 1 | U16 | 3 |  |  |  | 0..65535 | R | S | Mac address |  | X
Available* : | Parameter range limited to 3..9

## Tables
Operational Mode
Command description | Value | Parameter | Initializing | CB Supervisor | Free I/O | FW Update | Five CB Supervisor
Dummy Command | 0 | d.c. | N.A. | Available | Available | N.A. | Available
Reset Signalling | 2 | d.c. | N.A. | Available | Available | N.A. | Available
Start Programming Session | 4 | d.c. | N.A. | Available | Available | N.A. | Available
Abort Programming Session | 5 | d.c. | N.A. | Available | Available | N.A. | Available
Stop Programming Session | 6 | d.c. | N.A. | Available | Available | N.A. | Available
Open CB | 7 | d.c. | N.A. | Available | N.A. | N.A. | N.A.
Close CB | 8 | d.c. | N.A. | Available | N.A. | N.A. | N.A.
Reset CB | 9 | d.c. | N.A. | Available | N.A. | N.A. | N.A.
Wink Command | 10 | d.c. | N.A. | Available | Available | N.A. | Available
Set contact | 30 | Contact number 0..9 | N.A. | Available* | Available | N.A. | N.A.
Reset contact | 31 | Contact number 0..9 | N.A. | Available* | Available | N.A. | N.A.
Open CB number | 32 | CB number 0..4 | N.A. | N.A. | N.A. | N.A. | Available
Close CB number | 33 | CB number 0..4 | N.A. | N.A. | N.A. | N.A. | Available
Set Multiple Contacts | 34 | 0..0x03FF | N.A. | N.A. | Available | N.A. | N.A.
Start Autotest | 0x8007 | d.c. | N.A. | Available | Available | N.A. | Available
Change Password | 0x8008 | d.c. | N.A. | Available | Available | N.A. | Available
Reset statistics | 0x800C | d.c. | N.A. | Available | Available | N.A. | Available
Restore Default Parameters | 0x8016 | d.c. | N.A. | Available | Available | N.A. | Available
Available* : | Parameter range limited to 3..9