## Slide 1: SACE® Tmax® XT and Emax 2
Ekip™ Touch trip unit power supply options
OCTOber 2021

## Slide 2: SACE® Tmax XT
Self-supplied
Self-supplied through the current sensors with minimum of 0.2 x In*.
*0.3 x In for XT2 and XT4 with In≤100A
Auxiliary supply
Must be galvanically isolated 24V DC auxiliary voltage with the following characteristics:
Ekip Supply module
Two versions available:
24-48V DC
120-240V AC/DC
Ekip TT/T&P
These devices can be connected to the front test connector of the trip unit:
Ekip TT supplies temporarily power to the trip unit when breaker is off/tripped
Ekip T&P is used for programming trip unit via Ekip Connect 3 software
Ekip™ Touch trip units – power supply options

## Slide 3: SACE® Emax 2
Self-supplied
Power from internal current sensors
E1.2 – E4.2 requires a minimum 3 phase current of 80A to power trip unit
E6.2 requires a minimum 3 phase current of 160A to power trip unit
Auxiliary supply
Direct supply using provided ABB terminal blocks (using K1 and K2)
Typically used when no additional modules are present
Ekip Supply module
Two versions available:
24-48V DC
120-240V AC/DC
Ekip TT/T&P
These devices can be connected to the front test connector of the trip unit:
Ekip TT supplies temporarily power to the trip unit when breaker is off/tripped
Ekip T&P is used for programming & powering trip unit via Ekip Connect 3 software and laptop
Ekip™ Touch trip units – power supply options