## START HERE! - Instructions
ABB |  |  |  |  | Rev D, 7/13/2021
__
SACE® Tmax® XT molded case circuit breaker (MCCB) Ekip® Dip trip unit settings guide
Attention! Carefully read these instructions before using this guide. Always use the latest revision available at: https://electrification.us.abb.com/products/circuit-breakers/tmax-xt For troubleshooting and complete technical information, consult instruction manual
Technical Support:
888-385-1221, Option 1
eppc.support@us.abb.com
Instructions
1. User information is selected/entered in yellow cells only, e. g. -->
2. Individual worksheets are available (#3 below), or breaker schedule sheet (#4 below)
3. Individual worksheets show all possible thresholds by frame size (Tmax XT2, XT4, XT5, XT6, XT7) for L, S I and G protections
a. Select from the shortcuts below:
|  | LS/I | LSI | LSIG
Tmax XT2
Tmax XT4
Tmax XT5
Tmax XT6
Tmax XT7
b. Or select the tab in the file, e. g. for a Tmax XT5 with LSI trip unit:
c. Select the nominal rating, e. g. 600A
d. Select the current thresholds for each L, S and I protection, e. g. L = 540A, S = 2700A, I = 5400A
NOTE: Do not select I2 = I1 or I2 ≥ I3 as it will cause a configuration error, as signalled by blinking LEDs
e. Dip switch settings for each protection function are highlighted:
4. For breaker schedule, up to 20 breakers can be populated; go to 'Breaker Schedule' tab or click on the shortcut:
a. Carefully read the Instructions and Notes (below) before starting the worksheet; and if desired, enter your project name and breaker designations
b. Select the frame size from the drop-down options (XT2, XT4, XT5, XT6 or XT7), e. g. XT4
c. Select the nominal rating from the drop-down optons, e. g. 150A
d. Select the trip unit from the drop-down options (LS/I, LSI or LSIG), e. g. LSIG
e. Select the required setting for each protection as applicable (e. g. L = 120A, S = 675A, I = 1200A, G = 30A) from the drop-down options
NOTE: For LS/I cricuit breakers, either 'S' or 'I' can be set; this guide will default to 'I' settings
NOTE: Long-time pickup cannot be greater than nominal rating (In)
NOTE: Selecting 'OFF' for long-time pick up or short-time pickup defaults to fixed instantaneous override
NOTE: Do not select I2 = I1 or I2 ≥ I3 as it will cause a configuration error, as signalled by blinking LEDs
f. Repeat for each additional circuit breaker
The Ekip Dip Trip Unit Settings Guide is made available "as is" and with no express warranty. ABB further disclaims all other statutory and implied warranties, including, but not limited to, any warranty of fitness for particular purpose or merchantability. By acceptance and use of the Guide, User and User's Company agree that in no event will ABB be liable to the User or User's Company for any claims, liabilities, or damages even if caused by the negligence of ABB, and under no circumstances will ABB be liable for any indirect, special, incidental or consequential damages. User and User's Company are solely responsible for trip unit installation and settings which should be conducted by a certified engineer determined by User/User's Company.
ABB reserves the right to make technical changes or modify the contents of this document without prior notice. With regard to purchase orders, the agreed particulars shall prevail. ABB does not accept any responsibility whatsoever for potential errors or possible lack of information in this document. ABB reserves all rights in this document and in the subject matter and illustrations contained therein. Any reproduction, disclosure to third parties or utilization of its contents – in whole or in parts – is forbidden without prior written consent of ABB. ©2021 ABB. All rights reserved.
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Go now
Breaker schedule
Drop-down menu showing possible nominal ratings for this circuit breaker:
Select this tab for Tmax XT5 with LSI trip unit
'I' protection
Each of these are also drop-down selections
'S' protection
'L' protection
'L' protection
'S' protection
'I' protection
Carefully read these Instructions, before using this tab
Carefully read the Notes, and consult instruction manual for troubleshooting and complete technical information
Select this tab for breaker schedule worksheet
Type in the project and breaker designations
Frame Size drop-down selection
Nominal rating (In) drop-down selection
Trip unit drop-down selection
'L' protection
'S' protection
'I' protection
'G' protection

## Technical overview
ABB | Rev D, 7/13/2021
__
SACE® Tmax® XT MCCBs Ekip® Dip trip unit settings guide
The Ekip Dip Trip Unit Settings Guide is made available "as is" and with no express warranty. ABB further disclaims all other statutory and implied warranties, including, but not limited to, any warranty of fitness for particular purpose or merchantability. By acceptance and use of the Guide, User and User's Company agree that in no event will ABB be liable to the User or User's Company for any claims, liabilities, or damages even if caused by the negligence of ABB, and under no circumstances will ABB be liable for any indirect, special, incidental or consequential damages. User and User's Company are solely responsible for trip unit installation and settings which should be conducted by a certified engineer determined by User/User's Company.
ABB reserves the right to make technical changes or modify the contents of this document without prior notice. With regard to purchase orders, the agreed particulars shall prevail. ABB does not accept any responsibility whatsoever for potential errors or possible lack of information in this document. ABB reserves all rights in this document and in the subject matter and illustrations contained therein. Any reproduction, disclosure to third parties or utilization of its contents – in whole or in parts – is forbidden without prior written consent of ABB. ©2021 ABB. All rights reserved.

## data (hidden)
XT2 | 10 | 25 | 60 | 100 | 125 |  | I1XT2LS/I | 0.4 | 0.44 | 0.48 | 0.52 | 0.56 | 0.6 | 0.64 | 0.68 | 0.72 | 0.76 | 0.8 | 0.84 | 0.88 | 0.92 | 0.96 | 1 | [15 empty] | XT2 | 10 | XT210 | OK
XT4 | 40 | 60 | 100 | 150 | 225 | 250 | I1XT4LS/I | 0.4 | 0.44 | 0.48 | 0.52 | 0.56 | 0.6 | 0.64 | 0.68 | 0.72 | 0.76 | 0.8 | 0.84 | 0.88 | 0.92 | 0.96 | 1 | [15 empty] | XT2 | 25 | XT225 | OK
XT5 | 250 | 300 | 400 | 600 |  |  | I1XT5LS/I | 0.4 | 0.44 | 0.48 | 0.52 | 0.56 | 0.6 | 0.64 | 0.68 | 0.72 | 0.76 | 0.8 | 0.84 | 0.88 | 0.92 | 0.96 | 1 | [15 empty] | XT2 | 60 | XT260 | OK
XT6 | 600 | 800 |  |  |  |  | I1XT6LS/I | 0.4 | 0.44 | 0.48 | 0.52 | 0.56 | 0.6 | 0.64 | 0.68 | 0.72 | 0.76 | 0.8 | 0.84 | 0.88 | 0.92 | 0.96 | 1 | [15 empty] | XT2 | 100 | XT2100 | OK
XT7 | 600 | 800 | 1000 | 1200 |  |  | I1XT7LS/I | 0.4 | 0.44 | 0.48 | 0.52 | 0.56 | 0.6 | 0.64 | 0.68 | 0.72 | 0.76 | 0.8 | 0.84 | 0.88 | 0.92 | 0.96 | 1 | [15 empty] | XT2 | 125 | XT2125 | OK
[7 empty] | I1XT2LSI | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT4 | 40 | XT440 | OK
[7 empty] | I1XT4LSI | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT4 | 60 | XT460 | OK
[7 empty] | I1XT5LSI | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT4 | 100 | XT4100 | OK
[7 empty] | I1XT6LSI | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT4 | 150 | XT4150 | OK
[7 empty] | I1XT2LSIG | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT4 | 225 | XT4225 | OK
[7 empty] | I1XT4LSIG | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT4 | 250 | XT4250 | OK
[7 empty] | I1XT5LSIG | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT5 | 250 | XT5250 | OK
[7 empty] | I1XT6LSIG | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.92 | 0.94 | 0.96 | 0.98 | 1 | XT5 | 300 | XT5300 | OK
[7 empty] | I1XT7LSI | 0.4 | 0.42 | 0.45 | 0.47 | 0.5 | 0.52 | 0.55 | 0.57 | 0.6 | 0.62 | 0.65 | 0.67 | 0.7 | 0.72 | 0.75 | 0.77 | 0.8 | 0.82 | 0.85 | 0.87 | 0.9 | 0.92 | 0.95 | 0.97 | 1 | [6 empty] | XT5 | 400 | XT5400 | OK
[7 empty] | I1XT7LSIG | 0.4 | 0.42 | 0.45 | 0.47 | 0.5 | 0.52 | 0.55 | 0.57 | 0.6 | 0.62 | 0.65 | 0.67 | 0.7 | 0.72 | 0.75 | 0.77 | 0.8 | 0.82 | 0.85 | 0.87 | 0.9 | 0.92 | 0.95 | 0.97 | 1 | [6 empty] | XT5 | 600 | XT5600 | OK
[39 empty] | XT6 | 600 | XT6600 | OK
[7 empty] | I2XT2LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10 | [15 empty] | XT6 | 800 | XT6800 | OK
[7 empty] | I2XT4LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10 | [15 empty] | XT7 | 600 | XT7600 | OK
[7 empty] | I2XT5LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10 | [15 empty] | XT7 | 800 | XT7800 | OK
[7 empty] | I2XT6LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10 | [15 empty] | XT7 | 1000 | XT71000 | OK
[7 empty] | I2XT2LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10 | [15 empty] | XT7 | 1200 | XT71200 | OK
[7 empty] | I2XT4LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I2XT5LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I2XT6LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I2XT7LSI | OFF | 0.6 | 0.8 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[7 empty] | I2XT7LSIG | OFF | 0.6 | 0.8 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[7 empty] | I3XT2LS/I | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT4LS/I | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT5LS/I | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT6LS/I | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT2LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT4LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT5LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT6LSI | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT2LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT4LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT5LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT6LSIG | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT7LS/I | OFF | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4.5 | 5.5 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 10
[7 empty] | I3XT7LSI | OFF | 1.5 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
[7 empty] | I3XT7LSIG | OFF | 1.5 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
[7 empty] | I4XT2LSIG | OFF | 0.2 | 0.25 | 0.45 | 0.55 | 0.75 | 0.8 | 1
[7 empty] | I4XT4LSIG | OFF | 0.2 | 0.25 | 0.45 | 0.55 | 0.75 | 0.8 | 1
[7 empty] | I4XT5LSIG | OFF | 0.2 | 0.25 | 0.45 | 0.55 | 0.75 | 0.8 | 1
[7 empty] | I4XT6LSIG | OFF | 0.2 | 0.25 | 0.45 | 0.55 | 0.75 | 0.8 | 1
[7 empty] | I4XT7LSIG | OFF | 0.1 | 0.2 | 0.3 | 0.4 | 0.6 | 0.8 | 1

## DIP Settings (hidden)
|  | I1, LS/I, XT1-6 | [6 empty] | 0.04 | 0.08 | 0.16 | 0.32 |  |  |  | I2, XT1-6 |  |  |  |  | 1 | 1.5 | 2 | 5.5 |  |  | I3, XT1-6 |  |  |  |  | 1 | 1.5 | 2 | 5.5 |  |  | I4, XT1-6 |  |  |  | 0.2 | 0.25 | 0.55
XT2LS/I | XT2LS/I0.4 | 0.4 | 0 | 0 | 0 | 0 |  |  | ■□ | ■□ | ■□ | ■□ |  | XT2LS/I | XT2LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT2LS/I | XT2LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT2LSIG | XT2LSIGOFF | OFF | 0 | 0 | 0 | ■□ | ■□ | ■□
XT2LS/I | XT2LS/I0.44 | 0.44 | 1 | 0 | 0 | 0 |  |  | □■ | ■□ | ■□ | ■□ |  | XT2LS/I | XT2LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT2LS/I | XT2LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT2LSIG | XT2LSIG0.2 | 0.2 | 1 | 0 | 0 | □■ | ■□ | ■□
XT2LS/I | XT2LS/I0.48 | 0.48 | 0 | 1 | 0 | 0 |  |  | ■□ | □■ | ■□ | ■□ |  | XT2LS/I | XT2LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT2LS/I | XT2LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT2LSIG | XT2LSIG0.25 | 0.25 | 0 | 1 | 0 | ■□ | □■ | ■□
XT2LS/I | XT2LS/I0.52 | 0.52 | 1 | 1 | 0 | 0 |  |  | □■ | □■ | ■□ | ■□ |  | XT2LS/I | XT2LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT2LS/I | XT2LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT2LSIG | XT2LSIG0.45 | 0.45 | 1 | 1 | 0 | □■ | □■ | ■□
XT2LS/I | XT2LS/I0.56 | 0.56 | 0 | 0 | 1 | 0 |  |  | ■□ | ■□ | □■ | ■□ |  | XT2LS/I | XT2LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT2LS/I | XT2LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT2LSIG | XT2LSIG0.55 | 0.55 | 0 | 0 | 1 | ■□ | ■□ | □■
XT2LS/I | XT2LS/I0.6 | 0.6 | 1 | 0 | 1 | 0 |  |  | □■ | ■□ | □■ | ■□ |  | XT2LS/I | XT2LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT2LS/I | XT2LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT2LSIG | XT2LSIG0.75 | 0.75 | 1 | 0 | 1 | □■ | ■□ | □■
XT2LS/I | XT2LS/I0.64 | 0.64 | 0 | 1 | 1 | 0 |  |  | ■□ | □■ | □■ | ■□ |  | XT2LS/I | XT2LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT2LS/I | XT2LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT2LSIG | XT2LSIG0.8 | 0.8 | 0 | 1 | 1 | ■□ | □■ | □■
XT2LS/I | XT2LS/I0.68 | 0.68 | 1 | 1 | 1 | 0 |  |  | □■ | □■ | □■ | ■□ |  | XT2LS/I | XT2LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT2LS/I | XT2LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT2LSIG | XT2LSIG1 | 1 | 1 | 1 | 1 | □■ | □■ | □■
XT2LS/I | XT2LS/I0.72 | 0.72 | 0 | 0 | 0 | 1 |  |  | ■□ | ■□ | ■□ | □■ |  | XT2LS/I | XT2LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT2LS/I | XT2LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT4LSIG | XT4LSIGOFF | OFF | 0 | 0 | 0 | ■□ | ■□ | ■□
XT2LS/I | XT2LS/I0.76 | 0.76 | 1 | 0 | 0 | 1 |  |  | □■ | ■□ | ■□ | □■ |  | XT2LS/I | XT2LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT2LS/I | XT2LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT4LSIG | XT4LSIG0.2 | 0.2 | 1 | 0 | 0 | □■ | ■□ | ■□
XT2LS/I | XT2LS/I0.8 | 0.8 | 0 | 1 | 0 | 1 |  |  | ■□ | □■ | ■□ | □■ |  | XT2LS/I | XT2LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT2LS/I | XT2LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT4LSIG | XT4LSIG0.25 | 0.25 | 0 | 1 | 0 | ■□ | □■ | ■□
XT2LS/I | XT2LS/I0.84 | 0.84 | 1 | 1 | 0 | 1 |  |  | □■ | □■ | ■□ | □■ |  | XT2LS/I | XT2LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT2LS/I | XT2LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT4LSIG | XT4LSIG0.45 | 0.45 | 1 | 1 | 0 | □■ | □■ | ■□
XT2LS/I | XT2LS/I0.88 | 0.88 | 0 | 0 | 1 | 1 |  |  | ■□ | ■□ | □■ | □■ |  | XT2LS/I | XT2LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT2LS/I | XT2LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT4LSIG | XT4LSIG0.55 | 0.55 | 0 | 0 | 1 | ■□ | ■□ | □■
XT2LS/I | XT2LS/I0.92 | 0.92 | 1 | 0 | 1 | 1 |  |  | □■ | ■□ | □■ | □■ |  | XT2LS/I | XT2LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT2LS/I | XT2LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT4LSIG | XT4LSIG0.75 | 0.75 | 1 | 0 | 1 | □■ | ■□ | □■
XT2LS/I | XT2LS/I0.96 | 0.96 | 0 | 1 | 1 | 1 |  |  | ■□ | □■ | □■ | □■ |  | XT2LS/I | XT2LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT2LS/I | XT2LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT4LSIG | XT4LSIG0.8 | 0.8 | 0 | 1 | 1 | ■□ | □■ | □■
XT2LS/I | XT2LS/I1 | 1 | 1 | 1 | 1 | 1 |  |  | □■ | □■ | □■ | □■ |  | XT2LS/I | XT2LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT2LS/I | XT2LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT4LSIG | XT4LSIG1 | 1 | 1 | 1 | 1 | □■ | □■ | □■
XT4LS/I | XT4LS/I0.4 | 0.4 | 0 | 0 | 0 | 0 |  |  | ■□ | ■□ | ■□ | ■□ |  | XT4LS/I | XT4LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT4LS/I | XT4LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT5LSIG | XT5LSIGOFF | OFF | 0 | 0 | 0 | ■□ | ■□ | ■□
XT4LS/I | XT4LS/I0.44 | 0.44 | 1 | 0 | 0 | 0 |  |  | □■ | ■□ | ■□ | ■□ |  | XT4LS/I | XT4LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT4LS/I | XT4LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT5LSIG | XT5LSIG0.2 | 0.2 | 1 | 0 | 0 | □■ | ■□ | ■□
XT4LS/I | XT4LS/I0.48 | 0.48 | 0 | 1 | 0 | 0 |  |  | ■□ | □■ | ■□ | ■□ |  | XT4LS/I | XT4LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT4LS/I | XT4LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT5LSIG | XT5LSIG0.25 | 0.25 | 0 | 1 | 0 | ■□ | □■ | ■□
XT4LS/I | XT4LS/I0.52 | 0.52 | 1 | 1 | 0 | 0 |  |  | □■ | □■ | ■□ | ■□ |  | XT4LS/I | XT4LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT4LS/I | XT4LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT5LSIG | XT5LSIG0.45 | 0.45 | 1 | 1 | 0 | □■ | □■ | ■□
XT4LS/I | XT4LS/I0.56 | 0.56 | 0 | 0 | 1 | 0 |  |  | ■□ | ■□ | □■ | ■□ |  | XT4LS/I | XT4LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT4LS/I | XT4LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT5LSIG | XT5LSIG0.55 | 0.55 | 0 | 0 | 1 | ■□ | ■□ | □■
XT4LS/I | XT4LS/I0.6 | 0.6 | 1 | 0 | 1 | 0 |  |  | □■ | ■□ | □■ | ■□ |  | XT4LS/I | XT4LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT4LS/I | XT4LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT5LSIG | XT5LSIG0.75 | 0.75 | 1 | 0 | 1 | □■ | ■□ | □■
XT4LS/I | XT4LS/I0.64 | 0.64 | 0 | 1 | 1 | 0 |  |  | ■□ | □■ | □■ | ■□ |  | XT4LS/I | XT4LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT4LS/I | XT4LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT5LSIG | XT5LSIG0.8 | 0.8 | 0 | 1 | 1 | ■□ | □■ | □■
XT4LS/I | XT4LS/I0.68 | 0.68 | 1 | 1 | 1 | 0 |  |  | □■ | □■ | □■ | ■□ |  | XT4LS/I | XT4LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT4LS/I | XT4LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT5LSIG | XT5LSIG1 | 1 | 1 | 1 | 1 | □■ | □■ | □■
XT4LS/I | XT4LS/I0.72 | 0.72 | 0 | 0 | 0 | 1 |  |  | ■□ | ■□ | ■□ | □■ |  | XT4LS/I | XT4LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT4LS/I | XT4LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT6LSIG | XT6LSIGOFF | OFF | 0 | 0 | 0 | ■□ | ■□ | ■□
XT4LS/I | XT4LS/I0.76 | 0.76 | 1 | 0 | 0 | 1 |  |  | □■ | ■□ | ■□ | □■ |  | XT4LS/I | XT4LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT4LS/I | XT4LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT6LSIG | XT6LSIG0.2 | 0.2 | 1 | 0 | 0 | □■ | ■□ | ■□
XT4LS/I | XT4LS/I0.8 | 0.8 | 0 | 1 | 0 | 1 |  |  | ■□ | □■ | ■□ | □■ |  | XT4LS/I | XT4LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT4LS/I | XT4LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT6LSIG | XT6LSIG0.25 | 0.25 | 0 | 1 | 0 | ■□ | □■ | ■□
XT4LS/I | XT4LS/I0.84 | 0.84 | 1 | 1 | 0 | 1 |  |  | □■ | □■ | ■□ | □■ |  | XT4LS/I | XT4LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT4LS/I | XT4LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT6LSIG | XT6LSIG0.45 | 0.45 | 1 | 1 | 0 | □■ | □■ | ■□
XT4LS/I | XT4LS/I0.88 | 0.88 | 0 | 0 | 1 | 1 |  |  | ■□ | ■□ | □■ | □■ |  | XT4LS/I | XT4LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT4LS/I | XT4LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT6LSIG | XT6LSIG0.55 | 0.55 | 0 | 0 | 1 | ■□ | ■□ | □■
XT4LS/I | XT4LS/I0.92 | 0.92 | 1 | 0 | 1 | 1 |  |  | □■ | ■□ | □■ | □■ |  | XT4LS/I | XT4LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT4LS/I | XT4LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT6LSIG | XT6LSIG0.75 | 0.75 | 1 | 0 | 1 | □■ | ■□ | □■
XT4LS/I | XT4LS/I0.96 | 0.96 | 0 | 1 | 1 | 1 |  |  | ■□ | □■ | □■ | □■ |  | XT4LS/I | XT4LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT4LS/I | XT4LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT6LSIG | XT6LSIG0.8 | 0.8 | 0 | 1 | 1 | ■□ | □■ | □■
XT4LS/I | XT4LS/I1 | 1 | 1 | 1 | 1 | 1 |  |  | □■ | □■ | □■ | □■ |  | XT4LS/I | XT4LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT4LS/I | XT4LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT6LSIG | XT6LSIG1 | 1 | 1 | 1 | 1 | □■ | □■ | □■
XT5LS/I | XT5LS/I0.4 | 0.4 | 0 | 0 | 0 | 0 |  |  | ■□ | ■□ | ■□ | ■□ |  | XT5LS/I | XT5LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT5LS/I | XT5LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ |  | I4, XT7 | I4, XT7
XT5LS/I | XT5LS/I0.44 | 0.44 | 1 | 0 | 0 | 0 |  |  | □■ | ■□ | ■□ | ■□ |  | XT5LS/I | XT5LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT5LS/I | XT5LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT5LS/I | XT5LS/I0.48 | 0.48 | 0 | 1 | 0 | 0 |  |  | ■□ | □■ | ■□ | ■□ |  | XT5LS/I | XT5LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT5LS/I | XT5LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT7LSIG | XT7LSIGOFF | OFF | 0 | 0 | 0 | ■□ | ■□ | ■□
XT5LS/I | XT5LS/I0.52 | 0.52 | 1 | 1 | 0 | 0 |  |  | □■ | □■ | ■□ | ■□ |  | XT5LS/I | XT5LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT5LS/I | XT5LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT7LSIG | XT7LSIG0.1 | 0.1 | 0 | 0 | 1 | ■□ | ■□ | □■
XT5LS/I | XT5LS/I0.56 | 0.56 | 0 | 0 | 1 | 0 |  |  | ■□ | ■□ | □■ | ■□ |  | XT5LS/I | XT5LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT5LS/I | XT5LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT7LSIG | XT7LSIG0.2 | 0.2 | 0 | 1 | 0 | ■□ | □■ | ■□
XT5LS/I | XT5LS/I0.6 | 0.6 | 1 | 0 | 1 | 0 |  |  | □■ | ■□ | □■ | ■□ |  | XT5LS/I | XT5LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT5LS/I | XT5LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT7LSIG | XT7LSIG0.3 | 0.3 | 0 | 1 | 1 | ■□ | □■ | □■
XT5LS/I | XT5LS/I0.64 | 0.64 | 0 | 1 | 1 | 0 |  |  | ■□ | □■ | □■ | ■□ |  | XT5LS/I | XT5LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT5LS/I | XT5LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT7LSIG | XT7LSIG0.4 | 0.4 | 1 | 0 | 0 | □■ | ■□ | ■□
XT5LS/I | XT5LS/I0.68 | 0.68 | 1 | 1 | 1 | 0 |  |  | □■ | □■ | □■ | ■□ |  | XT5LS/I | XT5LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT5LS/I | XT5LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT7LSIG | XT7LSIG0.6 | 0.6 | 1 | 0 | 1 | □■ | ■□ | □■
XT5LS/I | XT5LS/I0.72 | 0.72 | 0 | 0 | 0 | 1 |  |  | ■□ | ■□ | ■□ | □■ |  | XT5LS/I | XT5LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT5LS/I | XT5LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT7LSIG | XT7LSIG0.8 | 0.8 | 1 | 1 | 0 | □■ | □■ | ■□
XT5LS/I | XT5LS/I0.76 | 0.76 | 1 | 0 | 0 | 1 |  |  | □■ | ■□ | ■□ | □■ |  | XT5LS/I | XT5LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT5LS/I | XT5LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT7LSIG | XT7LSIG1 | 1 | 1 | 1 | 1 | □■ | □■ | □■
XT5LS/I | XT5LS/I0.8 | 0.8 | 0 | 1 | 0 | 1 |  |  | ■□ | □■ | ■□ | □■ |  | XT5LS/I | XT5LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT5LS/I | XT5LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT5LS/I | XT5LS/I0.84 | 0.84 | 1 | 1 | 0 | 1 |  |  | □■ | □■ | ■□ | □■ |  | XT5LS/I | XT5LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT5LS/I | XT5LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT5LS/I | XT5LS/I0.88 | 0.88 | 0 | 0 | 1 | 1 |  |  | ■□ | ■□ | □■ | □■ |  | XT5LS/I | XT5LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT5LS/I | XT5LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT5LS/I | XT5LS/I0.92 | 0.92 | 1 | 0 | 1 | 1 |  |  | □■ | ■□ | □■ | □■ |  | XT5LS/I | XT5LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT5LS/I | XT5LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT5LS/I | XT5LS/I0.96 | 0.96 | 0 | 1 | 1 | 1 |  |  | ■□ | □■ | □■ | □■ |  | XT5LS/I | XT5LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT5LS/I | XT5LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT5LS/I | XT5LS/I1 | 1 | 1 | 1 | 1 | 1 |  |  | □■ | □■ | □■ | □■ |  | XT5LS/I | XT5LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT5LS/I | XT5LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT6LS/I | XT6LS/I0.4 | 0.4 | 0 | 0 | 0 | 0 |  |  | ■□ | ■□ | ■□ | ■□ |  | XT6LS/I | XT6LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT6LS/I | XT6LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT6LS/I | XT6LS/I0.44 | 0.44 | 1 | 0 | 0 | 0 |  |  | □■ | ■□ | ■□ | ■□ |  | XT6LS/I | XT6LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT6LS/I | XT6LS/I1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT6LS/I | XT6LS/I0.48 | 0.48 | 0 | 1 | 0 | 0 |  |  | ■□ | □■ | ■□ | ■□ |  | XT6LS/I | XT6LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT6LS/I | XT6LS/I1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT6LS/I | XT6LS/I0.52 | 0.52 | 1 | 1 | 0 | 0 |  |  | □■ | □■ | ■□ | ■□ |  | XT6LS/I | XT6LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT6LS/I | XT6LS/I2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT6LS/I | XT6LS/I0.56 | 0.56 | 0 | 0 | 1 | 0 |  |  | ■□ | ■□ | □■ | ■□ |  | XT6LS/I | XT6LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT6LS/I | XT6LS/I2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT6LS/I | XT6LS/I0.6 | 0.6 | 1 | 0 | 1 | 0 |  |  | □■ | ■□ | □■ | ■□ |  | XT6LS/I | XT6LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT6LS/I | XT6LS/I3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT6LS/I | XT6LS/I0.64 | 0.64 | 0 | 1 | 1 | 0 |  |  | ■□ | □■ | □■ | ■□ |  | XT6LS/I | XT6LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT6LS/I | XT6LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT6LS/I | XT6LS/I0.68 | 0.68 | 1 | 1 | 1 | 0 |  |  | □■ | □■ | □■ | ■□ |  | XT6LS/I | XT6LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT6LS/I | XT6LS/I4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT6LS/I | XT6LS/I0.72 | 0.72 | 0 | 0 | 0 | 1 |  |  | ■□ | ■□ | ■□ | □■ |  | XT6LS/I | XT6LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT6LS/I | XT6LS/I5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT6LS/I | XT6LS/I0.76 | 0.76 | 1 | 0 | 0 | 1 |  |  | □■ | ■□ | ■□ | □■ |  | XT6LS/I | XT6LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT6LS/I | XT6LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT6LS/I | XT6LS/I0.8 | 0.8 | 0 | 1 | 0 | 1 |  |  | ■□ | □■ | ■□ | □■ |  | XT6LS/I | XT6LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT6LS/I | XT6LS/I7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT6LS/I | XT6LS/I0.84 | 0.84 | 1 | 1 | 0 | 1 |  |  | □■ | □■ | ■□ | □■ |  | XT6LS/I | XT6LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT6LS/I | XT6LS/I7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT6LS/I | XT6LS/I0.88 | 0.88 | 0 | 0 | 1 | 1 |  |  | ■□ | ■□ | □■ | □■ |  | XT6LS/I | XT6LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT6LS/I | XT6LS/I8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT6LS/I | XT6LS/I0.92 | 0.92 | 1 | 0 | 1 | 1 |  |  | □■ | ■□ | □■ | □■ |  | XT6LS/I | XT6LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT6LS/I | XT6LS/I8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT6LS/I | XT6LS/I0.96 | 0.96 | 0 | 1 | 1 | 1 |  |  | ■□ | □■ | □■ | □■ |  | XT6LS/I | XT6LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT6LS/I | XT6LS/I9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT6LS/I | XT6LS/I1 | 1 | 1 | 1 | 1 | 1 |  |  | □■ | □■ | □■ | □■ |  | XT6LS/I | XT6LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT6LS/I | XT6LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
|  | I1, LS/I, XT7 | [11 empty] | XT2LSI | XT2LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT2LSI | XT2LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
[14 empty] | XT2LSI | XT2LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT2LSI | XT2LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT7LS/I | XT7LS/I0.4 | 0.4 | 0 | 0 | 0 | 0 |  |  | ■□ | ■□ | ■□ | ■□ |  | XT2LSI | XT2LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT2LSI | XT2LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT7LS/I | XT7LS/I0.44 | 0.44 | 0 | 0 | 0 | 1 |  |  | ■□ | ■□ | ■□ | □■ |  | XT2LSI | XT2LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT2LSI | XT2LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT7LS/I | XT7LS/I0.48 | 0.48 | 0 | 0 | 1 | 0 |  |  | ■□ | ■□ | □■ | ■□ |  | XT2LSI | XT2LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT2LSI | XT2LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT7LS/I | XT7LS/I0.52 | 0.52 | 0 | 0 | 1 | 1 |  |  | ■□ | ■□ | □■ | □■ |  | XT2LSI | XT2LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT2LSI | XT2LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT7LS/I | XT7LS/I0.56 | 0.56 | 0 | 1 | 0 | 0 |  |  | ■□ | □■ | ■□ | ■□ |  | XT2LSI | XT2LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT2LSI | XT2LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT7LS/I | XT7LS/I0.6 | 0.6 | 0 | 1 | 0 | 1 |  |  | ■□ | □■ | ■□ | □■ |  | XT2LSI | XT2LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT2LSI | XT2LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT7LS/I | XT7LS/I0.64 | 0.64 | 0 | 1 | 1 | 0 |  |  | ■□ | □■ | □■ | ■□ |  | XT2LSI | XT2LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT2LSI | XT2LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT7LS/I | XT7LS/I0.68 | 0.68 | 0 | 1 | 1 | 1 |  |  | ■□ | □■ | □■ | □■ |  | XT2LSI | XT2LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT2LSI | XT2LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT7LS/I | XT7LS/I0.72 | 0.72 | 1 | 0 | 0 | 0 |  |  | □■ | ■□ | ■□ | ■□ |  | XT2LSI | XT2LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT2LSI | XT2LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT7LS/I | XT7LS/I0.76 | 0.76 | 1 | 0 | 0 | 1 |  |  | □■ | ■□ | ■□ | □■ |  | XT2LSI | XT2LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT2LSI | XT2LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT7LS/I | XT7LS/I0.8 | 0.8 | 1 | 0 | 1 | 0 |  |  | □■ | ■□ | □■ | ■□ |  | XT2LSI | XT2LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT2LSI | XT2LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT7LS/I | XT7LS/I0.84 | 0.84 | 1 | 0 | 1 | 1 |  |  | □■ | ■□ | □■ | □■ |  | XT2LSI | XT2LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT2LSI | XT2LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT7LS/I | XT7LS/I0.88 | 0.88 | 1 | 1 | 0 | 0 |  |  | □■ | □■ | ■□ | ■□ |  | XT2LSI | XT2LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT2LSI | XT2LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT7LS/I | XT7LS/I0.92 | 0.92 | 1 | 1 | 0 | 1 |  |  | □■ | □■ | ■□ | □■ |  | XT2LSI | XT2LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT2LSI | XT2LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT7LS/I | XT7LS/I0.96 | 0.96 | 1 | 1 | 1 | 0 |  |  | □■ | □■ | □■ | ■□ |  | XT4LSI | XT4LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT4LSI | XT4LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT7LS/I | XT7LS/I1 | 1 | 1 | 1 | 1 | 1 |  |  | □■ | □■ | □■ | □■ |  | XT4LSI | XT4LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT4LSI | XT4LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
| I1, LSI and LSIG, XT1-6 | I1, LSI and LSIG, XT1-6 | [5 empty] | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 |  | XT4LSI | XT4LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT4LSI | XT4LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
[14 empty] | XT4LSI | XT4LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT4LSI | XT4LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT2LSI | XT2LSI0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□ |  | XT4LSI | XT4LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT4LSI | XT4LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT2LSI | XT2LSI0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□ |  | XT4LSI | XT4LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT4LSI | XT4LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT2LSI | XT2LSI0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□ |  | XT4LSI | XT4LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT4LSI | XT4LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT2LSI | XT2LSI0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□ |  | XT4LSI | XT4LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT4LSI | XT4LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT2LSI | XT2LSI0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□ |  | XT4LSI | XT4LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT4LSI | XT4LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT2LSI | XT2LSI0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□ |  | XT4LSI | XT4LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT4LSI | XT4LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT2LSI | XT2LSI0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□ |  | XT4LSI | XT4LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT4LSI | XT4LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT2LSI | XT2LSI0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□ |  | XT4LSI | XT4LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT4LSI | XT4LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT2LSI | XT2LSI0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□ |  | XT4LSI | XT4LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT4LSI | XT4LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT2LSI | XT2LSI0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□ |  | XT4LSI | XT4LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT4LSI | XT4LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT2LSI | XT2LSI0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□ |  | XT4LSI | XT4LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT4LSI | XT4LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT2LSI | XT2LSI0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□ |  | XT4LSI | XT4LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT4LSI | XT4LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT2LSI | XT2LSI0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□ |  | XT5LSI | XT5LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT5LSI | XT5LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT2LSI | XT2LSI0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□ |  | XT5LSI | XT5LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT5LSI | XT5LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT2LSI | XT2LSI0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□ |  | XT5LSI | XT5LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT5LSI | XT5LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT2LSI | XT2LSI0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□ |  | XT5LSI | XT5LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT5LSI | XT5LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT2LSI | XT2LSI0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■ |  | XT5LSI | XT5LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT5LSI | XT5LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT2LSI | XT2LSI0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■ |  | XT5LSI | XT5LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT5LSI | XT5LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT2LSI | XT2LSI0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■ |  | XT5LSI | XT5LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT5LSI | XT5LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT2LSI | XT2LSI0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■ |  | XT5LSI | XT5LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT5LSI | XT5LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT2LSI | XT2LSI0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■ |  | XT5LSI | XT5LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT5LSI | XT5LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT2LSI | XT2LSI0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■ |  | XT5LSI | XT5LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT5LSI | XT5LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT2LSI | XT2LSI0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■ |  | XT5LSI | XT5LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT5LSI | XT5LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT2LSI | XT2LSI0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■ |  | XT5LSI | XT5LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT5LSI | XT5LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT2LSI | XT2LSI0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■ |  | XT5LSI | XT5LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT5LSI | XT5LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT2LSI | XT2LSI0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■ |  | XT5LSI | XT5LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT5LSI | XT5LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT2LSI | XT2LSI0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■ |  | XT5LSI | XT5LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT5LSI | XT5LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT2LSI | XT2LSI0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■ |  | XT5LSI | XT5LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT5LSI | XT5LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT2LSI | XT2LSI0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■ |  | XT6LSI | XT6LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT6LSI | XT6LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT2LSI | XT2LSI0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■ |  | XT6LSI | XT6LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT6LSI | XT6LSI1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT2LSI | XT2LSI1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■ |  | XT6LSI | XT6LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT6LSI | XT6LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT4LSI | XT4LSI0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□ |  | XT6LSI | XT6LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT6LSI | XT6LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT4LSI | XT4LSI0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□ |  | XT6LSI | XT6LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT6LSI | XT6LSI2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT4LSI | XT4LSI0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□ |  | XT6LSI | XT6LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT6LSI | XT6LSI3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT4LSI | XT4LSI0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□ |  | XT6LSI | XT6LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT6LSI | XT6LSI3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT4LSI | XT4LSI0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□ |  | XT6LSI | XT6LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT6LSI | XT6LSI4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT4LSI | XT4LSI0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□ |  | XT6LSI | XT6LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT6LSI | XT6LSI5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT4LSI | XT4LSI0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□ |  | XT6LSI | XT6LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT6LSI | XT6LSI6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT4LSI | XT4LSI0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□ |  | XT6LSI | XT6LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT6LSI | XT6LSI7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT4LSI | XT4LSI0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□ |  | XT6LSI | XT6LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT6LSI | XT6LSI7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT4LSI | XT4LSI0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□ |  | XT6LSI | XT6LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT6LSI | XT6LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT4LSI | XT4LSI0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□ |  | XT6LSI | XT6LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT6LSI | XT6LSI8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT4LSI | XT4LSI0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□ |  | XT6LSI | XT6LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT6LSI | XT6LSI9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT4LSI | XT4LSI0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□ |  | XT6LSI | XT6LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT6LSI | XT6LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT4LSI | XT4LSI0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□ |  | XT2LSIG | XT2LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT2LSIG | XT2LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT4LSI | XT4LSI0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□ |  | XT2LSIG | XT2LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT2LSIG | XT2LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT4LSI | XT4LSI0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□ |  | XT2LSIG | XT2LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT2LSIG | XT2LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT4LSI | XT4LSI0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■ |  | XT2LSIG | XT2LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT2LSIG | XT2LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT4LSI | XT4LSI0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■ |  | XT2LSIG | XT2LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT2LSIG | XT2LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT4LSI | XT4LSI0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■ |  | XT2LSIG | XT2LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT2LSIG | XT2LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT4LSI | XT4LSI0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■ |  | XT2LSIG | XT2LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT2LSIG | XT2LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT4LSI | XT4LSI0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■ |  | XT2LSIG | XT2LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT2LSIG | XT2LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT4LSI | XT4LSI0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■ |  | XT2LSIG | XT2LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT2LSIG | XT2LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT4LSI | XT4LSI0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■ |  | XT2LSIG | XT2LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT2LSIG | XT2LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT4LSI | XT4LSI0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■ |  | XT2LSIG | XT2LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT2LSIG | XT2LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT4LSI | XT4LSI0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■ |  | XT2LSIG | XT2LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT2LSIG | XT2LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT4LSI | XT4LSI0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■ |  | XT2LSIG | XT2LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT2LSIG | XT2LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT4LSI | XT4LSI0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■ |  | XT2LSIG | XT2LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT2LSIG | XT2LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT4LSI | XT4LSI0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■ |  | XT2LSIG | XT2LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT2LSIG | XT2LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT4LSI | XT4LSI0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■ |  | XT2LSIG | XT2LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT2LSIG | XT2LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT4LSI | XT4LSI0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■ |  | XT4LSIG | XT4LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT4LSIG | XT4LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT4LSI | XT4LSI1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■ |  | XT4LSIG | XT4LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT4LSIG | XT4LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT5LSI | XT5LSI0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□ |  | XT4LSIG | XT4LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT4LSIG | XT4LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT5LSI | XT5LSI0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□ |  | XT4LSIG | XT4LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT4LSIG | XT4LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT5LSI | XT5LSI0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□ |  | XT4LSIG | XT4LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT4LSIG | XT4LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT5LSI | XT5LSI0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□ |  | XT4LSIG | XT4LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT4LSIG | XT4LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT5LSI | XT5LSI0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□ |  | XT4LSIG | XT4LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT4LSIG | XT4LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT5LSI | XT5LSI0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□ |  | XT4LSIG | XT4LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT4LSIG | XT4LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT5LSI | XT5LSI0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□ |  | XT4LSIG | XT4LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT4LSIG | XT4LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT5LSI | XT5LSI0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□ |  | XT4LSIG | XT4LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT4LSIG | XT4LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT5LSI | XT5LSI0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□ |  | XT4LSIG | XT4LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT4LSIG | XT4LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT5LSI | XT5LSI0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□ |  | XT4LSIG | XT4LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT4LSIG | XT4LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT5LSI | XT5LSI0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□ |  | XT4LSIG | XT4LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT4LSIG | XT4LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT5LSI | XT5LSI0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□ |  | XT4LSIG | XT4LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT4LSIG | XT4LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT5LSI | XT5LSI0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□ |  | XT4LSIG | XT4LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT4LSIG | XT4LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT5LSI | XT5LSI0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□ |  | XT4LSIG | XT4LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT4LSIG | XT4LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT5LSI | XT5LSI0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□ |  | XT5LSIG | XT5LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT5LSIG | XT5LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT5LSI | XT5LSI0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□ |  | XT5LSIG | XT5LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT5LSIG | XT5LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT5LSI | XT5LSI0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■ |  | XT5LSIG | XT5LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT5LSIG | XT5LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT5LSI | XT5LSI0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■ |  | XT5LSIG | XT5LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT5LSIG | XT5LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT5LSI | XT5LSI0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■ |  | XT5LSIG | XT5LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT5LSIG | XT5LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT5LSI | XT5LSI0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■ |  | XT5LSIG | XT5LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT5LSIG | XT5LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT5LSI | XT5LSI0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■ |  | XT5LSIG | XT5LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT5LSIG | XT5LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT5LSI | XT5LSI0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■ |  | XT5LSIG | XT5LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT5LSIG | XT5LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT5LSI | XT5LSI0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■ |  | XT5LSIG | XT5LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT5LSIG | XT5LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT5LSI | XT5LSI0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■ |  | XT5LSIG | XT5LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT5LSIG | XT5LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT5LSI | XT5LSI0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■ |  | XT5LSIG | XT5LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT5LSIG | XT5LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT5LSI | XT5LSI0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■ |  | XT5LSIG | XT5LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT5LSIG | XT5LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT5LSI | XT5LSI0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■ |  | XT5LSIG | XT5LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT5LSIG | XT5LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT5LSI | XT5LSI0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■ |  | XT5LSIG | XT5LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT5LSIG | XT5LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT5LSI | XT5LSI0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■ |  | XT5LSIG | XT5LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT5LSIG | XT5LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT5LSI | XT5LSI0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■ |  | XT5LSIG | XT5LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT5LSIG | XT5LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT5LSI | XT5LSI1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■ |  | XT6LSIG | XT6LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT6LSIG | XT6LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT6LSI | XT6LSI0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□ |  | XT6LSIG | XT6LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT6LSIG | XT6LSIG1 | 1 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT6LSI | XT6LSI0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□ |  | XT6LSIG | XT6LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT6LSIG | XT6LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT6LSI | XT6LSI0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□ |  | XT6LSIG | XT6LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT6LSIG | XT6LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT6LSI | XT6LSI0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□ |  | XT6LSIG | XT6LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT6LSIG | XT6LSIG2.5 | 2.5 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT6LSI | XT6LSI0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□ |  | XT6LSIG | XT6LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT6LSIG | XT6LSIG3 | 3 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT6LSI | XT6LSI0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□ |  | XT6LSIG | XT6LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT6LSIG | XT6LSIG3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT6LSI | XT6LSI0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□ |  | XT6LSIG | XT6LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT6LSIG | XT6LSIG4.5 | 4.5 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT6LSI | XT6LSI0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□ |  | XT6LSIG | XT6LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT6LSIG | XT6LSIG5.5 | 5.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT6LSI | XT6LSI0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□ |  | XT6LSIG | XT6LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT6LSIG | XT6LSIG6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT6LSI | XT6LSI0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□ |  | XT6LSIG | XT6LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT6LSIG | XT6LSIG7 | 7 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT6LSI | XT6LSI0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□ |  | XT6LSIG | XT6LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT6LSIG | XT6LSIG7.5 | 7.5 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT6LSI | XT6LSI0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□ |  | XT6LSIG | XT6LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT6LSIG | XT6LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT6LSI | XT6LSI0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□ |  | XT6LSIG | XT6LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT6LSIG | XT6LSIG8.5 | 8.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT6LSI | XT6LSI0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□ |  | XT6LSIG | XT6LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT6LSIG | XT6LSIG9 | 9 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT6LSI | XT6LSI0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□ |  | XT6LSIG | XT6LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT6LSIG | XT6LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT6LSI | XT6LSI0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□ |  |  | I2, XT7 LS/I | I2, XT7 LS/I | [9 empty] | I3, XT7 LS/I | I3, XT7 LS/I
XT6LSI | XT6LSI0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■
XT6LSI | XT6LSI0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■ |  | XT7LS/I | XT7LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT7LS/I | XT7LS/IOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT6LSI | XT6LSI0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■ |  | XT7LS/I | XT7LS/I1 | 1 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT7LS/I | XT7LS/I1 | 1 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT6LSI | XT6LSI0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■ |  | XT7LS/I | XT7LS/I1.5 | 1.5 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT7LS/I | XT7LS/I1.5 | 1.5 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT6LSI | XT6LSI0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■ |  | XT7LS/I | XT7LS/I2 | 2 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT7LS/I | XT7LS/I2 | 2 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT6LSI | XT6LSI0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■ |  | XT7LS/I | XT7LS/I2.5 | 2.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT7LS/I | XT7LS/I2.5 | 2.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT6LSI | XT6LSI0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■ |  | XT7LS/I | XT7LS/I3 | 3 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT7LS/I | XT7LS/I3 | 3 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT6LSI | XT6LSI0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■ |  | XT7LS/I | XT7LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT7LS/I | XT7LS/I3.5 | 3.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT6LSI | XT6LSI0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■ |  | XT7LS/I | XT7LS/I4.5 | 4.5 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT7LS/I | XT7LS/I4.5 | 4.5 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT6LSI | XT6LSI0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■ |  | XT7LS/I | XT7LS/I5.5 | 5.5 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT7LS/I | XT7LS/I5.5 | 5.5 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT6LSI | XT6LSI0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■ |  | XT7LS/I | XT7LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT7LS/I | XT7LS/I6.5 | 6.5 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT6LSI | XT6LSI0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■ |  | XT7LS/I | XT7LS/I7 | 7 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT7LS/I | XT7LS/I7 | 7 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT6LSI | XT6LSI0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■ |  | XT7LS/I | XT7LS/I7.5 | 7.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT7LS/I | XT7LS/I7.5 | 7.5 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT6LSI | XT6LSI0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■ |  | XT7LS/I | XT7LS/I8 | 8 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT7LS/I | XT7LS/I8 | 8 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT6LSI | XT6LSI1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■ |  | XT7LS/I | XT7LS/I8.5 | 8.5 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT7LS/I | XT7LS/I8.5 | 8.5 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT2LSIG | XT2LSIG0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□ |  | XT7LS/I | XT7LS/I9 | 9 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT7LS/I | XT7LS/I9 | 9 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT2LSIG | XT2LSIG0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□ |  | XT7LS/I | XT7LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT7LS/I | XT7LS/I10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT2LSIG | XT2LSIG0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□ |  |  | I2, XT7 LSI and LSIG | I2, XT7 LSI and LSIG | [9 empty] | I3, XT7 LSI and LSIG | I3, XT7 LSI and LSIG
XT2LSIG | XT2LSIG0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□
XT2LSIG | XT2LSIG0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□ |  | XT7LSI | XT7LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT7LSI | XT7LSIOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT2LSIG | XT2LSIG0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□ |  | XT7LSI | XT7LSI0.6 | 0.6 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT7LSI | XT7LSI1.5 | 1.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT2LSIG | XT2LSIG0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□ |  | XT7LSI | XT7LSI0.8 | 0.8 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT7LSI | XT7LSI2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT2LSIG | XT2LSIG0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□ |  | XT7LSI | XT7LSI1 | 1 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT7LSI | XT7LSI3 | 3 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT2LSIG | XT2LSIG0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□ |  | XT7LSI | XT7LSI1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT7LSI | XT7LSI4 | 4 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT2LSIG | XT2LSIG0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□ |  | XT7LSI | XT7LSI2 | 2 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT7LSI | XT7LSI5 | 5 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT2LSIG | XT2LSIG0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□ |  | XT7LSI | XT7LSI2.5 | 2.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT7LSI | XT7LSI6 | 6 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT2LSIG | XT2LSIG0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□ |  | XT7LSI | XT7LSI3 | 3 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT7LSI | XT7LSI7 | 7 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT2LSIG | XT2LSIG0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□ |  | XT7LSI | XT7LSI3.5 | 3.5 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT7LSI | XT7LSI8 | 8 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT2LSIG | XT2LSIG0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□ |  | XT7LSI | XT7LSI4 | 4 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT7LSI | XT7LSI9 | 9 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT2LSIG | XT2LSIG0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□ |  | XT7LSI | XT7LSI5 | 5 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT7LSI | XT7LSI10 | 10 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT2LSIG | XT2LSIG0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□ |  | XT7LSI | XT7LSI6 | 6 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT7LSI | XT7LSI11 | 11 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT2LSIG | XT2LSIG0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■ |  | XT7LSI | XT7LSI7 | 7 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT7LSI | XT7LSI12 | 12 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT2LSIG | XT2LSIG0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■ |  | XT7LSI | XT7LSI8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT7LSI | XT7LSI13 | 13 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT2LSIG | XT2LSIG0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■ |  | XT7LSI | XT7LSI9 | 9 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT7LSI | XT7LSI14 | 14 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT2LSIG | XT2LSIG0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■ |  | XT7LSI | XT7LSI10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT7LSI | XT7LSI15 | 15 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT2LSIG | XT2LSIG0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■ |  | XT7LSIG | XT7LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | XT7LSIG | XT7LSIGOFF | OFF | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□
XT2LSIG | XT2LSIG0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■ |  | XT7LSIG | XT7LSIG0.6 | 0.6 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■ | XT7LSIG | XT7LSIG1.5 | 1.5 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | □■
XT2LSIG | XT2LSIG0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■ |  | XT7LSIG | XT7LSIG0.8 | 0.8 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□ | XT7LSIG | XT7LSIG2 | 2 | 0 | 0 | 1 | 0 | ■□ | ■□ | □■ | ■□
XT2LSIG | XT2LSIG0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■ |  | XT7LSIG | XT7LSIG1 | 1 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■ | XT7LSIG | XT7LSIG3 | 3 | 0 | 0 | 1 | 1 | ■□ | ■□ | □■ | □■
XT2LSIG | XT2LSIG0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■ |  | XT7LSIG | XT7LSIG1.5 | 1.5 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□ | XT7LSIG | XT7LSIG4 | 4 | 0 | 1 | 0 | 0 | ■□ | □■ | ■□ | ■□
XT2LSIG | XT2LSIG0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■ |  | XT7LSIG | XT7LSIG2 | 2 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■ | XT7LSIG | XT7LSIG5 | 5 | 0 | 1 | 0 | 1 | ■□ | □■ | ■□ | □■
XT2LSIG | XT2LSIG0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■ |  | XT7LSIG | XT7LSIG2.5 | 2.5 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□ | XT7LSIG | XT7LSIG6 | 6 | 0 | 1 | 1 | 0 | ■□ | □■ | □■ | ■□
XT2LSIG | XT2LSIG0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■ |  | XT7LSIG | XT7LSIG3 | 3 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■ | XT7LSIG | XT7LSIG7 | 7 | 0 | 1 | 1 | 1 | ■□ | □■ | □■ | □■
XT2LSIG | XT2LSIG0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■ |  | XT7LSIG | XT7LSIG3.5 | 3.5 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | XT7LSIG | XT7LSIG8 | 8 | 1 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□
XT2LSIG | XT2LSIG0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■ |  | XT7LSIG | XT7LSIG4 | 4 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■ | XT7LSIG | XT7LSIG9 | 9 | 1 | 0 | 0 | 1 | □■ | ■□ | ■□ | □■
XT2LSIG | XT2LSIG1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■ |  | XT7LSIG | XT7LSIG5 | 5 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□ | XT7LSIG | XT7LSIG10 | 10 | 1 | 0 | 1 | 0 | □■ | ■□ | □■ | ■□
XT4LSIG | XT4LSIG0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□ |  | XT7LSIG | XT7LSIG6 | 6 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■ | XT7LSIG | XT7LSIG11 | 11 | 1 | 0 | 1 | 1 | □■ | ■□ | □■ | □■
XT4LSIG | XT4LSIG0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□ |  | XT7LSIG | XT7LSIG7 | 7 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□ | XT7LSIG | XT7LSIG12 | 12 | 1 | 1 | 0 | 0 | □■ | □■ | ■□ | ■□
XT4LSIG | XT4LSIG0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□ |  | XT7LSIG | XT7LSIG8 | 8 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■ | XT7LSIG | XT7LSIG13 | 13 | 1 | 1 | 0 | 1 | □■ | □■ | ■□ | □■
XT4LSIG | XT4LSIG0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□ |  | XT7LSIG | XT7LSIG9 | 9 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□ | XT7LSIG | XT7LSIG14 | 14 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | ■□
XT4LSIG | XT4LSIG0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□ |  | XT7LSIG | XT7LSIG10 | 10 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■ | XT7LSIG | XT7LSIG15 | 15 | 1 | 1 | 1 | 1 | □■ | □■ | □■ | □■
XT4LSIG | XT4LSIG0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□
XT4LSIG | XT4LSIG0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□
XT4LSIG | XT4LSIG0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□
XT4LSIG | XT4LSIG0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□
XT4LSIG | XT4LSIG0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□
XT4LSIG | XT4LSIG0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□
XT4LSIG | XT4LSIG0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□
XT4LSIG | XT4LSIG0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□
XT4LSIG | XT4LSIG0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□
XT4LSIG | XT4LSIG0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□
XT4LSIG | XT4LSIG0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□
XT4LSIG | XT4LSIG0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■
XT4LSIG | XT4LSIG0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■
XT4LSIG | XT4LSIG0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■
XT4LSIG | XT4LSIG0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■
XT4LSIG | XT4LSIG0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■
XT4LSIG | XT4LSIG0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■
XT4LSIG | XT4LSIG0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■
XT4LSIG | XT4LSIG0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■
XT4LSIG | XT4LSIG0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■
XT4LSIG | XT4LSIG0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■
XT4LSIG | XT4LSIG0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■
XT4LSIG | XT4LSIG0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■
XT4LSIG | XT4LSIG0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■
XT4LSIG | XT4LSIG0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■
XT4LSIG | XT4LSIG1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■
XT5LSIG | XT5LSIG0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□
XT5LSIG | XT5LSIG0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□
XT5LSIG | XT5LSIG0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□
XT5LSIG | XT5LSIG0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□
XT5LSIG | XT5LSIG0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□
XT5LSIG | XT5LSIG0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□
XT5LSIG | XT5LSIG0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□
XT5LSIG | XT5LSIG0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□
XT5LSIG | XT5LSIG0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□
XT5LSIG | XT5LSIG0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□
XT5LSIG | XT5LSIG0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□
XT5LSIG | XT5LSIG0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□
XT5LSIG | XT5LSIG0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□
XT5LSIG | XT5LSIG0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□
XT5LSIG | XT5LSIG0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□
XT5LSIG | XT5LSIG0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□
XT5LSIG | XT5LSIG0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■
XT5LSIG | XT5LSIG0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■
XT5LSIG | XT5LSIG0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■
XT5LSIG | XT5LSIG0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■
XT5LSIG | XT5LSIG0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■
XT5LSIG | XT5LSIG0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■
XT5LSIG | XT5LSIG0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■
XT5LSIG | XT5LSIG0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■
XT5LSIG | XT5LSIG0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■
XT5LSIG | XT5LSIG0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■
XT5LSIG | XT5LSIG0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■
XT5LSIG | XT5LSIG0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■
XT5LSIG | XT5LSIG0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■
XT5LSIG | XT5LSIG0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■
XT5LSIG | XT5LSIG1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■
XT6LSIG | XT6LSIG0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | ■□ | ■□
XT6LSIG | XT6LSIG0.42 | 0.42 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | ■□ | ■□
XT6LSIG | XT6LSIG0.44 | 0.44 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | ■□ | ■□
XT6LSIG | XT6LSIG0.46 | 0.46 | 1 | 1 | 0 | 0 | 0 | □■ | □■ | ■□ | ■□ | ■□
XT6LSIG | XT6LSIG0.48 | 0.48 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | ■□ | ■□
XT6LSIG | XT6LSIG0.5 | 0.5 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | ■□ | ■□
XT6LSIG | XT6LSIG0.52 | 0.52 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | ■□ | ■□
XT6LSIG | XT6LSIG0.54 | 0.54 | 1 | 1 | 1 | 0 | 0 | □■ | □■ | □■ | ■□ | ■□
XT6LSIG | XT6LSIG0.56 | 0.56 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | □■ | ■□
XT6LSIG | XT6LSIG0.58 | 0.58 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | □■ | ■□
XT6LSIG | XT6LSIG0.6 | 0.6 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | □■ | ■□
XT6LSIG | XT6LSIG0.62 | 0.62 | 1 | 1 | 0 | 1 | 0 | □■ | □■ | ■□ | □■ | ■□
XT6LSIG | XT6LSIG0.64 | 0.64 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | □■ | ■□
XT6LSIG | XT6LSIG0.66 | 0.66 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | □■ | ■□
XT6LSIG | XT6LSIG0.68 | 0.68 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | □■ | ■□
XT6LSIG | XT6LSIG0.7 | 0.7 | 1 | 1 | 1 | 1 | 0 | □■ | □■ | □■ | □■ | ■□
XT6LSIG | XT6LSIG0.72 | 0.72 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | ■□ | □■
XT6LSIG | XT6LSIG0.74 | 0.74 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | ■□ | □■
XT6LSIG | XT6LSIG0.76 | 0.76 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | ■□ | □■
XT6LSIG | XT6LSIG0.78 | 0.78 | 1 | 1 | 0 | 0 | 1 | □■ | □■ | ■□ | ■□ | □■
XT6LSIG | XT6LSIG0.8 | 0.8 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | ■□ | □■
XT6LSIG | XT6LSIG0.82 | 0.82 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | ■□ | □■
XT6LSIG | XT6LSIG0.84 | 0.84 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | ■□ | □■
XT6LSIG | XT6LSIG0.86 | 0.86 | 1 | 1 | 1 | 0 | 1 | □■ | □■ | □■ | ■□ | □■
XT6LSIG | XT6LSIG0.88 | 0.88 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | □■ | □■
XT6LSIG | XT6LSIG0.9 | 0.9 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | □■ | □■
XT6LSIG | XT6LSIG0.92 | 0.92 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | □■ | □■
XT6LSIG | XT6LSIG0.94 | 0.94 | 1 | 1 | 0 | 1 | 1 | □■ | □■ | ■□ | □■ | □■
XT6LSIG | XT6LSIG0.96 | 0.96 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | □■ | □■
XT6LSIG | XT6LSIG0.98 | 0.98 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | □■ | □■
XT6LSIG | XT6LSIG1 | 1 | X | 1 | 1 | 1 | 1 | □□ | □■ | □■ | □■ | □■
| I1, LSI and LSIG, XT7 | I1, LSI and LSIG, XT7
XT7LSI | XT7LSI0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | + | ■□ | ■□
XT7LSI | XT7LSI0.42 | 0.42 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | + | ■□ | □■
XT7LSI | XT7LSI0.45 | 0.45 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | + | □■ | ■□
XT7LSI | XT7LSI0.47 | 0.47 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | + | □■ | □■
XT7LSI | XT7LSI0.5 | 0.5 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | + | ■□ | ■□
XT7LSI | XT7LSI0.52 | 0.52 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | + | ■□ | □■
XT7LSI | XT7LSI0.55 | 0.55 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | + | □■ | ■□
XT7LSI | XT7LSI0.57 | 0.57 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | + | □■ | □■
XT7LSI | XT7LSI0.6 | 0.6 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | + | ■□ | ■□
XT7LSI | XT7LSI0.62 | 0.62 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | + | ■□ | □■
XT7LSI | XT7LSI0.65 | 0.65 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | + | □■ | ■□
XT7LSI | XT7LSI0.67 | 0.67 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | + | □■ | □■
XT7LSI | XT7LSI0.7 | 0.7 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | + | ■□ | ■□
XT7LSI | XT7LSI0.72 | 0.72 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | + | ■□ | □■
XT7LSI | XT7LSI0.75 | 0.75 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | + | □■ | ■□
XT7LSI | XT7LSI0.77 | 0.77 | 0 | 1 | 1 | 1 | 1 | ■□ | □■ | □■ | + | □■ | □■
XT7LSI | XT7LSI0.8 | 0.8 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | + | ■□ | ■□
XT7LSI | XT7LSI0.82 | 0.82 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | + | ■□ | □■
XT7LSI | XT7LSI0.85 | 0.85 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | + | □■ | ■□
XT7LSI | XT7LSI0.87 | 0.87 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | + | □■ | □■
XT7LSI | XT7LSI0.9 | 0.9 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | + | ■□ | ■□
XT7LSI | XT7LSI0.92 | 0.92 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | + | ■□ | □■
XT7LSI | XT7LSI0.95 | 0.95 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | + | □■ | ■□
XT7LSI | XT7LSI0.97 | 0.97 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | + | □■ | □■
XT7LSI | XT7LSI1 | 1 | 1 | 1 | 0 | X | X | □■ | □■ | ■□ | + | □□ | □□
XT7LSIG | XT7LSIG0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | ■□ | ■□ | ■□ | + | ■□ | ■□
XT7LSIG | XT7LSIG0.42 | 0.42 | 0 | 0 | 0 | 0 | 1 | ■□ | ■□ | ■□ | + | ■□ | □■
XT7LSIG | XT7LSIG0.45 | 0.45 | 0 | 0 | 0 | 1 | 0 | ■□ | ■□ | ■□ | + | □■ | ■□
XT7LSIG | XT7LSIG0.47 | 0.47 | 0 | 0 | 0 | 1 | 1 | ■□ | ■□ | ■□ | + | □■ | □■
XT7LSIG | XT7LSIG0.5 | 0.5 | 0 | 0 | 1 | 0 | 0 | ■□ | ■□ | □■ | + | ■□ | ■□
XT7LSIG | XT7LSIG0.52 | 0.52 | 0 | 0 | 1 | 0 | 1 | ■□ | ■□ | □■ | + | ■□ | □■
XT7LSIG | XT7LSIG0.55 | 0.55 | 0 | 0 | 1 | 1 | 0 | ■□ | ■□ | □■ | + | □■ | ■□
XT7LSIG | XT7LSIG0.57 | 0.57 | 0 | 0 | 1 | 1 | 1 | ■□ | ■□ | □■ | + | □■ | □■
XT7LSIG | XT7LSIG0.6 | 0.6 | 0 | 1 | 0 | 0 | 0 | ■□ | □■ | ■□ | + | ■□ | ■□
XT7LSIG | XT7LSIG0.62 | 0.62 | 0 | 1 | 0 | 0 | 1 | ■□ | □■ | ■□ | + | ■□ | □■
XT7LSIG | XT7LSIG0.65 | 0.65 | 0 | 1 | 0 | 1 | 0 | ■□ | □■ | ■□ | + | □■ | ■□
XT7LSIG | XT7LSIG0.67 | 0.67 | 0 | 1 | 0 | 1 | 1 | ■□ | □■ | ■□ | + | □■ | □■
XT7LSIG | XT7LSIG0.7 | 0.7 | 0 | 1 | 1 | 0 | 0 | ■□ | □■ | □■ | + | ■□ | ■□
XT7LSIG | XT7LSIG0.72 | 0.72 | 0 | 1 | 1 | 0 | 1 | ■□ | □■ | □■ | + | ■□ | □■
XT7LSIG | XT7LSIG0.75 | 0.75 | 0 | 1 | 1 | 1 | 0 | ■□ | □■ | □■ | + | □■ | ■□
XT7LSIG | XT7LSIG0.77 | 0.77 | 0 | 1 | 1 | 1 | 1 | ■□ | □■ | □■ | + | □■ | □■
XT7LSIG | XT7LSIG0.8 | 0.8 | 1 | 0 | 0 | 0 | 0 | □■ | ■□ | ■□ | + | ■□ | ■□
XT7LSIG | XT7LSIG0.82 | 0.82 | 1 | 0 | 0 | 0 | 1 | □■ | ■□ | ■□ | + | ■□ | □■
XT7LSIG | XT7LSIG0.85 | 0.85 | 1 | 0 | 0 | 1 | 0 | □■ | ■□ | ■□ | + | □■ | ■□
XT7LSIG | XT7LSIG0.87 | 0.87 | 1 | 0 | 0 | 1 | 1 | □■ | ■□ | ■□ | + | □■ | □■
XT7LSIG | XT7LSIG0.9 | 0.9 | 1 | 0 | 1 | 0 | 0 | □■ | ■□ | □■ | + | ■□ | ■□
XT7LSIG | XT7LSIG0.92 | 0.92 | 1 | 0 | 1 | 0 | 1 | □■ | ■□ | □■ | + | ■□ | □■
XT7LSIG | XT7LSIG0.95 | 0.95 | 1 | 0 | 1 | 1 | 0 | □■ | ■□ | □■ | + | □■ | ■□
XT7LSIG | XT7LSIG0.97 | 0.97 | 1 | 0 | 1 | 1 | 1 | □■ | ■□ | □■ | + | □■ | □■
XT7LSIG | XT7LSIG1 | 1 | 1 | 1 | 0 | X | X | □■ | □■ | ■□ | + | □□ | □□

## Breaker Schedule
| ABB |  |  |  | Instructions: To avoid errors, data must be entered using drop-down cells according to the following sequence: 1. Frame Size (XT2, XT4, XT5, XT6 or XT7) 2. In - Nominal rating(6) 3. Trip Unit (LS/I, LSI or LSIG) 4. Current thresholds I1, I2, I3, I4 as applicable
__
SACE® Tmax® XT MCCBs Ekip® Dip trip unit settings summary
| Project name/location: | Your project
|  | Breaker data(6, 7) |  |  | L - Long-time pickup(2, 4) |  |  | S - Short-time pickup(1, 3, 4, 5) |  |  | I - Instantaneous pickup(1, 3, 5) |  |  | G - Ground Fault
Ln | Breaker tag | Frame Size | In (A) | Trip Unit | I1 (A) | x | Dip switches | I2 (A) | x | Dip sw. | I3 (A) | x | Dip sw. | I4 (A) | x | Dip sw. | Notes: |  |  | In | In | In | In | In | In | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I1 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I2 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I3 | I4 | I4 | I4 | I4 | I4 | I4 | I4 | I4
1 | breaker 1 |  |  |  |  | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | ■□ | set dip switch to OFF position | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
2 | breaker 2 |  |  |  |  | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | □■ | set dip switch to ON position | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
3 | breaker 3 |  |  |  |  | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | □□ | dip switch can be set either to ON or OFF | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | breaker 4 |  |  |  |  | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (1) | only 'S' short-time or 'I' Instantaneous is selectable in LS/I breakers | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | breaker 5 |  |  |  |  | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (2) | Long-time pick up 'L' cannot exceed nominal current (In) | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (3) | "OFF" for 'S' and 'I' settings default to fixed instantaneous override | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
7 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (4) | Parameter incosisency if 'L' = 'S' All LED indicators blinking | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
8 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (5) | Parameter incosisency if 'S' ≥ 'I' All LED indicators blinking | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
9 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (6) | Available ratings (In) by frame size: XT2: 10, 25, 60, 100, 125 XT4: 40, 60, 100, 150, 225, 250 XT5: 250, 300, 400, 600 XT6: 600, 800 XT7: 600, 800, 1000, 1200 | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | (7) | for XT2-XT4, LSI or LSIG, set dip switches to 'Loc' and 'MAN': | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
15 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
16 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
17 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  | For troubleshooting / complete technical information, consult instruction manual |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
18 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
20 | [5 empty] | 0 |  |  | OFF |  |  | OFF |  |  | OFF |  |  |  | X | [37 empty] | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
The Ekip Dip Trip Unit Settings Guide is made available "as is" and with no express warranty. ABB further disclaims all other statutory and implied warranties, including, but not limited to, any warranty of fitness for particular purpose or merchantability. By acceptance and use of the Guide, User and User's Company agree that in no event will ABB be liable to the User or User's Company for any claims, liabilities, or damages even if caused by the negligence of ABB, and under no circumstances will ABB be liable for any indirect, special, incidental or consequential damages. User and User's Company are solely responsible for trip unit installation and settings which should be conducted by a certified engineer determined by User/User's Company.
ABB reserves the right to make technical changes or modify the contents of this document without prior notice. With regard to purchase orders, the agreed particulars shall prevail. ABB does not accept any responsibility whatsoever for potential errors or possible lack of information in this document. ABB reserves all rights in this document and in the subject matter and illustrations contained therein. Any reproduction, disclosure to third parties or utilization of its contents – in whole or in parts – is forbidden without prior written consent of ABB. ©2021 ABB. All rights reserved.

## XT2, LS-I
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [10 empty] | ← Short-time pickup (I2) / Instantaneous pickup (I3)
0 | current threshold | [9 empty] | 0 | current threshold
XT2 | In x (0.4 + Σ) |  |  |  | I1 - ANSI 49 | [5 empty] | XT2 | In x Σ |  |  |  | I2 / I3 - ANSI 51 / 50
Current Threshold | 0.04 | 0.08 | 0.16 | 0.32 | 10 | 25 | 60 | 100 | 125 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 10 | 25 | 60 | 100 | 125 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4 | 10 | 24 | 40 | 50 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.4 | 11 | 26.4 | 44 | 55 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.8 | 12 | 28.8 | 48 | 60 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 15 | 37.5 | 90 | 150 | 187.5 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.2 | 13 | 31.2 | 52 | 65 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 50 | 120 | 200 | 250 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.6 | 14 | 33.6 | 56 | 70 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25 | 62.5 | 150 | 250 | 312.5 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6 | 15 | 36 | 60 | 75 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30 | 75 | 180 | 300 | 375 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.4 | 16 | 38.4 | 64 | 80 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35 | 87.5 | 210 | 350 | 437.5 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.8 | 17 | 40.8 | 68 | 85 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 45 | 112.5 | 270 | 450 | 562.5 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.2 | 18 | 43.2 | 72 | 90 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 55 | 137.5 | 330 | 550 | 687.5 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.6 | 19 | 45.6 | 76 | 95 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 65 | 162.5 | 390 | 650 | 812.5 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8 | 20 | 48 | 80 | 100 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 70 | 175 | 420 | 700 | 875 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.4 | 21 | 50.4 | 84 | 105 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 75 | 187.5 | 450 | 750 | 937.5 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.8 | 22 | 52.8 | 88 | 110 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 200 | 480 | 800 | 1000 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.2 | 23 | 55.2 | 92 | 115 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 85 | 212.5 | 510 | 850 | 1062.5 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.6 | 24 | 57.6 | 96 | 120 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 90 | 225 | 540 | 900 | 1125 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 250 | 600 | 1000 | 1250 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT2, LSI
← Nominal (maximum amps) rating (In)
for XT2-XT4, LSI or LSIG,
set dip switches to 'Loc' and 'MAN'
| ← Long-time pickup (I1) | [11 empty] | ← Short-time pickup (I2) | [10 empty] | ← Instantaneous pickup (I3)
0 | current threshold | [10 empty] | 0 | current threshold | [9 empty] | 0 | current threshold
XT2 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 | [5 empty] | XT2 | In x Σ |  |  |  | I2 - ANSI 51 | [5 empty] | XT2 | In x Σ |  |  |  | I3 - ANSI 50
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 10 | 25 | 60 | 100 | 125 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 10 | 25 | 60 | 100 | 125 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 10 | 25 | 60 | 100 | 125 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4 | 10 | 24 | 40 | 50 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.2 | 10.5 | 25.2 | 42 | 52.5 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.4 | 11 | 26.4 | 44 | 55 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 15 | 37.5 | 90 | 150 | 187.5 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 15 | 37.5 | 90 | 150 | 187.5 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.6 | 11.5 | 27.6 | 46 | 57.5 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 50 | 120 | 200 | 250 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 50 | 120 | 200 | 250 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.8 | 12 | 28.8 | 48 | 60 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25 | 62.5 | 150 | 250 | 312.5 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25 | 62.5 | 150 | 250 | 312.5 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5 | 12.5 | 30 | 50 | 62.5 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30 | 75 | 180 | 300 | 375 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30 | 75 | 180 | 300 | 375 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.2 | 13 | 31.2 | 52 | 65 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35 | 87.5 | 210 | 350 | 437.5 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35 | 87.5 | 210 | 350 | 437.5 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.4 | 13.5 | 32.4 | 54 | 67.5 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 45 | 112.5 | 270 | 450 | 562.5 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 45 | 112.5 | 270 | 450 | 562.5 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.6 | 14 | 33.6 | 56 | 70 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 55 | 137.5 | 330 | 550 | 687.5 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 55 | 137.5 | 330 | 550 | 687.5 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.8 | 14.5 | 34.8 | 58 | 72.5 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 65 | 162.5 | 390 | 650 | 812.5 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 65 | 162.5 | 390 | 650 | 812.5 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6 | 15 | 36 | 60 | 75 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 70 | 175 | 420 | 700 | 875 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 70 | 175 | 420 | 700 | 875 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.2 | 15.5 | 37.2 | 62 | 77.5 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 75 | 187.5 | 450 | 750 | 937.5 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 75 | 187.5 | 450 | 750 | 937.5 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.4 | 16 | 38.4 | 64 | 80 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 200 | 480 | 800 | 1000 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 200 | 480 | 800 | 1000 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.6 | 16.5 | 39.6 | 66 | 82.5 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 85 | 212.5 | 510 | 850 | 1062.5 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 85 | 212.5 | 510 | 850 | 1062.5 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.8 | 17 | 40.8 | 68 | 85 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 90 | 225 | 540 | 900 | 1125 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 90 | 225 | 540 | 900 | 1125 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7 | 17.5 | 42 | 70 | 87.5 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 250 | 600 | 1000 | 1250 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 250 | 600 | 1000 | 1250 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.2 | 18 | 43.2 | 72 | 90 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.4 | 18.5 | 44.4 | 74 | 92.5 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.6 | 19 | 45.6 | 76 | 95 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.8 | 19.5 | 46.8 | 78 | 97.5 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8 | 20 | 48 | 80 | 100 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.2 | 20.5 | 49.2 | 82 | 102.5 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.4 | 21 | 50.4 | 84 | 105 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.6 | 21.5 | 51.6 | 86 | 107.5 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.8 | 22 | 52.8 | 88 | 110 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9 | 22.5 | 54 | 90 | 112.5 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.2 | 23 | 55.2 | 92 | 115 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.4 | 23.5 | 56.4 | 94 | 117.5 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.6 | 24 | 57.6 | 96 | 120 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.8 | 24.5 | 58.8 | 98 | 122.5 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT2, LSIG
← Nominal (maximum amps) rating (In)
for XT2-XT4, LSI or LSIG,
set dip switches to 'Loc' and 'MAN'
| ← Long-time pickup (I1) | [11 empty] | ← Short-time pickup (I2) | [10 empty] | ← Instantaneous pickup (I3) | [10 empty] | ← Ground fault (I4)
0 | current threshold | [10 empty] | 0 | current threshold | [9 empty] | 0 | current threshold | [9 empty] | 0 | current threshold
XT2 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 | [5 empty] | XT2 | In x Σ |  |  |  | I2 - ANSI 51 | [5 empty] | XT2 | In x Σ |  |  |  | I3 - ANSI 50 | [5 empty] | XT2 | In x Σ |  |  | I4 - ANSI 51N
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 10 | 25 | 60 | 100 | 125 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 10 | 25 | 60 | 100 | 125 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 10 | 25 | 60 | 100 | 125 | 6 | Current Threshold | 0.2 | 0.25 | 0.55 | 10 | 25 | 60 | 100 | 125 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4 | 10 | 24 | 40 | 50 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.2 | 10.5 | 25.2 | 42 | 52.5 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0 | 0.2 | ▪▪ | ▪▪ | ▪▪ | 2 | 5 | 12 | 20 | 25 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.4 | 11 | 26.4 | 44 | 55 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 15 | 37.5 | 90 | 150 | 187.5 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 15 | 37.5 | 90 | 150 | 187.5 | 0 | 0.25 | ▪▪ | ▪▪ | ▪▪ | 2.5 | 6.25 | 15 | 25 | 31.25 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.6 | 11.5 | 27.6 | 46 | 57.5 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 50 | 120 | 200 | 250 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 50 | 120 | 200 | 250 | 0 | 0.45 | ▪▪ | ▪▪ | ▪▪ | 4.5 | 11.25 | 27 | 45 | 56.25 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4.8 | 12 | 28.8 | 48 | 60 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25 | 62.5 | 150 | 250 | 312.5 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25 | 62.5 | 150 | 250 | 312.5 | 0 | 0.55 | ▪▪ | ▪▪ | ▪▪ | 5.5 | 13.75 | 33 | 55 | 68.75 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5 | 12.5 | 30 | 50 | 62.5 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30 | 75 | 180 | 300 | 375 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30 | 75 | 180 | 300 | 375 | 0 | 0.75 | ▪▪ | ▪▪ | ▪▪ | 7.5 | 18.75 | 45 | 75 | 93.75 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.2 | 13 | 31.2 | 52 | 65 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35 | 87.5 | 210 | 350 | 437.5 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35 | 87.5 | 210 | 350 | 437.5 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | 8 | 20 | 48 | 80 | 100 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.4 | 13.5 | 32.4 | 54 | 67.5 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 45 | 112.5 | 270 | 450 | 562.5 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 45 | 112.5 | 270 | 450 | 562.5 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.6 | 14 | 33.6 | 56 | 70 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 55 | 137.5 | 330 | 550 | 687.5 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 55 | 137.5 | 330 | 550 | 687.5 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5.8 | 14.5 | 34.8 | 58 | 72.5 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 65 | 162.5 | 390 | 650 | 812.5 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 65 | 162.5 | 390 | 650 | 812.5 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6 | 15 | 36 | 60 | 75 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 70 | 175 | 420 | 700 | 875 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 70 | 175 | 420 | 700 | 875 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.2 | 15.5 | 37.2 | 62 | 77.5 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 75 | 187.5 | 450 | 750 | 937.5 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 75 | 187.5 | 450 | 750 | 937.5 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.4 | 16 | 38.4 | 64 | 80 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 200 | 480 | 800 | 1000 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 200 | 480 | 800 | 1000 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.6 | 16.5 | 39.6 | 66 | 82.5 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 85 | 212.5 | 510 | 850 | 1062.5 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 85 | 212.5 | 510 | 850 | 1062.5 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6.8 | 17 | 40.8 | 68 | 85 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 90 | 225 | 540 | 900 | 1125 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 90 | 225 | 540 | 900 | 1125 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7 | 17.5 | 42 | 70 | 87.5 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 250 | 600 | 1000 | 1250 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 250 | 600 | 1000 | 1250 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.2 | 18 | 43.2 | 72 | 90 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.4 | 18.5 | 44.4 | 74 | 92.5 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.6 | 19 | 45.6 | 76 | 95 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7.8 | 19.5 | 46.8 | 78 | 97.5 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8 | 20 | 48 | 80 | 100 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.2 | 20.5 | 49.2 | 82 | 102.5 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.4 | 21 | 50.4 | 84 | 105 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.6 | 21.5 | 51.6 | 86 | 107.5 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8.8 | 22 | 52.8 | 88 | 110 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9 | 22.5 | 54 | 90 | 112.5 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.2 | 23 | 55.2 | 92 | 115 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.4 | 23.5 | 56.4 | 94 | 117.5 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.6 | 24 | 57.6 | 96 | 120 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9.8 | 24.5 | 58.8 | 98 | 122.5 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 10 | 25 | 60 | 100 | 125 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT4, LS-I
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [11 empty] | ← Short-time pickup (I2) / Instantaneous pickup (I3)
0 | current threshold | [10 empty] | 0 | current threshold
XT4 | In x (0.4 + Σ) |  |  |  | I1 - ANSI 49 | [6 empty] | XT4 | In x Σ |  |  |  | I2 / I3 - ANSI 51 / 50
Current Threshold | 0.04 | 0.08 | 0.16 | 0.32 | 40 | 60 | 100 | 150 | 225 | 250 | 7 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 40 | 60 | 100 | 150 | 225 | 250 | 7
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 16 | 24 | 40 | 60 | 90 | 100 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | OFF | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 17.6 | 26.4 | 44 | 66 | 99 | 110 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 19.2 | 28.8 | 48 | 72 | 108 | 120 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 60 | 90 | 150 | 225 | 337.5 | 375 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20.8 | 31.2 | 52 | 78 | 117 | 130 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 120 | 200 | 300 | 450 | 500 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 22.4 | 33.6 | 56 | 84 | 126 | 140 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 150 | 250 | 375 | 562.5 | 625 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 24 | 36 | 60 | 90 | 135 | 150 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 180 | 300 | 450 | 675 | 750 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25.6 | 38.4 | 64 | 96 | 144 | 160 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 210 | 350 | 525 | 787.5 | 875 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 27.2 | 40.8 | 68 | 102 | 153 | 170 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 270 | 450 | 675 | 1012.5 | 1125 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 28.8 | 43.2 | 72 | 108 | 162 | 180 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 330 | 550 | 825 | 1237.5 | 1375 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30.4 | 45.6 | 76 | 114 | 171 | 190 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 260 | 390 | 650 | 975 | 1462.5 | 1625 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 32 | 48 | 80 | 120 | 180 | 200 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 280 | 420 | 700 | 1050 | 1575 | 1750 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 33.6 | 50.4 | 84 | 126 | 189 | 210 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 450 | 750 | 1125 | 1687.5 | 1875 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35.2 | 52.8 | 88 | 132 | 198 | 220 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 320 | 480 | 800 | 1200 | 1800 | 2000 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 36.8 | 55.2 | 92 | 138 | 207 | 230 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 340 | 510 | 850 | 1275 | 1912.5 | 2125 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 38.4 | 57.6 | 96 | 144 | 216 | 240 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 540 | 900 | 1350 | 2025 | 2250 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 400 | 600 | 1000 | 1500 | 2250 | 2500 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT4, LSI
← Nominal (maximum amps) rating (In)
for XT2-XT4, LSI or LSIG,
set dip switches to 'Loc' and 'MAN'
| ← Long-time pickup (I1) | [12 empty] | ← Short-time pickup (I2) | [11 empty] | ← Instantaneous pickup (I3)
0 | current threshold | [11 empty] | 0 | current threshold | [10 empty] | 0 | current threshold
XT4 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 | [6 empty] | XT4 | In x Σ |  |  |  | I2 - ANSI 51 | [6 empty] | XT4 | In x Σ |  |  |  | I3 - ANSI 50
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 40 | 60 | 100 | 150 | 225 | 250 | 7 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 40 | 60 | 100 | 150 | 225 | 250 | 7 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 40 | 60 | 100 | 150 | 225 | 250 | 7
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 16 | 24 | 40 | 60 | 90 | 100 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 16.8 | 25.2 | 42 | 63 | 94.5 | 105 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 17.6 | 26.4 | 44 | 66 | 99 | 110 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 60 | 90 | 150 | 225 | 337.5 | 375 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 60 | 90 | 150 | 225 | 337.5 | 375 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 18.4 | 27.6 | 46 | 69 | 103.5 | 115 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 120 | 200 | 300 | 450 | 500 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 120 | 200 | 300 | 450 | 500 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 19.2 | 28.8 | 48 | 72 | 108 | 120 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 150 | 250 | 375 | 562.5 | 625 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 150 | 250 | 375 | 562.5 | 625 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 30 | 50 | 75 | 112.5 | 125 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 180 | 300 | 450 | 675 | 750 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 180 | 300 | 450 | 675 | 750 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20.8 | 31.2 | 52 | 78 | 117 | 130 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 210 | 350 | 525 | 787.5 | 875 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 210 | 350 | 525 | 787.5 | 875 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 21.6 | 32.4 | 54 | 81 | 121.5 | 135 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 270 | 450 | 675 | 1012.5 | 1125 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 270 | 450 | 675 | 1012.5 | 1125 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 22.4 | 33.6 | 56 | 84 | 126 | 140 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 330 | 550 | 825 | 1237.5 | 1375 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 330 | 550 | 825 | 1237.5 | 1375 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 23.2 | 34.8 | 58 | 87 | 130.5 | 145 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 260 | 390 | 650 | 975 | 1462.5 | 1625 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 260 | 390 | 650 | 975 | 1462.5 | 1625 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 24 | 36 | 60 | 90 | 135 | 150 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 280 | 420 | 700 | 1050 | 1575 | 1750 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 280 | 420 | 700 | 1050 | 1575 | 1750 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 24.8 | 37.2 | 62 | 93 | 139.5 | 155 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 450 | 750 | 1125 | 1687.5 | 1875 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 450 | 750 | 1125 | 1687.5 | 1875 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25.6 | 38.4 | 64 | 96 | 144 | 160 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 320 | 480 | 800 | 1200 | 1800 | 2000 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 320 | 480 | 800 | 1200 | 1800 | 2000 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 26.4 | 39.6 | 66 | 99 | 148.5 | 165 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 340 | 510 | 850 | 1275 | 1912.5 | 2125 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 340 | 510 | 850 | 1275 | 1912.5 | 2125 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 27.2 | 40.8 | 68 | 102 | 153 | 170 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 540 | 900 | 1350 | 2025 | 2250 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 540 | 900 | 1350 | 2025 | 2250 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 28 | 42 | 70 | 105 | 157.5 | 175 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 400 | 600 | 1000 | 1500 | 2250 | 2500 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 400 | 600 | 1000 | 1500 | 2250 | 2500 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 28.8 | 43.2 | 72 | 108 | 162 | 180 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 29.6 | 44.4 | 74 | 111 | 166.5 | 185 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30.4 | 45.6 | 76 | 114 | 171 | 190 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 31.2 | 46.8 | 78 | 117 | 175.5 | 195 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 32 | 48 | 80 | 120 | 180 | 200 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 32.8 | 49.2 | 82 | 123 | 184.5 | 205 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 33.6 | 50.4 | 84 | 126 | 189 | 210 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 34.4 | 51.6 | 86 | 129 | 193.5 | 215 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35.2 | 52.8 | 88 | 132 | 198 | 220 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 36 | 54 | 90 | 135 | 202.5 | 225 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 36.8 | 55.2 | 92 | 138 | 207 | 230 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 37.6 | 56.4 | 94 | 141 | 211.5 | 235 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 38.4 | 57.6 | 96 | 144 | 216 | 240 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 39.2 | 58.8 | 98 | 147 | 220.5 | 245 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT4, LSIG
← Nominal (maximum amps) rating (In)
for XT2-XT4, LSI or LSIG,
set dip switches to 'Loc' and 'MAN'
| ← Long-time pickup (I1) | [12 empty] | ← Short-time pickup (I2) | [11 empty] | ← Instantaneous pickup (I3) | [11 empty] | ← Ground fault (I4)
0 | current threshold | [11 empty] | 0 | current threshold | [10 empty] | 0 | current threshold | [10 empty] | 0 | current threshold
XT4 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 | [6 empty] | XT4 | In x Σ |  |  |  | I2 - ANSI 51 | [6 empty] | XT4 | In x Σ |  |  |  | I3 - ANSI 50 | [6 empty] | XT4 | In x Σ |  |  | I4 - ANSI 51N
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 40 | 60 | 100 | 150 | 225 | 250 | 7 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 40 | 60 | 100 | 150 | 225 | 250 | 7 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 40 | 60 | 100 | 150 | 225 | 250 | 7 | Current Threshold | 0.2 | 0.25 | 0.55 | 40 | 60 | 100 | 150 | 225 | 250 | 7
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 16 | 24 | 40 | 60 | 90 | 100 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 16.8 | 25.2 | 42 | 63 | 94.5 | 105 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0 | 0.2 | ▪▪ | ▪▪ | ▪▪ | 8 | 12 | 20 | 30 | 45 | 50 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 17.6 | 26.4 | 44 | 66 | 99 | 110 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 60 | 90 | 150 | 225 | 337.5 | 375 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 60 | 90 | 150 | 225 | 337.5 | 375 | 0 | 0.25 | ▪▪ | ▪▪ | ▪▪ | 10 | 15 | 25 | 37.5 | 56.25 | 62.5 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 18.4 | 27.6 | 46 | 69 | 103.5 | 115 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 120 | 200 | 300 | 450 | 500 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 80 | 120 | 200 | 300 | 450 | 500 | 0 | 0.45 | ▪▪ | ▪▪ | ▪▪ | 18 | 27 | 45 | 67.5 | 101.25 | 112.5 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 19.2 | 28.8 | 48 | 72 | 108 | 120 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 150 | 250 | 375 | 562.5 | 625 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 150 | 250 | 375 | 562.5 | 625 | 0 | 0.55 | ▪▪ | ▪▪ | ▪▪ | 22 | 33 | 55 | 82.5 | 123.75 | 137.5 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20 | 30 | 50 | 75 | 112.5 | 125 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 180 | 300 | 450 | 675 | 750 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 180 | 300 | 450 | 675 | 750 | 0 | 0.75 | ▪▪ | ▪▪ | ▪▪ | 30 | 45 | 75 | 112.5 | 168.75 | 187.5 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 20.8 | 31.2 | 52 | 78 | 117 | 130 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 210 | 350 | 525 | 787.5 | 875 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 210 | 350 | 525 | 787.5 | 875 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | 32 | 48 | 80 | 120 | 180 | 200 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 21.6 | 32.4 | 54 | 81 | 121.5 | 135 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 270 | 450 | 675 | 1012.5 | 1125 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 270 | 450 | 675 | 1012.5 | 1125 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 22.4 | 33.6 | 56 | 84 | 126 | 140 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 330 | 550 | 825 | 1237.5 | 1375 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 330 | 550 | 825 | 1237.5 | 1375 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 23.2 | 34.8 | 58 | 87 | 130.5 | 145 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 260 | 390 | 650 | 975 | 1462.5 | 1625 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 260 | 390 | 650 | 975 | 1462.5 | 1625 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 24 | 36 | 60 | 90 | 135 | 150 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 280 | 420 | 700 | 1050 | 1575 | 1750 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 280 | 420 | 700 | 1050 | 1575 | 1750 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 24.8 | 37.2 | 62 | 93 | 139.5 | 155 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 450 | 750 | 1125 | 1687.5 | 1875 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 450 | 750 | 1125 | 1687.5 | 1875 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 25.6 | 38.4 | 64 | 96 | 144 | 160 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 320 | 480 | 800 | 1200 | 1800 | 2000 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 320 | 480 | 800 | 1200 | 1800 | 2000 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 26.4 | 39.6 | 66 | 99 | 148.5 | 165 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 340 | 510 | 850 | 1275 | 1912.5 | 2125 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 340 | 510 | 850 | 1275 | 1912.5 | 2125 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 27.2 | 40.8 | 68 | 102 | 153 | 170 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 540 | 900 | 1350 | 2025 | 2250 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 540 | 900 | 1350 | 2025 | 2250 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 28 | 42 | 70 | 105 | 157.5 | 175 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 400 | 600 | 1000 | 1500 | 2250 | 2500 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 400 | 600 | 1000 | 1500 | 2250 | 2500 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 28.8 | 43.2 | 72 | 108 | 162 | 180 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 29.6 | 44.4 | 74 | 111 | 166.5 | 185 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 30.4 | 45.6 | 76 | 114 | 171 | 190 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 31.2 | 46.8 | 78 | 117 | 175.5 | 195 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 32 | 48 | 80 | 120 | 180 | 200 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 32.8 | 49.2 | 82 | 123 | 184.5 | 205 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 33.6 | 50.4 | 84 | 126 | 189 | 210 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 34.4 | 51.6 | 86 | 129 | 193.5 | 215 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 35.2 | 52.8 | 88 | 132 | 198 | 220 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 36 | 54 | 90 | 135 | 202.5 | 225 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 36.8 | 55.2 | 92 | 138 | 207 | 230 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 37.6 | 56.4 | 94 | 141 | 211.5 | 235 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 38.4 | 57.6 | 96 | 144 | 216 | 240 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 39.2 | 58.8 | 98 | 147 | 220.5 | 245 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 40 | 60 | 100 | 150 | 225 | 250 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT5, LS-I
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [9 empty] | ← Short-time pickup (I2) / Instantaneous pickup (I3)
0 | current threshold | [8 empty] | 0 | current threshold
XT5 | In x (0.4 + Σ) |  |  |  | I1 - ANSI 49 |  |  |  |  | XT5 | In x Σ |  |  |  | I2 / I3 - ANSI 51 / 50
Current Threshold | 0.04 | 0.08 | 0.16 | 0.32 | 250 | 300 | 400 | 600 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 250 | 300 | 400 | 600 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 120 | 160 | 240 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 110 | 132 | 176 | 264 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 144 | 192 | 288 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 375 | 450 | 600 | 900 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 130 | 156 | 208 | 312 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 500 | 600 | 800 | 1200 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 168 | 224 | 336 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 625 | 750 | 1000 | 1500 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 150 | 180 | 240 | 360 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 750 | 900 | 1200 | 1800 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 160 | 192 | 256 | 384 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 875 | 1050 | 1400 | 2100 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 170 | 204 | 272 | 408 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1125 | 1350 | 1800 | 2700 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 216 | 288 | 432 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1375 | 1650 | 2200 | 3300 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 190 | 228 | 304 | 456 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1625 | 1950 | 2600 | 3900 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 200 | 240 | 320 | 480 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1750 | 2100 | 2800 | 4200 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 210 | 252 | 336 | 504 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1875 | 2250 | 3000 | 4500 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 264 | 352 | 528 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2000 | 2400 | 3200 | 4800 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 230 | 276 | 368 | 552 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2125 | 2550 | 3400 | 5100 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 288 | 384 | 576 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2250 | 2700 | 3600 | 5400 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2500 | 3000 | 4000 | 6000 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT5, LSI
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [10 empty] | ← Short-time pickup (I2) | [9 empty] | ← Instantaneous pickup (I3)
0 | current threshold | [9 empty] | 0 | current threshold | [8 empty] | 0 | current threshold
XT5 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 |  |  |  |  | XT5 | In x Σ |  |  |  | I2 - ANSI 51 |  |  |  |  | XT5 | In x Σ |  |  |  | I3 - ANSI 50
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 250 | 300 | 400 | 600 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 250 | 300 | 400 | 600 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 250 | 300 | 400 | 600 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 120 | 160 | 240 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 105 | 126 | 168 | 252 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 110 | 132 | 176 | 264 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 375 | 450 | 600 | 900 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 375 | 450 | 600 | 900 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 115 | 138 | 184 | 276 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 500 | 600 | 800 | 1200 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 500 | 600 | 800 | 1200 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 144 | 192 | 288 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 625 | 750 | 1000 | 1500 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 625 | 750 | 1000 | 1500 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 125 | 150 | 200 | 300 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 750 | 900 | 1200 | 1800 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 750 | 900 | 1200 | 1800 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 130 | 156 | 208 | 312 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 875 | 1050 | 1400 | 2100 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 875 | 1050 | 1400 | 2100 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 135 | 162 | 216 | 324 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1125 | 1350 | 1800 | 2700 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1125 | 1350 | 1800 | 2700 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 168 | 224 | 336 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1375 | 1650 | 2200 | 3300 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1375 | 1650 | 2200 | 3300 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 145 | 174 | 232 | 348 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1625 | 1950 | 2600 | 3900 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1625 | 1950 | 2600 | 3900 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 150 | 180 | 240 | 360 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1750 | 2100 | 2800 | 4200 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1750 | 2100 | 2800 | 4200 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 155 | 186 | 248 | 372 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1875 | 2250 | 3000 | 4500 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1875 | 2250 | 3000 | 4500 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 160 | 192 | 256 | 384 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2000 | 2400 | 3200 | 4800 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2000 | 2400 | 3200 | 4800 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 165 | 198 | 264 | 396 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2125 | 2550 | 3400 | 5100 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2125 | 2550 | 3400 | 5100 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 170 | 204 | 272 | 408 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2250 | 2700 | 3600 | 5400 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2250 | 2700 | 3600 | 5400 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 175 | 210 | 280 | 420 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2500 | 3000 | 4000 | 6000 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2500 | 3000 | 4000 | 6000 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 216 | 288 | 432 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 185 | 222 | 296 | 444 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 190 | 228 | 304 | 456 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 195 | 234 | 312 | 468 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 200 | 240 | 320 | 480 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 205 | 246 | 328 | 492 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 210 | 252 | 336 | 504 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 215 | 258 | 344 | 516 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 264 | 352 | 528 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 225 | 270 | 360 | 540 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 230 | 276 | 368 | 552 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 235 | 282 | 376 | 564 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 288 | 384 | 576 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 245 | 294 | 392 | 588 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT5, LSIG
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [10 empty] | ← Short-time pickup (I2) | [9 empty] | ← Instantaneous pickup (I3) | [9 empty] | ← Ground fault (I4)
0 | current threshold | [9 empty] | 0 | current threshold | [8 empty] | 0 | current threshold | [8 empty] | 0 | current threshold
XT5 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 |  |  |  |  | XT5 | In x Σ |  |  |  | I2 - ANSI 51 |  |  |  |  | XT5 | In x Σ |  |  |  | I3 - ANSI 50 |  |  |  |  | XT5 | In x Σ |  |  | I4 - ANSI 51N
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 250 | 300 | 400 | 600 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 250 | 300 | 400 | 600 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 250 | 300 | 400 | 600 | 6 | Current Threshold | 0.2 | 0.25 | 0.55 | 250 | 300 | 400 | 600 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 100 | 120 | 160 | 240 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 105 | 126 | 168 | 252 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0 | 0.2 | ▪▪ | ▪▪ | ▪▪ | 50 | 60 | 80 | 120 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 110 | 132 | 176 | 264 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 375 | 450 | 600 | 900 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 375 | 450 | 600 | 900 | 0 | 0.25 | ▪▪ | ▪▪ | ▪▪ | 62.5 | 75 | 100 | 150 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 115 | 138 | 184 | 276 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 500 | 600 | 800 | 1200 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 500 | 600 | 800 | 1200 | 0 | 0.45 | ▪▪ | ▪▪ | ▪▪ | 112.5 | 135 | 180 | 270 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 120 | 144 | 192 | 288 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 625 | 750 | 1000 | 1500 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 625 | 750 | 1000 | 1500 | 0 | 0.55 | ▪▪ | ▪▪ | ▪▪ | 137.5 | 165 | 220 | 330 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 125 | 150 | 200 | 300 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 750 | 900 | 1200 | 1800 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 750 | 900 | 1200 | 1800 | 0 | 0.75 | ▪▪ | ▪▪ | ▪▪ | 187.5 | 225 | 300 | 450 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 130 | 156 | 208 | 312 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 875 | 1050 | 1400 | 2100 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 875 | 1050 | 1400 | 2100 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | 200 | 240 | 320 | 480 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 135 | 162 | 216 | 324 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1125 | 1350 | 1800 | 2700 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1125 | 1350 | 1800 | 2700 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 140 | 168 | 224 | 336 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1375 | 1650 | 2200 | 3300 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1375 | 1650 | 2200 | 3300 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 145 | 174 | 232 | 348 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1625 | 1950 | 2600 | 3900 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1625 | 1950 | 2600 | 3900 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 150 | 180 | 240 | 360 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1750 | 2100 | 2800 | 4200 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1750 | 2100 | 2800 | 4200 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 155 | 186 | 248 | 372 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1875 | 2250 | 3000 | 4500 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1875 | 2250 | 3000 | 4500 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 160 | 192 | 256 | 384 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2000 | 2400 | 3200 | 4800 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2000 | 2400 | 3200 | 4800 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 165 | 198 | 264 | 396 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2125 | 2550 | 3400 | 5100 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2125 | 2550 | 3400 | 5100 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 170 | 204 | 272 | 408 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2250 | 2700 | 3600 | 5400 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2250 | 2700 | 3600 | 5400 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 175 | 210 | 280 | 420 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2500 | 3000 | 4000 | 6000 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2500 | 3000 | 4000 | 6000 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 180 | 216 | 288 | 432 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 185 | 222 | 296 | 444 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 190 | 228 | 304 | 456 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 195 | 234 | 312 | 468 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 200 | 240 | 320 | 480 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 205 | 246 | 328 | 492 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 210 | 252 | 336 | 504 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 215 | 258 | 344 | 516 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 220 | 264 | 352 | 528 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 225 | 270 | 360 | 540 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 230 | 276 | 368 | 552 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 235 | 282 | 376 | 564 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 288 | 384 | 576 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 245 | 294 | 392 | 588 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 250 | 300 | 400 | 600 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT6, LS-I
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [7 empty] | ← Short-time pickup (I2) / Instantaneous pickup (I3)
0 | current threshold | [6 empty] | 0 | current threshold
XT6 | In x (0.4 + Σ) |  |  |  | I1 - ANSI 49 |  |  | XT6 | In x Σ |  |  |  | I2 / I3 - ANSI 51 / 50
Current Threshold | 0.04 | 0.08 | 0.16 | 0.32 | 600 | 800 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 600 | 800 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 320 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 264 | 352 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 288 | 384 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 312 | 416 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 336 | 448 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 384 | 512 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 408 | 544 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2700 | 3600 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 432 | 576 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3300 | 4400 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 456 | 608 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3900 | 5200 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 504 | 672 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4500 | 6000 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 528 | 704 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 552 | 736 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5100 | 6800 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 576 | 768 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT6, LSI
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [8 empty] | ← Short-time pickup (I2) | [7 empty] | ← Instantaneous pickup (I3)
0 | current threshold | [7 empty] | 0 | current threshold | [6 empty] | 0 | current threshold
XT6 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 |  |  | XT6 | In x Σ |  |  |  | I2 - ANSI 51 |  |  | XT6 | In x Σ |  |  |  | I3 - ANSI 50
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 600 | 800 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 600 | 800 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 600 | 800 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 320 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 252 | 336 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 264 | 352 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 276 | 368 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 288 | 384 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 400 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 312 | 416 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 324 | 432 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2700 | 3600 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2700 | 3600 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 336 | 448 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3300 | 4400 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3300 | 4400 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 348 | 464 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3900 | 5200 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3900 | 5200 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 372 | 496 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4500 | 6000 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4500 | 6000 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 384 | 512 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 396 | 528 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5100 | 6800 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5100 | 6800 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 408 | 544 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 420 | 560 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 432 | 576 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 444 | 592 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 456 | 608 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 468 | 624 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 492 | 656 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 504 | 672 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 516 | 688 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 528 | 704 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 540 | 720 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 552 | 736 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 564 | 752 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 576 | 768 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 588 | 784 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT6, LSIG
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [8 empty] | ← Short-time pickup (I2) | [7 empty] | ← Instantaneous pickup (I3) | [7 empty] | ← Ground fault (I4)
0 | current threshold | [7 empty] | 0 | current threshold | [6 empty] | 0 | current threshold | [6 empty] | 0 | current threshold
XT6 | In x (0.4 + Σ) |  |  |  |  | I1 - ANSI 49 |  |  | XT6 | In x Σ |  |  |  | I2 - ANSI 51 |  |  | XT6 | In x Σ |  |  |  | I3 - ANSI 50 |  |  | XT6 | In x Σ |  |  | I4 - ANSI 51N
Current Threshold | 0.02 | 0.04 | 0.08 | 0.16 | 0.32 | 600 | 800 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 600 | 800 | 6 | Current Threshold | 1 | 1.5 | 2 | 5.5 | 600 | 800 | 6 | Current Threshold | 0.2 | 0.25 | 0.55 | 600 | 800 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 320 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 252 | 336 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0 | 0.2 | ▪▪ | ▪▪ | ▪▪ | 120 | 160 | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 264 | 352 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 0 | 0.25 | ▪▪ | ▪▪ | ▪▪ | 150 | 200 | 0
0.46 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 276 | 368 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 0 | 0.45 | ▪▪ | ▪▪ | ▪▪ | 270 | 360 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 288 | 384 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 0 | 0.55 | ▪▪ | ▪▪ | ▪▪ | 330 | 440 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 300 | 400 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 0 | 0.75 | ▪▪ | ▪▪ | ▪▪ | 450 | 600 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 312 | 416 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 0
0.54 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 324 | 432 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2700 | 3600 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2700 | 3600 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 336 | 448 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3300 | 4400 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3300 | 4400 | 0
0.58 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 348 | 464 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3900 | 5200 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3900 | 5200 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 372 | 496 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4500 | 6000 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4500 | 6000 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 384 | 512 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 0
0.66 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 396 | 528 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5100 | 6800 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5100 | 6800 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 408 | 544 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 420 | 560 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 432 | 576 | 0
0.74 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 444 | 592 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 456 | 608 | 0
0.78 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 468 | 624 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 492 | 656 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 504 | 672 | 0
0.86 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 516 | 688 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 528 | 704 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 540 | 720 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 552 | 736 | 0
0.94 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 564 | 752 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 576 | 768 | 0
0.98 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 588 | 784 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT7, LS-I
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [9 empty] | ← Short-time pickup (I2) / Instantaneous pickup (I3)
0 | current threshold | [8 empty] | 0 | current threshold
XT7 |  |  |  |  | I1 - ANSI 49 |  |  |  |  | XT7 |  |  |  |  | I2 / I3 - ANSI 51 / 50
Current Threshold | In x Σ |  |  |  | 600 | 800 | 1000 | 1200 | 6 | Current Threshold | In x Σ |  |  |  | 600 | 800 | 1000 | 1200 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 240 | 320 | 400 | 480 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0
0.44 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 264 | 352 | 440 | 528 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0
0.48 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 288 | 384 | 480 | 576 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 1500 | 1800 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 312 | 416 | 520 | 624 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 2000 | 2400 | 0
0.56 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 336 | 448 | 560 | 672 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 2500 | 3000 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 600 | 720 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 3000 | 3600 | 0
0.64 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 384 | 512 | 640 | 768 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 3500 | 4200 | 0
0.68 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 408 | 544 | 680 | 816 | 0 | 4.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2700 | 3600 | 4500 | 5400 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 432 | 576 | 720 | 864 | 0 | 5.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3300 | 4400 | 5500 | 6600 | 0
0.76 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 456 | 608 | 760 | 912 | 0 | 6.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3900 | 5200 | 6500 | 7800 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 800 | 960 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 7000 | 8400 | 0
0.84 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 504 | 672 | 840 | 1008 | 0 | 7.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4500 | 6000 | 7500 | 9000 | 0
0.88 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 528 | 704 | 880 | 1056 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 8000 | 9600 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 552 | 736 | 920 | 1104 | 0 | 8.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5100 | 6800 | 8500 | 10200 | 0
0.96 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 576 | 768 | 960 | 1152 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 9000 | 10800 | 0
1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 10000 | 12000 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT7, LSI
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [11 empty] | ← Short-time pickup (I2) | [9 empty] | ← Instantaneous pickup (I3)
0 | current threshold | [10 empty] | 0 | current threshold | [8 empty] | 0 | current threshold
XT7 | [6 empty] | I1 - ANSI 49 |  |  |  |  | XT7 |  |  |  |  | I2 - ANSI 51 |  |  |  |  | XT7 |  |  |  |  | I3 - ANSI 50
Current Threshold | In x Σ | [5 empty] | 600 | 800 | 1000 | 1200 | 6 | Current Threshold | In x Σ |  |  |  | 600 | 800 | 1000 | 1200 | 6 | Current Threshold | In x Σ |  |  |  | 600 | 800 | 1000 | 1200 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 240 | 320 | 400 | 480 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 252 | 336 | 420 | 504 | 0 | 0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 600 | 720 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 1500 | 1800 | 0
0.45 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 270 | 360 | 450 | 540 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 800 | 960 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 2000 | 2400 | 0
0.47 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 282 | 376 | 470 | 564 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 3000 | 3600 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 300 | 400 | 500 | 600 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 1500 | 1800 | 0 | 4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2400 | 3200 | 4000 | 4800 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 312 | 416 | 520 | 624 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 2000 | 2400 | 0 | 5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3000 | 4000 | 5000 | 6000 | 0
0.55 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 330 | 440 | 550 | 660 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 2500 | 3000 | 0 | 6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3600 | 4800 | 6000 | 7200 | 0
0.57 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 342 | 456 | 570 | 684 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 3000 | 3600 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 7000 | 8400 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 360 | 480 | 600 | 720 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 3500 | 4200 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 8000 | 9600 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 372 | 496 | 620 | 744 | 0 | 4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2400 | 3200 | 4000 | 4800 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 9000 | 10800 | 0
0.65 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 390 | 520 | 650 | 780 | 0 | 5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3000 | 4000 | 5000 | 6000 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 10000 | 12000 | 0
0.67 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 402 | 536 | 670 | 804 | 0 | 6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3600 | 4800 | 6000 | 7200 | 0 | 11 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6600 | 8800 | 11000 | 13200 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 420 | 560 | 700 | 840 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 7000 | 8400 | 0 | 12 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7200 | 9600 | 12000 | 14400 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 432 | 576 | 720 | 864 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 8000 | 9600 | 0 | 13 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7800 | 10400 | 13000 | 15600 | 0
0.75 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 450 | 600 | 750 | 900 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 9000 | 10800 | 0 | 14 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8400 | 11200 | 14000 | 16800 | 0
0.77 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 462 | 616 | 770 | 924 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 10000 | 12000 | 0 | 15 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9000 | 12000 | 15000 | 18000 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 480 | 640 | 800 | 960 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 492 | 656 | 820 | 984 | 0
0.85 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 510 | 680 | 850 | 1020 | 0
0.87 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 522 | 696 | 870 | 1044 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 540 | 720 | 900 | 1080 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 552 | 736 | 920 | 1104 | 0
0.95 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 570 | 760 | 950 | 1140 | 0
0.97 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 582 | 776 | 970 | 1164 | 0
1 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.

## XT7, LSIG
← Nominal (maximum amps) rating (In)
| ← Long-time pickup (I1) | [11 empty] | ← Short-time pickup (I2) | [9 empty] | ← Instantaneous pickup (I3) | [9 empty] | ← Ground fault (I4)
0 | current threshold | [10 empty] | 0 | current threshold | [8 empty] | 0 | current threshold | [8 empty] | 0 | current threshold
XT7 | [6 empty] | I1 - ANSI 49 |  |  |  |  | XT7 |  |  |  |  | I2 - ANSI 51 |  |  |  |  | XT7 |  |  |  |  | I3 - ANSI 50 |  |  |  |  | XT7 |  |  |  | I4 - ANSI 51N
Current Threshold | In x Σ | [5 empty] | 600 | 800 | 1000 | 1200 | 6 | Current Threshold | In x Σ |  |  |  | 600 | 800 | 1000 | 1200 | 6 | Current Threshold | In x Σ |  |  |  | 600 | 800 | 1000 | 1200 | 6 | Current Threshold | In x Σ |  |  | 600 | 800 | 1000 | 1200 | 6
0.4 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 240 | 320 | 400 | 480 | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0 | OFF | ▪▪ | ▪▪ | ▪▪ | OFF | OFF | OFF | OFF | 0
0.42 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 252 | 336 | 420 | 504 | 0 | 0.6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 600 | 720 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 1500 | 1800 | 0 | 0.1 | ▪▪ | ▪▪ | ▪▪ | 60 | 80 | 100 | 120 | 0
0.45 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 270 | 360 | 450 | 540 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 800 | 960 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 2000 | 2400 | 0 | 0.2 | ▪▪ | ▪▪ | ▪▪ | 120 | 160 | 200 | 240 | 0
0.47 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 282 | 376 | 470 | 564 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 3000 | 3600 | 0 | 0.3 | ▪▪ | ▪▪ | ▪▪ | 180 | 240 | 300 | 360 | 0
0.5 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 300 | 400 | 500 | 600 | 0 | 1.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 900 | 1200 | 1500 | 1800 | 0 | 4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2400 | 3200 | 4000 | 4800 | 0 | 0.4 | ▪▪ | ▪▪ | ▪▪ | 240 | 320 | 400 | 480 | 0
0.52 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 312 | 416 | 520 | 624 | 0 | 2 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1200 | 1600 | 2000 | 2400 | 0 | 5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3000 | 4000 | 5000 | 6000 | 0 | 0.6 | ▪▪ | ▪▪ | ▪▪ | 360 | 480 | 600 | 720 | 0
0.55 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 330 | 440 | 550 | 660 | 0 | 2.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1500 | 2000 | 2500 | 3000 | 0 | 6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3600 | 4800 | 6000 | 7200 | 0 | 0.8 | ▪▪ | ▪▪ | ▪▪ | 480 | 640 | 800 | 960 | 0
0.57 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 342 | 456 | 570 | 684 | 0 | 3 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 1800 | 2400 | 3000 | 3600 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 7000 | 8400 | 0 | 1 | ▪▪ | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0
0.6 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 360 | 480 | 600 | 720 | 0 | 3.5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2100 | 2800 | 3500 | 4200 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 8000 | 9600 | 0
0.62 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 372 | 496 | 620 | 744 | 0 | 4 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 2400 | 3200 | 4000 | 4800 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 9000 | 10800 | 0
0.65 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 390 | 520 | 650 | 780 | 0 | 5 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3000 | 4000 | 5000 | 6000 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 10000 | 12000 | 0
0.67 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 402 | 536 | 670 | 804 | 0 | 6 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 3600 | 4800 | 6000 | 7200 | 0 | 11 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6600 | 8800 | 11000 | 13200 | 0
0.7 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 420 | 560 | 700 | 840 | 0 | 7 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4200 | 5600 | 7000 | 8400 | 0 | 12 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7200 | 9600 | 12000 | 14400 | 0
0.72 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 432 | 576 | 720 | 864 | 0 | 8 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 4800 | 6400 | 8000 | 9600 | 0 | 13 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 7800 | 10400 | 13000 | 15600 | 0
0.75 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 450 | 600 | 750 | 900 | 0 | 9 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 5400 | 7200 | 9000 | 10800 | 0 | 14 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 8400 | 11200 | 14000 | 16800 | 0
0.77 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 462 | 616 | 770 | 924 | 0 | 10 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 6000 | 8000 | 10000 | 12000 | 0 | 15 | ▪▪ | ▪▪ | ▪▪ | ▪▪ | 9000 | 12000 | 15000 | 18000 | 0
0.8 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 480 | 640 | 800 | 960 | 0
0.82 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 492 | 656 | 820 | 984 | 0
0.85 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 510 | 680 | 850 | 1020 | 0
0.87 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 522 | 696 | 870 | 1044 | 0
0.9 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 540 | 720 | 900 | 1080 | 0
0.92 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 552 | 736 | 920 | 1104 | 0
0.95 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 570 | 760 | 950 | 1140 | 0
0.97 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 582 | 776 | 970 | 1164 | 0
1 | ▪▪ | ▪▪ | ▪▪ | + | ▪▪ | ▪▪ | 600 | 800 | 1000 | 1200 | 0
©2021 ABB Inc. All rights reserved. Specifications subject to change without notice.