# GENERAL

## SECTION INCLUDES.

### Medium Voltage Paralleling Switchgear

#### Equipment designed for multiple parallel generators including paralleling controls and related distribution equipment.

## RELATED SECTIONS

### 26 13 13 Medium Voltage Metal-Clad Switchgear

### 26 36 23 11 Medium Voltage Automatic Transfer Switchgear

## REFERENCES: The medium voltage switchgear in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### ANSI/IEEE C37.04 Standard for Ratings and Requirements for AC High-Voltage Circuit Breakers with Rated Maximum Voltage Above 1000V

### ANSI/IEEE C37.09 Standard Test Procedures for AC High-Voltage Circuit Breakers with Rated Maximum Voltage Above 1000V

### ANSI/IEEE C37.010 Application Guide for AC High-Voltage Circuit Breakers > 1000 Vac Rated on a Symmetrical Current Basis

### ANSI/IEEE C37.011 Guide for the Application of Transient Recovery Voltage for AC High-Voltage Circuit Breakers

### ANSI/IEEE C37.012 IEEE Application Guide for Capacitance Current Switching for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis

### ANSI/IEEE C37.11 IEEE Standard Requirements for Electrical Control for AC High-Voltage (>1000 V) Circuit Breakers

### IEEE/IEC 62271-37-013 IEEE/IEC International Standard for High-Voltage Switchgear and Control-gear – Part 37-013: Alternating-Current Generator Circuit-Breakers

### ANSI/IEEE C37.20.2 IEEE Standard for Metal-Clad Switchgear

### ANSI/NEMA C37.55 Medium-Voltage Metal-Clad Switchgear Assemblies - Conformance Test Procedures

### ANSI/IEEE C37.2 IEEE Standard Electrical Power System Device Function Numbers, Acronyms, and Contact Designations

### ANSI/IEEE C37.90 IEEE Standard for Relays and Relay Systems Associated with Electric Power Apparatus

### ANSI/IEEE C57.13 IEEE Standard Requirements for Instrument Transformers

### ANSI/NEMA C39.1 Requirements for Electrical Analog Indicating Instruments

### ANSI/IEEE C37.06 American National Standard  for AC High-Voltage Circuit Breakers - Rated on a Symmetrical Current Basis - Preferred Ratings and Related Required Capabilities

## SUBMITTALS

### Manufacturer Requirements:  Manufacturer shall provide [electronic] copies of the following documents to owner for review and evaluation in accordance with general requirements of Division 1 and Division 26:

#### An outline and general arrangement drawing including dimensions, weights and shipping sections;

#### Shop Drawings on specified product including floor plan drawing, leveling channels and cable conduit entrance locations;

#### A specification clarification and deviation statement;

#### A catalog cut sheet and other descriptive material of all major components;

#### A list of like systems previously delivered (upon request only);

#### A complete Bill of Materials separated into each sub-assembly and showing manufacturer’s part number, quantity, and description of each part.  If another manufacturer makes the part, the description shall indicate the other manufacturer and their part number;

#### Short circuit, coordination and arc flash studies can optionally be provided.

### Electrical Contractor Requirements

#### The electrical contractor shall be responsible for supplying a complete system short circuit analysis and coordination study for all protective devices.

#### The contractor must supply and coordinate the duties of an independent testing firm to perform on-site physical inspection and testing of all protective devices and ensure the devices have been calibrated and set to the settings determined in the coordination study.

#### This work must be performed prior to energization of the equipment and field start-up will not be allowed until verification is provided.

#### Each protective device shall bear the testing firm certification label to verify appropriate testing has been performed.

## INSTALLATION, OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide [electronic] copies of installation, operation, and maintenance procedures to owner with delivered equipment in accordance with general requirements of Division 1 and Division 16

### The operating and maintenance manual shall include the following:

#### Shop Drawings.

#### A complete description of system operating sequences as interpreted by the manufacturer.

#### Parts identification for replaceable parts and assemblies.

#### Complete point-to-point wiring diagrams showing connections between paralleling controls and Engine Generators and other external equipment requiring control-wiring connections.

#### Complete point-to-point wiring diagrams showing connection of component devices supplied inside paralleling equipment.

#### Interconnection diagrams showing connections between unit assemblies.

#### Schematic diagrams of control and alarm circuits, outline drawings and detailed three-line diagrams of potential and current secondary circuits.

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of paralleling switchgear equipment for [15] years.

### [Switchgear shall be qualified for use in seismic areas as follows:

#### High seismic loading as defined in IEEE Std 693-2005, with 1.8 amplification factor.

#### IBC-2018/CBC-2019, [SDS = 1.88, Ip = 1.0 (standard)], [SDS = 2.0g, Ip = 1.0 (Advance Switchgear)], [SDS = 2.5g, IP=1.5 (SafeGear and SafeGear HD) Switchgear], for all locations in the facility in accordance with ICC-ES-AC156.]

## DELIVERY, STORAGE, AND HANDLING

### Contractor shall store, protect and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Sections shall be mounted on shipping skids and wrapped for protection.

### Contractor shall inspect and report concealed damage to carrier within 48 hours.

### Contractor shall store in a clean, dry space. Cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic. Heat enclosures to prevent condensation.

### Contractor shall handle in accordance with manufacturer's recommendations to avoid damaging equipment, installed devices, and finish. [Lift only by installed lifting eyes.]

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow (standards) service conditions before, during and after equipment installation

### Environmental conditions affecting the switchgear must be within the usual service conditions as outlined in Clause 4 of ANSI/IEEE C37.20.2-2015.

## WARRANTY

### Manufacturer shall warranty equipment to be free from defects in materials and workmanship for 1 year from date of energization or 18 months from date of shipment, whichever occurs first. The equipment must be received, stored, and installed in accordance with the manufacturer’s installation publications and/or maintenance manuals to avoid nullifying this warranty.

### [Manufacturer shall offer an extended warranty of [1-5] years.]

## FIELD MEASUREMENTS

### Contractor shall make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code.

# PRODUCTS

## MANUFACTURER

### ABB Inc. (ABB Zenith) products have been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.

## EQUIPMENT

### General Description:

#### Furnish ABB Inc. Medium Voltage Paralleling Switchgear Type Zenith TruCommand PSG (or approved equal).

#### Furnish complete engine-generator control system with devices for the operation, control and paralleling of [   ] engine-generator sets for automatic standby operation.  (Controls for all modes of operation must be provided at this time).

#### Each engine-generator is rated [    ] kW, [    ] V, and 0.8 PF, three-phase, [ 3 / 4 ]-wire, and 60 Hz.

#### Control power supply to the controls will be 24VDC [125 VDC] from the engine batteries [station batteries].

#### [Furnish a remote annunciator to interface to the PSG to duplicate the annunciation [on the generator controls and master controls]].

#### Equipment shall be provided using [UL listed] metal-clad switchgear designed in compliance with IEEE C37.20.2.

#### Cable termination compartments shall be rear accessible.

#### Draw-out vacuum circuit breakers shall be used for switching devices and arranged for single or double throw operation as specified and interlocked for safe and reliable operation.

#### All coils, relays timers, and accessories shall be front accessible, and isolated by grounded metal barriers from all high voltage primary devices.

#### Interconnecting bus shall be [silver-plated] [tin-plated] copper, insulated by flame retardant, non-hydroscopic, fluidized bed epoxy.

#### Main bus support and primary bushings shall be [polyester] [epoxy].  Standoff insulators shall be [epoxy] [polyester].

#### Provide single or multi-ratio current transformers or sensors as indicated on drawings.

#### Potential transformers or sensors shall be provided for each source and on the load bus.

##### Voltage transformers shall be drawout type with current-limiting fuses and with BIL rating equal to the switchgear.  Transformer ratios as per drawings.

##### Secondary control wiring shall be minimum No. 14 extra flexible, stranded, tinned-copper control wire, Type SIS cross-linked polyethylene, rated 600v.

##### Crimp-type uninsulated spade terminals shall be furnished on all wire ends, except where no-insulated ring terminals are used to connect to fuse blocks, instrument studs or terminal block points with two or more wire connections.

##### Secondary control wires shall be armored where they pass through primary compartments.

#### Provide the following switchgear accessories:

##### Manual racking crank

##### Breaker removal lift truck

##### [IR windows on cable termination compartment covers] [continuous monitoring]

##### [Remote racking, ABB Smart Rack]

##### [Fungus proofing]

NOTE TO SPECIFIER: RODENT PROOFING IS AVAILABLE ONLY ON ARC RESISTANT ENCLOSURES

##### [Rodent proofing]

### Paralleling Switchgear Ratings

#### Voltage: [4160V] [7200V] [12000V] [12470V] [13200V] [13800V] [As indicated on drawings].

#### 3Ø, 3W connected system

#### Ampacity: [1,200A] [2,000A] [3,000A] [As specified on drawings.]

#### Interruption rating: [25] [31.5] [40] [50] [63] kAIC [As specified on drawings.]

#### BIL rating shall be a minimum of 60 kV for 5 kV rated equipment and a minimum of 95 kV for 15 kV rated equipment.

### Enclosure

#### Enclosure shall be suitable for [indoor location] [or] [outdoor location] [as indicated on drawings].

#### Outdoor rated enclosures shall be a non-walk-in design and provided with heaters controlled by thermostats.  Heater power supply shall be supplied from [external source] [as indicated on drawings]

NOTE TO SPECIFIER: ARC RESISTANT ENCLOSURE IS AVAILABLE ONLY ON INDOOR RATED ENCLOSURES.

#### [Provide equipment in an arc resistant enclosure tested to IEEE C30.20.7, type [2] [2B] [2BC] [as indicated on drawings]].

## SYSTEM COMPONENT REQUIREMENTS

### Refer to Contract Drawings for actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; interrupting and withstand ratings of devices, buses, and components; and other required details.

### Power Switching Devices

#### All power switching shall be performed using draw-out mounted, vacuum interrupter circuit breakers.  Vacuum contactors are not allowed.

NOTE TO SPECIFIER: SELECTION OF CIRCUIT BREAKERS SHOULD BE SUPPORTED BY DETAILED SYSTEM ANALYSIS TO TAKE INTO CONSIDERATION THE X/R AND %DC OF COMPONENTS

#### Circuit breakers complying with IEEE C37.04 shall be applied for sources where the short circuit current impedances on the line side of the ATS have an X/R ratio of 17 or less.  Applications above this threshold should be supported by analysis.  For sources where the short circuit current impedances on the line side of the ATS have an X/R ratio that exceeds 50, the circuit breaker shall comply with IEEE/IEC 62271-37-013.

#### ADVAC G (Generator) when X/R over 50.

#### Draw-out mechanism shall be operable with the breaker doors closed.  Shutters shall cover the primary stabs when the breaker is withdrawn from the Connect position.

NOTE TO SPECIFIER: RELAYS CAN BE OMITTED IF PROTECTIVE FUNCTIONS ARE PROVIDED EXTERNALLY

### [Protective Relays:  Provide protective relays as indicated by drawings:

#### Provide ABB Relion Relays.   Relay shall be [ABB REG615] [ABB REX640] [Utility grade, GE Multilin SR489 series] [industrial grade, Woodward MFR series] [or equal].

#### Provide protective relays for each utility source and for each generator source.

#### The engine-generator protective relay shall be powered by the breaker trip power source.

#### The engine-generator protective relay(s) shall provide the following functionality as a minimum:

##### 25 - Synch Check and synch-check with dead-bus

##### 27/59 - Under voltage and over voltage

##### 32R - Reverse power protection

##### 81 O/U - Over and under frequency

##### 40 – Loss of field

##### 51N - Neutral ground fault.

#### Relays shall be a withdrawable-unit design.

#### [Relays shall have the capability of communicating using IEC 61850 GOOSE messaging.]

#### One rear RS485 port that can be programmed for Modbus RTU communications to provide basic metering data.

NOTE TO SPECIFIER: INSERT OTHER SPECIFICATIONS FOR REQUIRED RELAYS HERE.

### Master and Generator Control Logic

#### Master control logic shall be imbedded in a PLC [in a redundant hot synchronized fashion].  The control logic shall be written such that, in the event that the Master PLC functions were to fail, the system will still be capable of starting the engine-generators upon any start signal from the remote ATS’s.

#### Each generator shall also contain its own PLC for generator control and alarm/shutdown functions separate from the Master PLC.

#### All breakers that are controlled by PLC’s are to have breaker failure logic.  This logic will monitor a failure to close or a failure to open upon PLC command.

#### Hard-wired backup automatic engine starting and paralleling shall be included for instances when the Master PLC system is not available and an emergency start is present.

#### The system must be capable of communicating to specific devices that are monitoring devices controlled by this system, via [RS-485 and acting as a Modbus RTU master], [ethernet and acting as Modbus TCP client].  These devices include: power quality meters, ATS’s, and protective relays.

## NOTE TO SPECIFIER:  THE FOLLOWING SECTIONS DESCRIBE THE CONTROL SECTIONS THAT CAN BE CONFIGURED WITH OR WITHOUT OPTIONS.

### Engine-Generator Control Section:  Each engine-generator control system shall be equipped at minimum with the following devices: (Digital representation of these devices is not acceptable.)

#### Breaker control switch, pistol grip (52s)

#### Engine-generator controller, Woodward compatible.

##### Governor (speed control and load sharing), by engine generator manufacturer.  This device is mounted at the generator only.

##### Loading control interface to governor system (part of multi-function generator controller)

##### Automatic synchronizer

#### RX3i, VersaMax PLC, ABB or equal, included with back-up power supply for use during DC engine cranking

#### Breaker status lights:

##### Open (Red)

##### Closed (Red)

##### [Locked-out (White)]

##### [Racked-out (Amber)]

#### Synchro-switch, removable keyed T-handle

#### Analog kilowatt meter, scaled from zero to the maximum of the kW based on the CT and PT ratios, 4.5” switchboard meter with 1% accuracy

#### Analog amp meter, scaled from zero to the maximum primary current based on the CT ratio, 4.5” switchboard meter with 1% accuracy and separate switch

#### Engine Control Switch, [3], [4], [5] -position

##### Off

##### Automatic

##### Manual

#### Speed manual control device (65s), if engine is capable of remote speed biasing

#### Voltage manual control device (90s), if engine is capable of remote voltage biasing

#### Reset pushbutton

#### Light Test pushbutton

#### Generator annunciator 5x5 LED type, with the following indications: (digital representations of these lights alone are not acceptable) All alarm and shutdown lights shall flash until acknowledged or reset:

##### Low Oil Pressure, Alarm (amber), Shutdown (red).

##### High Water Temperature, Alarm (amber), Shutdown (red).

##### Engine Over crank, Shutdown (red).

##### Engine Over speed, Shutdown (red).

##### Generator Breaker Locked Out, Shutdown (red).

##### Fail to Synchronize, Shutdown (red).

##### Generator Summary Alarm, Alarm (amber).

##### Battery Charger Failure, Alarm (amber).

##### Generator Controller Not in AUTO, Status (red).

##### Engine Running, Status (green).

##### Generator Summary Shutdown, Shutdown (red).

##### Auxiliary Power Failure, Alarm (amber).

##### Low Water Temperature, Alarm (amber).

##### Emergency Stop Activated, Shutdown (red).

##### Start Signal Received, Status (green).

##### Engine Cooling Down, Status (green).

##### Low Coolant Level, Alarm (amber).

##### Generator Breaker Failed to Close, Alarm (amber).

##### Generator Breaker Failed to Open, Alarm (amber).

##### Remote Generator Breaker is Open, Shutdown (red).

##### [Day-Tank Low Fuel, Alarm (amber), Shutdown (red).]

##### [Ground Fault, Alarm (amber).] (optional)

##### [Air Damper Activated, Shutdown (red).] (optional)

## NOTE TO SPECIFIER: THE FOLLOWING BRACKETED DEVICES SHALL BE SELECTED IN ADDITION TO THE BASE SWITCHES AND METERING AS DESIRED

#### Analog volt meter, scaled from zero to the maximum primary voltage based on the PT ratio, 4.5” switchboard meter with 1% accuracy and separate switch (standard)

#### Analog frequency meter, scaled to +/- 5 Hz from nominal, 4.5” switchboard meter with 1% accuracy (standard)

#### [Analog kilovar meter, scaled the same as the Kilowatt meter, 4.5” switchboard meter with 1% accuracy] (optional)

#### [Analog power factor meter, scaled from 0.5 (lag) to 1 .0 to 0.5 (lead), 4.5” switchboard meter with 1% accuracy] (optional)

#### [Watt-hour demand meter, switchboard type] (optional)

#### [Emergency Stop Pushbutton] (optional)

#### 86 lock-out relay, for use with the protective relay (standard)

### Master Control Section: The master control section shall be equipped at a minimum with the following devices and any additional for providing a functional system:

#### HMI Interface Panel as specified in the ‘HMI Interface Panel’ section.

#### Master control PLC, type Rx3i series, ABB or equal, included with back-up power supply for use during DC engine cranking. [Provide Redundant Master controllers fully equipped with power supplies, CPU’s, and I/O points.]

#### A system shall be provided, with visual fault indication, to monitor the PLC network communications system and PLC status. Means shall be provided to identify which PLC on the network has faulted or has lost communications in the event of a fault.

#### Synch-check relay

#### Light Test pushbutton

#### Reset pushbutton

#### Horn silence pushbutton

#### Master annunciator 5x5 LED type, with the following indications: (digital representations of these lights alone are not acceptable) All alarm and shutdown lights shall flash until acknowledged or reset:

##### System Gen. Bus Under Frequency, Alarm (red).

##### System Gen. Bus Over Frequency, Alarm (red).

##### System Not in Auto, Status (red).

##### Load add/shed, one per priority, Load Add (green), Load Shed (red).

##### Auxiliary Power Failure, Alarm (red).

##### Load Demand Mode is Active, Status (green).

##### Building Exerciser is Active, Status (green).

##### System Test Mode is Active, Status (amber).

##### Emergency Start Signal Received, Status (red).

##### Emergency Start Signal Fuse Blown, Alarm (red).

##### Emergency Power Available, Status (green).

##### System Summary Alarm – see detail in ACS, Alarm (red)

##### System Gen. Bus Overload, Alarm (red).

##### Standby mode is Active, Status (green).

##### Master Interface Panel (ACS) Failure, Alarm (red).

##### [Remote / Interrupt Signal Received, Status (green).]

##### [Main Tank Low Fuel, Alarm (amber).]

##### [Main Tank High Fuel Level, Alarm (amber).]

##### [Main Tank Fuel Leak, Alarm (red).]

#### System AUTO/MAN selector switch

#### Mounted on the door:

##### Synch panel:

###### Two (2) synchro-lights

###### Two (2) analog volt meters (running/incoming), scaled from zero to the maximum primary voltage based on the PT ratio, 4.5” switchboard meter with 1% accuracy

###### Two (2) analog frequency meters (running/incoming), scaled to +/- 5 Hz from nominal, 4.5” switchboard meter with 1% accuracy

###### Analog SynchroScope, 4.5” switchboard meter with 1% accuracy

##### [Bus summing analog kilowatt meter, scaled from zero to the maximum of the kW based on the CT and PT ratios, 4.5” switchboard meter with 1% accuracy] (provided as part of PQM meter)

##### [Bus summing analog kilovar meter, scaled from zero to the maximum of the kilovar based on the CT and PT ratios, 4.5” switchboard meter with 1% accuracy] (provided as part of PQM meter)

##### [Bus summing analog amp meter, scaled from zero to the maximum primary current based on the CT ratio, 4.5” switchboard meter with 1% accuracy and separate switch] (provided as part of PQM meter)

##### [Bus analog power factor meter, scaled from 0.5 (lag) to 1 .0 to 0.5 (lead), 4.5” switchboard meter with 1% accuracy] (provided as part of PQM meter)

##### [Power Quality Meter, GE PQM, ABB or equivalent]

#### [Breaker control switch, pistol grip (52s)] (For loadbank breaker if included)

#### [Breaker status lights:]

##### Open (Red)

##### Closed (Red)

##### [Locked-out (White)]

##### [Racked-out (Amber)]

### ATS Equipment: see Related Section “Medium Voltage Automatic Transfer Switchgear (1.02.B)

### HMI Interface Panel [ACS/OIP]

#### The HMI Interface panel is to be [housed in a separate enclosure], [housed within the PSG equipment].

#### [Provide a [17”], [19”], [24”] SCADA color touch screen that will be used as the Advanced control system panel (ACS).]

##### The ACS shall be connected to the Master PLCs via an Ethernet network.

##### The ACS shall be equipped for 24 VDC control power.

##### The ACS shall be equipped with a minimum 15 GB hard drive.

##### The ACS shall not be used for automatic operation of the system.  The purpose of the ACS is to act as a user interface to the Paralleling Equipment control system as defined in this section.

#### The ACS shall be supplied with SCADA software that is used to manually control and display the status of the Paralleling Equipment system.

##### [The SCADA software shall be capable of hosting a Java website where all screens can be viewed and controlled remotely on the Local Area Network via a standard web browser.

###### The need for the installation of any software other than an operating system and an Internet browser on the remote computer is not acceptable.

###### Accessing the ACS from additional computers will not require any additional licenses or fees.

###### Accessing the ACS from remote computers (on the LAN) should be as straight forward as accessing a web page on the Internet.]

#### The SCADA software shall be equipped with the following features:

##### No control or metering screen should be more than 3 touches away from any other screen.

##### A screen that is dedicated solely to the display of the one-line representation of the Paralleling Equipment system and all other equipment that is controlled or monitored by this control system.  The one-line device symbols are to be equipped with navigation buttons to simplify screen navigation.

##### Capable of monitoring each of the engine-generators and their respective breakers.  Equipped with:

###### Complete power metering to include: watts, vars, power factor, frequency, amperes, and voltage (3 and 4 wire measurements, as applicable.)

###### Engine run hours.

###### Engine status.

##### Number of generator breaker operations.

##### Generator optimization.

###### Capable of manually assigning engine priorities.

###### Capable of setting the system to automatically determine the priority of the engines based on engine runtime and the number of engine starts.

##### Load Optimization and Control

###### Capable of manually prioritizing each load before or anytime after installation by just changing the value on the ACS.  No field wiring or PLC coding required.

###### Load add/shed shall be controlled by the ACS/PLC system.  The loads shall be divided into blocks by the number of generators paralleling as well as sub-priorities for each load.  The load adding and shedding of these priorities shall be decided based on available generator capacity compared to the size of load.  The load priorities shall be settable in the ACS touch panel and include active display of the actual load.  Block shedding shall be included for generator failures with automatic re-adding based on capacity.  Under-frequency conditions shall require manual intervention for identifying and re-setting load add operations.  Hard-wired control switches for controlling remote transfer switches when the PLC/ACS system is not available shall be provided.

##### Trending and event logging

###### The system shall designate 1 Gigabyte of hard disk space for storing the database file for the system trending and event logging.  This shall be user definable up to 10 Gigabytes.

###### The system shall be capable of trending and logging data at a resolution of one (1) second.

###### The system shall be setup trend and log the following values until the designated space on the hard drive is full at which time the information will be overwritten in a FIFO procedure:

###### Trend the analog values of watts, vars, frequency, and voltage for each generator and other monitored sources.  All pieces of the emergency power equipment that is to be monitored shall be equipped with a power metering device that will monitor all three phases and provide this information over [Modbus RTU], [Modbus TCP].  In addition to the generator breaker, the following is a list of all pieces of equipment that are to be monitored: [to be filled in by the Consulting Engineer].

###### Log the position of the generator breaker and all generator indicator lights.

###### Log the position of the system indicator lights and the status of all controlled breakers and of all monitored ATSs.

###### Alarm logging:

###### The system shall record all alarm events with time stamp.

###### The alarm events can be acknowledged one at a time or all at once.

###### The system shall be capable of storing the latest 20,000 alarms.  (Over 1-year of storage.)

##### Notification: The ACS shall be capable of delivering e-mail messages when any shutdown occurs.  The message must contain the time and date of the alarm.

##### The ACS shall be capable of monitoring the number of operations and the suggested maintenance period for each of the following pieces of equipment:

###### Each generator (run hours)

###### Each controlled breaker (# of operations)

###### Each ATS (# of transfers)

##### Based on either the number of operations or the time lapse since the last maintenance for each type of device, the ACS shall calculate the next expected maintenance date.

##### The ACS shall be capable of notifying persons specified via e-mail message.

##### The software shall include a communications screen that identifies all Ethernet devices and Modbus devices supplied with the control system and their communication status (Green / Red).

### Engine-Generator

#### The engine-generator manufacturer shall:

##### Provide dry contacts to meet NFPA 110 requirements.

##### Provide a Woodward compatible isochronous governing system.

##### If the generator is equipped with its own circuit breaker, a normally open breaker position dry contact shall be provided.

### Governor/Speed Control

#### The control system shall be designed for operation with engine-generator units having speed-matching, load-sharing electronic type isochronous governors.

#### The electronic control, with isochronous load-sharing feature and speed adjustment devices, shall be supplied by the engine-generator supplier and mounted and wired in the equipment.  The governor shall be Woodward Model 2301A or equal.

#### A speed-control adjustment device, compatible with the governor, shall be provided on each generator-control cubicle for manual speed adjustment.

### Voltage Regulator

#### Voltage regulators and voltage sensing devices shall be supplied by the generator set supplier and shall be mounted on the generator.

#### A voltage control adjustment device compatible with the voltage regulator shall be provided on the generator-control equipment for manual voltage adjustment.

#### 120VAC shall be supplied from each generator sensing PT to the corresponding voltage regulator.

#### Voltage regulator shall be equipped with VAR/PFC capability.

#### The engine generator supplier shall be responsible for ensuring the generators being supplied each have the same pitch [2/3] [4/5].

### Automatic Synchronizer

#### Each power source that is to be synchronized with the generator bus shall be equipped with its own automatic synchronizer.

#### The synchronizer shall bias the speed and voltage of the incoming generator to match that of the referenced source bus.  The synchronizer shall measure incoming generator voltage, frequency and phase angle, and compare those measurements to the referenced source bus.  The synchronizer shall give a CLOSE signal to the respective breaker when the generator is within synchronizing limits for a preset length of time.

#### The synchronizer shall be provided with a separate manual speed control to adjust each of the synchronizing limits.  The range of adjustments shall be:

##### Frequency differential:  Approximately ±0.005Hz to ±2.0Hz.

##### Phase angle differential:  Approximately ±0.1° to ±15.0°.

##### Voltage differential:  Approximately ±1% to ± 20%

##### The synchronizer and governor manufacturer shall be the same.

#### A synch mode selector switch with RUN-OFF-CHECK-PERMISSIVE positions shall be provided to aid in testing and facilitate troubleshooting. In RUN mode, the synchronizer shall be enabled for active synchronization and synch check function. In CHECK, mode, the synchronizer shall perform the sync-check function only (without active synchronization). In PERMISSIVE mode, the synchronizer shall annunciate when generator and bus are in synchronism, but shall not allow breaker closure.  The automatic synchronizer shall be capable of being switched between each of these modes via discrete inputs.

## SEQUENCE OF OPERATION

### The equipment is designed for use as emergency standby.  The equipment shall be factory tested to provide the following modes of operation, even if all the modes will not be initially commissioned:

#### Emergency Standby Mode of Operation

##### Upon notification of a loss of normal power to any part of the system load as indicated from the ATS device, automatically:

###### Start all available engine-generators.

###### Parallel them together on the main generator bus.

###### Once enough generators are online to carry the priority #1 load, or once a user-defined time has passed, transfer the system load in order of load priority to the engine-generators that are online.    Each load shall be controlled by its own ‘load add’ and ‘load shed’ control relays.

###### As additional engine-generators come online, transfer additional loads to the engine-generators.

###### After an adjustable period of time the system shall allow generators to optimize down to only the required number to be online to avoid wet stacking.  The stopping and starting sequences shall be settable thru the main interface panel device and allow settings based on manual priorities or by engine run time.

###### If the engine-generators become overloaded, the system shall shed load until the engine-generators are no longer overloaded.  Shed loads in order of lowest priority.

###### The load transfer scheme shall be controlled thru the remote [ATS devices] [downstream electrically operated circuit breakers from the ATS device].

##### The ATS devices shall ensure that if generator power is ever lost at the emergency side of the transfer operator that the device will automatically bypass any delays or sequences and transfer the load back to the normal source if it is available.

##### Once the utility sources have returned and the load has been transferred back to the normal source by the remote ATS devices, the emergency start signal shall be removed and the generator paralleling system will go offline, the generators will cool-down and then shut down.

##### [Provide automatic load-bank testing operations to start and parallel the generators and operate a load-bank breaker].

#### System Test and Peak Shave

##### The system will be notified to start by one of the following non-emergency-start signals:  Building Exerciser, remote dry contact, or manually initiated.

##### Each of the non-emergency start signals can be user selected to isolate the system load from the utility source via the downstream ATS devices.

##### Once the engine-generators are online, the system will enable the appropriate ATS devices to transfer onto the generator system.

##### After an adjustable time period, the system shall allow generators to optimize down to only the required number to be online to avoid wet stacking.  The stopping and starting sequences shall be settable thru the HMI interface panel device and allow settings based on manual priorities or by engine run time.

##### After the Peak Shave signal is removed, the ATS devices will transfer the load back to the normal source, the emergency start signal shall be removed, the generator paralleling system will go offline, the generators will cool-down and then shut down.

##### If there is a utility outage during the Peak Shave mode of operation:

###### The system will go into emergency standby mode.

If necessary, the system shall load shed loads starting with the lowest priority load until the building load is below the generator capacity.

At the same time, any generators not currently running will be signaled to start and parallel to the generator bus.

The load add/shed operations and optimization sequences will occur as previously described.

###### When the utility power has returned for a specified period of time the system will transfer back to the utility source via the ATS devices.

##### Once the utility sources have returned and the load has been transferred back to the normal source by the remote ATS devices, the emergency start signal shall be removed and the generator paralleling system will go offline, the generators will cool-down and then shut down.

#### [Provide automatic load-bank testing operations to start and parallel the generators and operate a load-bank breaker].

#### Source Optimization - (Load demand operation) – While the engines are running and the total load decreases to a preset level, the generators will be shut down but ready for automatic restart if needed.

#### Load Shedding - In the event that the total plant load exceeds the maximum capacity of the available generators some loads will be shed.  Each load will be individually shed from and added to the system based on its kilowatt level.

#### System Test – Ability to test the generators un-loaded or with load.

#### Manual Operation – Complete manual capability of paralleling the generators together as well as supplying emergency power upon failure of automatic operation.

#### Building Exerciser – Ability to run the engines on a user defined schedule.  The generators may be scheduled to run unloaded or loaded via downstream transfer devices-ATS’s.

## FINISH

### All steel surfaces shall be chemically cleaned prior to painting.

### Exterior paint color shall be ANSI 61 Light Gray over phosphate - type rust inhibitor.

## FACTORY TESTS

### The following production tests shall be performed prior to shipment:

#### Ring-out all AC and DC control circuits.

#### Check operation of all metering, relaying and controller devices using secondary current and/or voltage injection.

#### Factory simulate the utility and generator sources for ensuring proper automatic and manual operations for the paralleling system.

#### Production tests as required by ANSI/IEEE C37.20.2.

#### Factory witness testing and test reports available if specified.

## PREPARATION FOR SHIPMENT

### Provide suitable packaging and supports to enable the equipment to withstand shocks and vibrations from normal domestic shipping and handling.

# EXECUTION

## EXAMINATION

### The following procedures shall be performed by the Contractor.

#### Examine installation area to assure there is enough clearance to install switchgear.

#### Check concrete pads for uniformity and level surface.

#### Verify that equipment is ready to install.

#### Verify field measurements are as [{shown on drawings] [instructed by manufacturer}].

#### Verify that required utilities are available, in proper location and ready for use.

#### Beginning of installation signifies installer accepts condition of equipment.

## LOCATION – Specify location of equipment

## INSTALLATION

NOTE TO SPECIFIER: ADDITIONAL PROVISIONS AND EDITING MAY BE REQUIRED FOR THIS PART.

### Installation shall be performed by the Contractor.

#### Install per manufacturer's instructions.

#### Install required safety labels.

### Inspection and operational tests shall be conducted by the contractor in the presence of the engineer, to indicate that the switch satisfies the specifications.

## START-UP SERVICE

### Provide a qualified service engineer to assist in the following:

#### Pre-installation meeting with the contractor, engineer and other related personnel to coordinate the installation, interconnection of all related equipment and start-up requirements.

#### Start-up of the system with complete testing.

#### Four (4) hours of on-site training for operating personnel.

END OF SECTION