# GENERAL

## SECTION INCLUDES

### This specification describes metal enclosed vacuum circuit breaker in series with an air insulated load break switch. The switch or switches shall be on the line side of breakers as indicated on the plans or described in this specification. The device may be either stand alone or close coupled to the primary side of secondary substation style transformer as indicated on drawings.

## REFERENCES

### The equipment and components in this specification shall be designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### IEEE C37.20.3 Standard for Metal-Enclosed Interrupter (MEI) Switchgear Assemblies Standard for Metal-Enclosed Interrupter Switchgear (1 kV–38 kV)

### IEEE C37.20.4 Standard for Indoor AC Switches (1 kV - 38 kV) for Use in Metal-Enclosed Switchgear

### IEEE C37.04  Standard for Ratings and Requirements for AC High-Voltage Circuit Breakers with Rated Maximum Voltage Above 1000 V

### IEEE C37.09 Standard Test Procedures for AC High-Voltage Circuit Breakers with Rated Maximum Voltage Above 1000 V

### ANSI C37.54 Indoor AC High-Voltage Circuit Breakers Applied As Removable Elements In Metal-Enclosed Switchgear - Conformance Test Procedures

### ANSI C37.57 Switchgear - Metal-Enclosed Interrupter Switchgear Assemblies - Conformance Testing

### ANSI C37.58 Switchgear - Indoor AC Medium-Voltage Switches For Use In Metal-Enclosed Switchgear - Conformance Test Procedures

## DEFINITIONS

## SYSTEM DESCRIPTION

### The switches shall be applied on a [solidly] [low resistance] [high resistance] [ungrounded] power system nominally rated at [     ]kV.

## SUBMITTALS

### Manufacturer shall provide [3] copies of the following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26]:

#### Product Data on specified product;

#### Shop Drawings on specified product;

## INSTALLATION, OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide [3] copies of installation, operation and maintenance procedures to owner in accordance with general requirements of Division [1] [01] and Division [16] [26].

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of medium voltage metal enclosed switchgear for [25] years.

### Medium voltage metal enclosed switchgear shall be listed and/or classified by Underwriters Laboratories in accordance with standards listed in Article 1.02 of this specification.

### Equipment shall be qualified for use in seismic areas as follows:

#### High seismic loading as defined in ASCE 7-10, IBC 2021 and CBC 2022.

#### CBC-2022, Sds = 2.00g, Ip = 1.5, for z/h equal to 1 and Sds = 2.5g, Ip = 1.5, for z/h equal to 0 in accordance with ICC-ES-AC156.

#### Seismic compliance shall be qualified through shake table testing. Further extension based on experience-based data methodology is permissible.  Compliance by calculation only is not acceptable. Seismic compliance shall apply to both NEMA 1 and NEMA 3R enclosures.

## DELIVERY, STORAGE, AND HANDLING

### Contractor shall store, protect, and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Ship each section in individual shipping splits for ease of handling. Each section shall be mounted on shipping skids and wrapped for protection.

### Contractor shall inspect and report concealed damage to carrier within 48 hours.

### Contractor shall store in a clean, dry space. Cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic. Heat enclosures to prevent condensation.

### Contractor shall handle in accordance with manufacturer's recommendations to avoid damaging equipment, installed devices, and finish. [Lift only by installed lifting eyes.]

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow (standards) service conditions before, during and after switchgear installation.

### [		] shall be located in well ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between minus 30 and plus 40 degrees C. Indoor locations shall be protected to prevent moisture from entering enclosure.

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for 1 year from date of installation or 18 months from date of shipment, whichever occurs first.

## FIELD MEASUREMENTS

### Contractor shall make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code

# PRODUCTS

## MANUFACTURER

### ABB BreakMaster V has been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.

## EQUIPMENT

### Furnish ABB BreakMaster V switchgear (or pre-approved equal).

## COMPONENTS

### Refer to Contract Drawings for actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; interrupting and withstand ratings of devices, buses, and components; and other required details.

### Ratings

#### Breakers shall be rated: [600Amp][1200 Amp], nominally [5kV, 60kV BIL] [15kV, 95kV BIL], 3 - phase, 3 – wire, [31.5kA] [40kA] symmetrical.  Higer rated breakers are acceptable. The switches shall be rated either 600 or 1200 amperes as shown on the plans.

### Protective Relay (select only one of the following):

#### ABB REF615

#### ABB RET615

#### ABB RED615

#### GE Multilin T30

#### GE Multilin F-35

#### SEL 751A

#### Remote relay

#### Customer supplied. Blank plate by factory.

### Metering

1. 	Metering PTs shall be [from external section] [provided]. Note to specifier: PTs not available for “front access only” applications.

2. 	Provide [provision for customer metering] [PQM II or equal].

3. 	Metering shall include A, V, W, Wh, Wcost, var, varh, VA, VAh, Hz, and PF in True RMS or displacement (fundamental) quantities.

4. 	Power analysis features shall include an event recorder, waveform capture, trace memory, harmonic spectrum display (through the 62nd harmonic with total harmonic distortion) and a data logger function. All analysis data shall be non-volatile.

5. 	Four switch inputs shall be provided which can be programmed for relay activation, counters, logic, demand sync, reset and alarms. Four output relays shall be provided which can be programmed to activate on alarms, setpoints, switch inputs, kWh pulse, trace memory triggers or communications control. These output relays shall also be able to use demand metering values of A, VAR, W and VA to control load shedding.

6. 	PLC interface shall be provided via four isolated 4-20mA outputs programmable from measured and calculated parameters.

7. 	Transducer monitoring shall be provided via a 4-20mA input.

8. 	Local user interface shall include a keypad and display for entering all setpoints and reading all measured values, and LED indicators for output relays, communication status and alarm status.

9. 	An RS232 computer interface port shall be located on the front panel. Two RS485 and one RS232 communication ports shall be provided for simultaneous access using ModBus® RTU protocol. Windows® based software shall be provided to enable setpoint programming.

10. 	Provide [ammeter & switch] [ammeter without switch] [voltmeter & switch] [voltmeter without switch].

### Current Transformers

#### Furnish and install C____ Relay Class CTs on the load side of the breaker. The CT ratio shall be___________ or as indicated on drawings.

#### Furnish and install C____ Relay Class CTs on the line side of the breaker. The CT ratio shall be___________ or as indicated on drawings.

#### Furnish and install ground fault sensor, type C____ relay class transformer with a ratio of ________A.

#### Furnish and install C____ Relay Class CTs on the transformer secondary. CT ratio shall be___________ or as indicated on drawings.   CT secondary conductors shall be installed in ½” Rigid Galvanized Steel conduit routed to protective relay terminal board located within the BreakMaster V control compartment.

### Construction

#### Each section of the equipment lineup shall be constructed of sheet steel and shall be bolted frame construction. Each section shall be adequately braced and shall have adequate venting to prevent distortion of the cubicle doors and windows under operating conditions. Operating conditions shall include normal operations under load, short circuits, and fuse operation and interruption of short circuits up to the specified rating of the switch.

#### Each stack shall be front connected and front accessible, unless special project requirements dictate differently. Interlock provisions shall be provided so that the lower breaker compartment door cannot be opened until the line side switch is opened.

#### Enclosure shall be constructed of 11-gauge sheet steel. This shall include doors, back panels, and side panels.

#### Each section shall have a front steel door with safety protected observation windows that shall allow sufficient viewing of the switch contact position. All steel doors shall have concealed hinges and bolting hardware to secure the door in the closed position. A mechanical switch and door interlock shall be provided to prevent opening the door when the switch is in the "on" position.

#### Individual doors shall be provided for each switch compartment and for each breaker compartment.

#### The standard indoor depth shall be 50 inches.  An optional depth of 60 inches shall be available for special applications or the mounting of additional devices.  Each section shall be 35 inches wide.

#### Top access covers shall be removable for faster conduit installation from above.

#### Louvered ventilation openings shall be provided as required.

#### [Provide rodent barriers.]

#### [Enclosure shall be dust resistant]

#### Outdoor equipment shall be weather resistant, gasketed, and equipped with long life space heaters. Control power shall be from [an external source][from a CPT mounted in the lineup]. The outdoor equipment shall be provided with removable filters for the ventilation louvers. The roof shall be sloped for moisture runoff.  A four-inch channel base shall also be provided. The outdoor construction shall be non-walk-in. The outdoor equipment shall have the same paint process as above and shall be the same color.

#### [Provide undercoating on outdoor equipment base.]

#### Provide space heaters on indoor equipment. Space heaters shall be fed from [local control power transformer] [remote source].

#### [Space heaters, when provided shall be thermostatically controlled.]

#### [Light & convenience receptacle.]

#### Lifting angles or other suitable means for lifting shall be provided.

#### [Provide a mimic bus on the front of the lineup.]

#### [Provide tamper resistant hardware.]

#### [The switchgear shall be UL listed.]

### Bus

#### The switchgear bus shall be [tin plated] [silver plated] copper. The main bus shall be fully rated. Conical washer bolts shall be provided on all bus joints. The main bus shall be braced to withstand the effects of a short circuit within the ratings of the equipment.  Supports for the main bus shall be polyester glass. [The main bus shall be fully insulated]

#### A full-length ground bus shall be provided in the equipment lineup. A 4/0 lug shall be provided at each end of the ground bus. The ground bus shall be arranged for future extension.

#### Where bus bars are insulated to allow closer spacing, the insulation used shall be sleeve type. Where joints are made, the joints shall be sealed with molded covers.

### Air Interrupter Switches

#### The air interrupter switches shall be gang operated, stored energy type, 3 - pole, single throw, 2 - position (open / close) and either 600 or 1200 amperes as shown on the plans. The switch mechanism shall be externally operable from the front or side of the cubicle. Each switch shall utilize a direct acting spring charged mechanism for both opening and closing and shall be of the quick-make, quick-break type. The opening and close of the switch shall be independent of the speed at which the handle is moved. "Teasing" of the switch poles will not be permitted. Each switch shall be manually or electrically operated as shown on the plans.

#### Each switch shall have main and arcing contacts and be designed to provide maximum endurance for load interrupting and fault closing. The arcing contacts shall be spring-loaded on-break and shall be last in and last-out. The arcing contacts shall operate in an arc chute designed to assist in interruption and liberate no appreciable gases on interruption.

#### All components, except the operating handle system, shall be mounted on a jig-welded frame to form a rugged unitized assembly to ensure all parts function as required. A strict quality control program shall be instituted and followed.

#### The main blades of each switch shall be made of electrolytically pure cold rolled copper. All contact points shall be heavily silver plated on the blades as well as the hinges and jaw castings. Each of these castings shall be one piece to provide maximum heat dissipation and continuous heat transfer.

#### The rating of the interrupter switches shall be [600A, 5kV, 60kV BIL, 40kA momentary, 40kA fault close asymmetrical] [600A, 5kV, 60kV BIL, 61kA momentary, 61kA fault close asymmetrical] [1200A, 5kV, 60kV BIL, 40kA momentary, 40kA fault close asymmetrical] [1200A, 5kV, 60kV BIL, 61kA momentary, 61kA fault close asymmetrical] [600A, 5kV, 95kV BIL, 40kA momentary, 40kA fault close asymmetrical] [600A, 5kV, 95kV BIL, 61kA momentary, 61kA fault close asymmetrical] [1200A, 5kV, 95kV BIL, 40kA momentary, 40kA fault close asymmetrical] [1200A, 5kV, 95kV BIL, 61kA momentary, 61kA fault close asymmetrical] [600A, 15kV, 95kV BIL, 40kA momentary, 40kA fault close asymmetrical] [600A, 15kV, 95kV BIL, 61kA momentary, 61kA fault close asymmetrical] [1200A, 15kV, 95kV BIL, 40kA momentary, 40kA fault close asymmetrical] [1200A, 15kV, 95kV BIL, 61kA momentary, 61kA fault close asymmetrical].

#### The switch shall conform to or exceed ANSI/IEEE Standards for high-voltage air switches and switchgear assemblies C37.20.3, C37.20.4, C37.54, C37.57 and C37.58. Upon request, test certificates shall be provided confirming published interrupting, short-time, momentary, BIL, dielectric and fault-closing ratings.

#### All components of each shall be completely checked and operated in compliance with documented quality assurance procedure to ensure that all parts function as intended after manufacture and assembly. Testing shall consist of power frequency withstand and mechanical operations.

#### Interphase barriers shall be provided for each switch. Horizontal barriers between the switch and cable terminals or breaker compartment (when required) shall be provided.

#### Provision shall be included for locking the switch in the open or closed position. The door shall be mechanically interlocked with the air interrupter switch to prevent closing the switch with the door open and to prevent opening the door with the switch closed.

#### Switch operating handles shall be externally mounted [removable] [non-removable] (except for electric operators), self-leveling, and padlockable with multiple padlocks in either the open or closed position. OPEN/CLOSE indicators shall advise operators of the switch position.

### Switch Accessories

#### [Auxiliary contacts, 3NO/3NC]

#### [Mechanical type operations counter]

#### [Shunt trip, rated [110 VAC] [125 VDC]]

#### [Spare fuse holder]

#### [Blown fuse indication]

#### [Blown fuse trip]

### Each lineup shall be provided with a permanent non-corrosive nameplate. All units shall have appropriate hazardous danger signs prominently displayed on the exterior and interior of each section.

### Provisions for terminations shall be NEMA Drill configuration only.

### [Provide key interlocks as indicated on drawings.]

### [Provide [distribution class] [intermediate class] [station class] lightning arresters, rated (3kV, 6kV, 9kV, 10kV, 12kV, 15kV) where indicated on drawings.  Note to specifier:  arresters are not available for “front access only” applications.

### Medium voltage vacuum circuit breakers

      - Construction and Type

##### Each breaker shall be stationary mounted in compartment below switch and separated with full horizontal metal barrier.  Breakers shall be electrically located on the load side of switch.

##### The power circuit breakers shall be electrically operated, 3-pole, draw-out type utilizing vacuum interrupters.

          - [Circuit breakers to be ABB type VD4, utilizing a spring type stored-energy actuated operating mechanism and a mechanical anti-pump device in lieu of an anti-pump relay, for ratings of 5-15kV, up to 40kA.]

          - [Circuit breakers to be ABB type VM1, utilizing a magnetically actuated operating mechanism, for ratings of 5-15kV, up to 31.5kA.]

        - Opening and closing speed shall be independent of the operator or of control voltage within the rated control voltage range when VM1 breakers are specified.

        - Circuit breakers of the same type, rating and control circuits shall be electrically and mechanically interchangeable.

        - Breakers shall use vacuum interrupters embedded in epoxy for protection against dust, water and debris accumulation on the interrupters and for protection against accidental impact during breaker transport.

      - Ratings

        - The ratings of the breaker shall be chosen from the following values:

| Maximum Voltage (kV) | Power Frequency Withstand (kV) | Impulse Level (BIL) (kV) | Rated Short Circuit Current (kA rms) | Close and Latch (kA peak) | Rated Voltage Range Factor (K) |
| --- | --- | --- | --- | --- | --- |
| 5 | 19 | 60 | 31.5 | 82 | 1.0 |
| 5 | 19 | 60 | 40 | 104 | 1.0 |
| 15 | 36 | 95 | 31.5 | 82 | 1.0 |
| 15 | 36 | 95 | 40 | 104 | 1.0 |

      - Controls

        - Circuit breaker trip and close circuits shall be electrically separate.

        - Provisions shall be provided for manual breaker tripping. These provisions shall be mounted and easily accessible on the front of the breaker.

        - The breaker shall have flags to indicate open or closed position. Only the correct status flag for any single function shall be visible.

        - The control voltage shall be [48 V DC] [120 V AC] [125 V DC]

        - Charge, trip and close circuits shall be separately fused. Dead front pull-out fuses shall be used.

          - [Close, trip and/or charge circuits to be separately protected with a Molded Case Circuit Breaker (MCCB)]

      - Auxiliary Contacts

        - For 5-15kV, 31.5-40kA (9) ‘a’ and (8) ‘b’ auxiliary contacts will be mounted on the breaker and wired through the umbilical secondary disconnect system.

      - Interlocks

        - The circuit breaker module shall include all necessary interlocks for proper sequencing and safe operation.

        - Interference blocking shall prevent insertion of a lower rated breaker into a higher rated compartment.

### Instrument Transformers

#### Current transformers with shorting terminal block shall be provided.  Current ratings shall be as indicated on drawings.

#### Provide potential transformers with fused primary, stationary mounted, rated and configured as indicated on drawings.

### Control Power

#### Where indicated on drawings, provide a stationary mounted control power transformer rated 5 kVA.  Note to specifier:  CPT not available for “front access only” applications.

### [Asset Health Monitoring] (Note: Standard is no asset health monitoring)

- Switchgear shall be equipped for 24x7 monitoring of the temperature at all incoming and outgoing primary cable connections using the ABB SwitchgearMD™ [wireless] [infrared] monitoring systems.  (Note: If partial discharge is required, then only wireless can be selected. Standard offering is infrared.)

- Switchgear shall be equipped for 24x7 monitoring of internal humidity.

- [Switchgear shall be equipped for 24x7 monitoring of partial discharge activity in designated compartments.]  (Note: Partial Discharge monitoring is optional. Must use wireless monitoring system if PD detection is required. Standard is monitoring of the cable connection temperatures and switchgear humidity only.)

- [Main bus and non-cable lug pad joints to be monitored for temperature.] (Note:  Standard is monitoring of incoming/outgoing cable connections only.)

- Monitoring system shall trigger alarms based on configurable thresholds.

- Monitored data will be displayed on an HMI unit mounted on the door of an instrument compartment.

- [Monitored data to be made available to a remote system such as a SCADA or a Data Historian.] (Note: Standard is no data made available to remote systems.)

## FINISH

### All steel surfaces shall be chemically cleaned prior to painting and undergo a phosphate treatment.

### All surfaces shall be finished in ANSI 61 Light Gray. The paint finish shall be rated for 1000-hour salt spray, per IEEE C37.20.3.

# EXECUTION

## FACTORY TESTING

### The equipment shall be factory assembled in its entirety and tested in accordance with production testing requirements in IEEE C37.20.2 prior to shipment.

### Factory Witness Testing (Note:  Standard is no factory witness testing)

      - [Factory witness testing shall be included in the price of the switchgear.]

      - [Factory witness testing shall allow up to 3 members the applicable number of days to witness the factory tests as listed above.]

      - [Buyer must be made aware of factory test dates in advance to facilitate arrangement of travel plans.]

## EXAMINATION

### The following procedures shall be performed by the Contractor.

#### Examine installation area to assure there is enough clearance to install switchboard.

#### Check concrete pads for uniformity and level surface.

#### Verify that equipment is ready to install.

#### Verify field measurements are as [shown on Drawings] [instructed by manufacturer].

#### Verify that required utilities are available, in proper location and ready for use.

#### Beginning of installation means installer accepts conditions.

## INSTALLATION

### Installation shall be performed by the Contractor.

#### Install per manufacturer's instructions.

#### Install required safety labels.

## FIELD TESTING AND COMMISSIONING

### All testing and commissioning is to be performed per the latest NETA and/or local requirements.

### When SwitchgearMDTM system is installed, the T&C contractor, owner or operator must record baseline data from temperature, humidity and partial discharge sensors at least 4 but no more than 24 hours after energization

## TRAINING

    - [Manufacturer to provide x hours of switchgear operations training.] (Note: Training is not included as standard.)

    - [Provide x hours of SwitchgearMD™ asset health monitoring training.]  (Note: This training is only required if SwitchgearMD is specified. Eight (8) hours training minimum is recommended.)

END OF SECTION