SAMI STAR

Frequency Converters

SCALAR CONTROLSCALAR CONTROL

Code:	3AFE 58057142

Revision:	E

Language:	EN

Issued by:	FIDRI/EIB

Date:		03.05.94

File:			SCAL40E.DOC

Created with:	Word for Windows 2.0

Designer 3.1

Table of revisions:

Date:	Code:	Rev.:	Remark:

1990-12-24	3AFE58057142	A	First issue

1994-05-03	3AFE58057142	E	Corrections,Thermal model

added,Cosfiifactor.

Table of references:

For information on:	See:

The technical data and specifications are valid at the time of printing.

We reserve the right to subsequent alterations.

Contents	Page

1.	USE OF THE EEPROM MEMORY	7

2.	CURRENT AND UC MEASUREMENT CALIBRATION	8

2.1	Elimination of the output current offset	8

2.2	Calibration of the Uc measurement	9

3.	DIAGNOSTICS	10

3.1	Memory battery backup	10

3.2	Status and fault messages	11

3.3	Fault history	13

3.4	Short-circuit and earth-fault test	13

3.5	Serial data communications supervision	14

3.6	ABB Master Fieldbus communications supervision	15

3.7	Peak current and current balance supervision	16

4.	SELECTION OF OPTIONS	17

5.	START AND STOP	18

5.1	Use of the STATUS_CMD 13T command word	19

6.	REFERENCE VALUES	21

7.	ACTUAL VALUES	22

8.	FREQUENCY REFERENCE VALUE INTEGRATOR	25

8.1	Variable slope function in frequency reference integrator	25

8.2	Parameters	26

9.	FORMATION OF THE OUTPUT VOLTAGE	28

9.1	Parameters	28

10.	UC OVERVOLTAGE CONTROL	30

10.1	Control operation	30

10.2	Uc-control parameters	30

11.	TORQUE LIMIT CONTROL	31

11.1	Torque limit control parameters	33

12.	STABILIZERS	34

12.1	Torque stabilization	34

12.2	Uc stabilization	35

12.3	Flux stabilization	35

13.	IR COMPENSATION (TORQUE MAXIMIZATION)	37

13.1	Developing a motor flux	37

13.2	Calculation of additional voltage	38

13.3	Peak current limiting control	39

13.4	Automatic search of maximum compensation	39

13.5	IR-compensation by using constant voltage addition	39

13.6	IR compensation parameters	40

Page

14.	DC BRAKING	42

14.1	Parameters of DC braking	42

15.	STALL PROTECTION	43

15.1	Stall protection parameters	43

16.	SLIP COMPENSATION	44

16.1	Slip compensation parameters	44

17.	RUNNING START	45

17.1	Running start operation	45

17.2	Running start parameters	46

18.	POWER LOSS CONTROL	47

18.1	Control operation	47

18.2	Power loss control parameters	47

19.	SPEED MEASUREMENT	49

19.1	Speed measurement parameters	50

20.	SPEED CONTROL	52

20.1	Setting the speed reference	53

20.2	Rounding function of the speed integrator	53

20.3	Integrator control in running start	54

20.4	Acceleration compensation	54

20.5	PI control	55

20.6	Drooping	57

20.7	Speed control parameters	57

21.	TORQUE CONTROL	59

21.1	Torque control parameters	59

22.	CHANGE OF THE CONTROL MODE	60

23.	DROOPING BASED ON IRE	60

24.	TREND BUFFERS	61

25.	D/A CONVERTER	65

26.	MOTOR THERMAL MODEL	69

26.1	The effect of different loads on temperature rise	72

26.2	Thermal model panel indications	74

26.3	Thermal model setting parameters	74

26.4	Input signals:	75

26.5	Output signals:	75

27.	COMMUNICATION TABLE	76

28.	GENERAL BLOCK DIAGRAM (57777931)	135

29.	IDENTIFICATION OF THE MEMORY CIRCUITS	136

30.	SOFTWARE REVISIONS	137

30.1	Changes in the scalar control software	137

GENERAL

The present manual describes the use of SAMI STAR scalar control and the parameter range in the program memory version SAFRSC 4.04.  The description covers the 1...1299 parameter range.  The range 1300 to higher parameter addresses is dealt with in the

SAMI STAR APPLICATION BLOCKS Manual

SAFRSC 4.04 / SAFRVC 4.00

3AFE58057401

The entire program is stored in two EPROM memory circuits .  The circuits are mounted on the SAFT 187 CON control card.  The identification labels are:

SAFRSC 4.04E         	SAFRSC 4.04E

D17		   		D18

56020322  94MMDD     	56020331  94MMDD

NOTE! Memory circuits D17 and D18 must have the same version and date.

In this manual, when referring to the communication table, parameter names, sequential numbers and type identifiers T, TEE or TM are used.

- 	T	measuring point in general, the value is not saved in the

EEPROM.

-	TEE	parameter which can be saved in the EEPROM.

-	TM	measuring point which is protected by the battery backup.

SINGLE DRIVE / SECTIONAL DRIVE

Software version SAFRSC 4.04 can be used in single and sectional drives.

SECTIONAL DRIVE

In sectional drives SAMI is connecting to external world via SAFT 189 TSI card. In that case the drive can be controlled only via serial communication. Control Panel SAFP 21 PAN is connected to serial channel 1 or 2. Parameter CP2_SERIAL_CH 337TEE has to be set to the right channel according to application :

CP2_SERIAL_CH 337TEE = 1 	Connected to ch 1

CP2_SERIAL_CH 337TEE = 2	Connected to ch 2

SINGLE DRIVE

In single drives SAMI is connecting to external world via SAFT 188 IOC and SAFT 174 TBC cards. In that case there is available digital input / output, analog input/output and serial communication interface.

Control Panel SAFP 21 PAN is connected always to serial channel 2.

The program sets automatically value 2 to parameter CP2_SERIAL_CH 337TEE.

The following list shows parameters, whose initial values are different in single and sectional drives :

COMMUNICATION PARAMETERS IN CHANNEL 1

Name		Address/	initial value

Type 		sectional drive	single drive

IVAL0 		114TEE	21		10

IX0		115TEE	214		247

IVAL1		116TEE	23		9

IX1		117TEE	210		248

IVAL2		118TEE	25		9

IX2		119TEE	211		249

IVAL3		120TEE	27		8

IX3		121TEE	208		15

IVAL4		122TEE	29		8

IX4		123TEE	201		16

CP2_SERIAL_CH 337TEE	1		2

APPLICATION BLOCK SCALAR CONTROL

START1	1386TEE	0		1343

STOP1	1389TEE	0		1344

RESET	1391TEE	0		1349

FREF		1392TEE	0		1574

1.	USE OF THE EEPROM MEMORY

A knowledge of how to use an EEPROM memory circuit is important since the inverter related parameters and the application program data are stored in the EEPROM.  A completely different inverter application can be implemented only by changing the EEPROM circuit.

When auxiliary voltages are connected to the control card and the EEPROM circuit contains data, the control function is instantly ready for use.

A write enable and disable state of the EEPROM memory circuit is dependent on the position of the selector plug S4.   When S4 is in the a-b position, write is enabled, and when it is in the a-c position, write is disabled.  If an attempt is made to write to the memory when the selector is in the disabled position, the status message SA 52 (CP1) or "NO WR TO EEPROM" (CP2) is displayed.  The message is turned off when EEPROMLOCK 8T is set to zero.  A write disable mode can be used when it is desired to avoid an unqualified change of EEPROM memory content due to misuse or malfunction.

When the EEPROM is a new circuit, i.e. empty, the inverter's software transfers so-called INITIALIZATION VALUES for the parameters.  These values are given in the communication table.  During initialization, when storing is executed, the code "SA 51" is displayed on the control panel CP1 or the message "STORED TO BACKUP" is displayed on the control panel CP2.  After the initialization the code "SA 50" is displayed on the CP1 or "NO BACKUP/NEW EP" on the CP2.  A start-up of the inverter is not allowed until the auxiliary voltage supply has been switched off for about 15 seconds.  This is done in order to ensure that no false start occurs using wrong parameter values for the drive.

When it is desired to change a parameter value to be stored in the EERPOM, proceed as follows:

-	set EEPROMLOCK 8T = 0 (reset EEPROM writing lock),

-	set the desired parameter values,

-	wait until CP1 displays the message "SA 51" or CP2 "STORED TO

BACKUP",

-	set EEPROMLOCK 8T = 0.

Parameter values can be changed also during an inverter run.

Any used EEPROM can be set to zero and initialized again as follows:

-	set DEBUGADDR 216T = 28670,

-	change DEBUGDATA 217T content,

-	switch off auxiliary voltage supply and wait for about 15 seconds,

-	switch on auxiliary voltage supply.

The program now functions as in the process of initialization of the new

EEPROM circuit (see above).

2.	CURRENT AND UC MEASUREMENT CALIBRATION

The drive's rated supply voltage is given to the program in voltage units by means of the SAMI_AC_RATEDVOLTAGE 65TEE parameter.  The rated voltage value is given in the Matching Card type designation.  For example, SAFT 40F380 has a rated voltage of 380 V as shown by the last three digits.  A definition of the supply voltage is extremely important on the 415 V drives, since its value is needed not only for other parameters but also for current measurement scaling.

The program includes the elimination of the output current measurement offset and a Uc-measurement calibration option.

2.1	Elimination of the output current offset

The offset error compensation always functions when the  inverter is not running.  The highest permissible offset value the program can eliminate in current measurement is determined by using the CURRENTOFFSET 190TEE parameter.  If the error is larger, the inverter displays the FL 19 current measurement fault message during the start-up process.

When it is desired to adjust the current measurement circuit of the SAFT 187 CON control card, proceed as follows:

-	Remember that the control card is under the main circuit potential and

exercise care.

-	Set the CURRENTOFFSET 190TEE parameter to zero.

-	Observe the IR 219T measuring point content and adjust the offset as close to

zero as possible by means of the trimmer R12.

-	Observe the IS 220T measuring point content and adjust the offset as close to

zero as possible by means of the trimmer R13.

-	Finally, set 190TEE to the value of 50 (50 = 5 %).

2.2	Calibration of the Uc measurement

The Uc measurement calibration function operates only on request.  It can be used when the Uc measurement error has a significant value. The program allows us to eliminate measurement errors of 5 %.  A calibration is performed as follows:

-	Check that the SAMI_AC_RATEDVOLTAGE 65TEE parameter content

corresponds to the rated supply voltage.

-	Set EEPROMLOCK 8T = 1.

-	Measure Uc voltage by means of a voltmeter (main contactor closed).

-	Observe the UCVOLTAGE 257T content, i.e. voltage measured by the inverter

in volts, and compare it with the voltage measured by a voltmeter.

-	If the difference between the two values is too large (e.g. >2 %), set the value

measured by the voltmeter as the content of parameter

UCMEASURED_ON_BUS 258TEE in volts.

-	Set the parameter FIND_UC_OFFSET 260T = 1.

-	Check that the content of the measuring point 257T and the voltmeter readout

are approximately of the same value.

-	Finally, set 8T to zero.

The program block is automatically disconnected after the calibration.

3.	DIAGNOSTICS

The program contains a comprehensive diagnostics facility which can be used for drive adjustments and especially for troubleshooting. The diagnostics encompasses the following functions:

-	memory battery backup,

-	status and fault messages,

-	fault history,

-	short-circuit and earth-fault testing during start-up (GTO),

-	serial data communications monitoring.

In addition to this the program has 8 trend buffers and a control program for the 4-channel D/A converter.  For their descriptions, see sections 24 and 25.

3.1	Memory battery backup

The SAFT 187 CON card includes a small battery which helps to retain diagnostic data in memory when the power is otherwise disconnected from the card.  This battery backup is connected by means of selector plug S3 of the SAFT 187 CON control card (position a-b).

If the battery is empty, it takes about 30 hours to recharge it.  A fully charged battery

retains data for about 300 hours.

In the event of a supply voltage failure, the program stores the following data to battery protected memory locations:

-	fault words FAULTWORD0...2 	210TM...212TM

-	fault buffer FLT_QUEUE       	176TM...181TM

-	trend buffers TRENDBUF1...8  	500TM...1299TM

-	fault display (FL)

-	in addition, 12 extra parameters can be stored to the memory

by means of the application program RAMSTORE functional block.

3.2	Status and fault messages

In the program, status and fault messages of the inverter are grouped into three fault words.Each bit of a fault word corresponds to a certain fault or status of the inverter.

Inverter hardware faults are grouped in FAULTWORD0 210TM,

software faults in FAULTWORD1 211TM and

status data in FAULTWORD2 212TM.

When a fault occurs, the control panel CP1 reports a fault code and the control panel CP2 displays a fault message.  CP1's codes are divided into "FL" tripping type codes and "SA" codes which do not stop a drive but can prevent its start-up.

The "FL" messages are continuously displayed and should be reset by means of the RESET pushbutton (with the exception of the functional block programmable faults FL 25 and FL 26).  If a fault is displayed when a power failure occurs (battery backup connected), the fault message reappears on the control panel when the power supply is reconnected.  This does not, however, inhibit a start-up of the inverter if the actual fault has been eliminated.  The fault message is removed by pressing the RESET pushbutton.

The "SA" type messages are displayed for a short period of time or a message is blinking until the fault is eliminated.  In normal conditions status messages need not be reset, with the exception of the SA 56 (RESET) messages associated with the battery backup and the SA 52 (8T = 0) associated with the EEPROM use.

An undervoltage fault FL 7 is automatically reset when the intermediate circuit voltage is sufficient and there are no other faults.

Undervoltage tripping limit is 70% of the nominal Uc voltage. If necessary it can be set

60% of the nominal Uc voltage.

Pin header S7, selection of Uc-under voltage release on the SAFT 187 CON.

-	70% level, S7 in position a-a

-	60% level, S7 in position a-b.

Fault and status messages

CP1		CP2

FL1		CHOP UNDERVOLT	Chopper undervoltage (GTO)

FL2		CHOP OVERVOLT		Chopper overvoltage (GTO)

FL3		AUX UNDERVOLT	Auxiliary voltage fault

FL4		OVERTEMPERATURE	Inverter overheat

FL5		OVERCURRENT	Overcurrent

FL6		DC OVERVOLT	DC intermediate circuit overvoltage

FL7		DC UNDERVOLT	DC intermediate circuit undervoltage

FL8

FL9		U1 FAULT		U1 phase fault

FL10		U2 FAULT		U2 phase fault

FL11		V1 FAULT		V1 phase fault

FL12		V2 FAULT		V2 phase fault

FL13		W1 FAULT		W1 phase fault

FL14		W2 FAULT		W2 phase fault

FL15		SHORT CIRC/EFLT	Output short circuit/earth fault (GTO)

FL16

FL17		COMMUNIC FAULT	Serial data communication fault

FL18		TACHO LOSS	Tachometer fault

FL19		I MEAS FAULT	Current measurement fault

FL20		MOTOR STALLED	Stall protection triggered

FL21		MATCH CARD FAULT	Matching card fault

FL22		PROCESSOR FAULT	Processor fault

FL23

FL24

FL25		DIS25 FAULT	Functional block programmable fault

FL26		DIS26 FAULT	Functional block programmable fault

FL28		LNKFLTMA FAULT	SamiNode fault

FL29		MOT OVERTEMP FLT	Overload of motor

SA50	NO BACKUP/NEW EP	New EEPROM

SA51	STORED TO BACKUP	Storing to EEPROM

SA52	NO WR TO EEPROM	Storing to EEPROM failed

SA53	PARAM TOO LOW	Parameter too low

SA54	PARAM TOO HIGH	Parameter too high

SA55	ILLEGAL PARAM	Attempt of storing to an illegal address

SA56	NO BATT BACKUP	No battery backup

SA57	LOW AC/DC VOLT	Low voltage (main contactor open)

SA58	START INHIBIT	Start-up inhibited

SA59	SYSTEM RESTART	Processor reset message

SA60	MOT OVERTEMP ALM	Overload alarm

3.3	Fault history

The program contains the six-location fault buffer FLT_QUEUE 176TM...181TM.  On

receiving a fault code the program stores the FL number to the 176 TM - the most significant

location of the buffer. When the operator presses the RESET pushbutton, the program

stores -1 to the location 176TM and transfers the previous FL number to the location 177TM.

This allows the operator to separate fault messages related to the different instants from

each other.  If several faults occur simultaneously, the program cannot define the relative

sequence of the codes but, rather, all the codes are stored to the fault buffer.

3.4	Short-circuit and earth-fault test

Presence of a short circuit or earth fault in the output terminals could lead to serious damage

of the components, particularly in GTO inverters.  For this reason a test for measuring a

possible short-circuit or earth-fault current in the inverter output is executed prior to start-up

in connection with the GTO-inverter chopper charge program.   If the peak current IPEAK

244T is higher than the limit set by parameter E_S_LIMIT 275TEE, the program displays the

fault message (FL 15). The indication is not precise and occurs only during the start-up

procedure so that it cannot be used for actual earth-fault protection.

In GTR inverters, only an earth-fault test is executed in connection with the start-up.

3.5	Serial data communications supervision

The SAFT 187 CON control card has two serial data communication channels.

The baud rate for channel 1 is selected by means of the selector plug S1. The position a-c gives 4800 Bd and the position a-b 9600 Bd.

The baud rate for channel 2 is set by means of parameter CH2BAUDRATE 170TEE.  See the communication table.

Both serial data communication channels can be supervised by means of the message

timeouts. The supervision is based on examining the time between received messages. If the

period between messages is too long, actions to be performed can be defined by means of

the SELMACONT 171TEE parameter.  The duration of the permissible delay is determined

by the COMM_TIMEOUT 172TEE parameter (channel 1) and by the COMM_TIMEOUT2 157TEE parameter (channel 2).

Parameters

Action in the event of a break in the data communications link,

SELMACONT 171TEE

-	0 = no supervision

-	1 = message to control panel

-	2 = message to the panel and inverter stopped by downward integration

-	3 = message to the panel and shut down immediately

Permissible transmission delay for the channel 1,

COMM_TIMEOUT 172TEE

-	0 = no supervision of channel 1

-	1 = 21 ms

-	2 = 42 ms

-	3 = 63 ms  etc.

Permissible transmission delay for the channel 2,

COMM_TIMEOUT2 157TEE

-	0 = no supervision of channel 2

-	1 = 21 ms

-	2 = 42 ms

-	3 = 63 ms  etc.

3.6	ABB Master Fieldbus communications supervision

The supervision is based on status word SAMINODE_COMM 1T which is

send by SamiNode. Parameter SAMINODE_CONT 2351TEE determine

the operation in the case of communication error.

Communication is supervised only when SAMI is working.

Parameters

Action after the communication break, SAMINODE_CONT 2351TEE

-	0 = no supervision

-	1 = message to control panel

-	2 = message to the panel and inverter stopped by downward integration

-	3 = message to the panel and shut down immediately

3.7	Peak current and current balance supervision

An analog hardware connection is used to check the inverter output currents continuously in order to prevent overcurrents.  The hardware connection can be used also to store the

peak current values which are converted by means of an A/D converter and then saved

in the measuring points IPEAK 244T and IPEAK_AD 418T.  If the IPEAK value is

excessively high, it is diagnosed as a current measurement fault.

During normal running, the hardware is used to monitor overshoot of the overcurrent limit

continuously.  When an overshoot occurs the hardware automatically switches off the current but a single overshoot of the overcurrent limit will not cause an overcurrent trip.

If eight consecutive short-time overcurrent releases occur in 2.4 ms, the hardware

performs an overcurrent trip. NOTE! RG 4 inverters have SW tripping after first single

overshoot of the overcurrent limit, please see section 30 and description of changes for

SAFRSC4.04E. The number of short-time overcurrent releases can be observed at the

measuring point IPEAKCOUNT 397T.

In asymmetry tests, the currents IR 219T and IS 220T are used to calculate the value of IT.

The differences between the peak values of all three phase currents IR, IS and IT are

calculated and the greatest detected asymmetry is stored in the measuring point

CURRENTBALANCE 274T.  When using CURRENTBALANCE 274T, note that this measuring point does not see the actual asymmetry at very low frequencies. The calculation of unsymmetry is done only above the frequency limit BAL_FREQ_LIMIT 290TEE.

Parameters

The lower limit for calculation of unsymmetry, BAL_FREQ_LIMIT 290TEE

-	Scaling: 100 = 1Hz

Measuring points

Peak current	 IPEAK 244T

-	Scaling: 2300 = tripping limit

Asymmetry of the current	CURRENTBALANCE 274T

-	Scaling: 10 = 1 % asymmetry of the rated current

4.	SELECTION OF OPTIONS

The software contains a number of extra application-related functions. Each extra function

has its own selection parameter.  An extra function selection, however, requires that the

function be activated by the manufacturer.  Extra functions are dealt with in more detail

in the appropriate sections of the manual.

Options and selection parameters

-	IR compensation, 		IRCOMPSEL 	85TEE *

-	Stall protection, 		STALLPROTECTSEL 	86TEE

-	Running start, 		FLYINGSTARTSEL 	87TEE

-	Power loss control, 	NETFAILSEL 	88TEE

-	Slip compensation, 	SLIPCOMPSEL 	89TEE *

-	Integrator S curve selection,	INTEGMODESEL 	91TEE *

-	Trend buffers, 		TRENDBUFSEL 	93TEE *

-	D/A converters, 		DATRANSFSEL 	95TEE *

-	Torque control, 		TORQCONTSEL 	90TEE

-	Speed measurement, 	SPEEDMEASSEL 	94TEE

-	Speed control, 		SPEEDCONTSEL 	92TEE

-	DC-braking			DCBRAKESEL	96TEE *

The asterisk marked options have been activated at the factory.

A selection of options can also be executed by means of the packed control word

SCDRIVETYPE 166TEE.  An explanation of the bits of the parameter is presented in the

communication table.

5.	START AND STOP

Start and stop requests are typically generated by the application-related programmable blocks which transmit control request commands from control panel pushbuttons and digital inputs of the I/O card to the control addresses of the scalar control block.

There are three start-up addresses: START 2T, START1_P 24T and START2_P 25T.  The

2T is intended for use with a normal running at a variable frequency/speed reference value. The 24T and 25T are used for running at a fixed reference value.  A start-up takes

place when the non-zero value (<>0) is written to the above-mentioned memory location.

Start-up request START 2T

-	FREQREF 29T frequency reference value

-	SPEEDREF 27T speed reference value

-	1386 - pin address of a functional block program

Start-up request START1_P 24T

-	FREQ1 161TEE fixed frequency reference value

-	SPEED1 167TEE fixed speed reference value

-	1387 - pin address of a functional block program

Start-up request START2_P 25T

-	FREQ2 162TEE fixed frequency reference value

-	SPEED2 168TEE fixed speed reference value

-	1388 - pin address of a functional block program

There are two stop addresses: STOP 3T and COAST_STOP 22T. The 3T address performs frequency value integration down to zero.  The frequency-controlled inverter

is stopped when the frequency has dropped below the value determined by the

parameter STOP_FREQ 77TEE.  The speed-controlled inverter is stopped when

the frequency FACT 239T measured on the motor shaft has dropped below the value

determined by the parameter STOP_FREQ 77TEE. The 22T request immediately

stops the inverter. A stop takes place when a non-zero value (<>0) is written to the

above-mentioned memory locations.

Stop request STOP 3T

-	1389 - pin address of a functional block program

Stop request COAST_STOP 22T

-	1390 - pin address of a functional block program

A stop or start-up command can be given in an arbitrary sequence but only the last request remains in force.  When stop and start-up requests come at the same time, the inverter

stops.  When the inverter has stopped, a new request can be initiated only after the restart delay set by the parameter RESTARTDELAY 75TEE (0...20 s, factory setting 3 s).  If start-

up attempt is made while a stop command remains continuously in force, CP1 displays the "SA 58" message and the CP2 "START INHIBIT" message.

5.1	Use of the STATUS_CMD 13T command word

All the inverter's control commands can be given by means of the packed bit-coded command word STATUS_CMD 13T.

When the STATUS_CMD 13T is in use (the content is <> 0), no commands are accepted from the control parameters START 2T, START1_P 24T, START2_P 25T

or STOP 3T.  A RESET 12T is permitted and it also resets the STATUS_CMD 13T.

The inverter can be either speed, frequency or torque controlled by means of the

STATUS_CMD 13T.  Bits 1 (STOP by current limit) and 10 (bypass of the speed integrator) only function when the inverter is speed controlled.

When the STATUS_CMD 13T and the functional block software are used, the SCALAR-block control word connections are:

START1	1386 = 2

START2	1387 = 24

START3	1388 = 25

STOP	1389 = 3

STOP2	1390 = 22

The meaning of the STATUS_CMD 13T bits are:

0 = STOP by ramp.

1 = STOP by current limit.

The input and output of the speed integrator are set to zero and the drive stops when speed controlled on the preset current limits.

2 = COAST STOP

The inverter is shut down immediately.

3 =

4 =

5 =

6 = START at 27T/29T speed (speed reference/frequency reference)

7 = START at 167TEE/161TEE speed

8 = START at 168TEE/162TEE speed

9 = RESET

Note!  This control resets the STATUS_CMD 13T.

10 = Bypass of the speed integrator.

The speed reference is transferred direct to the integrator output 	ROWSPEEDREF2 295T and to the rounding function output SPEEDREF2 233T.

11 =

12 =

13 =

14 =

15 =

6.	REFERENCE VALUES

Frequency reference value, FREQREF 29T

-	Scaling: 0.01 Hz (5000 = 50 Hz)

-	1392 - pin address of a functional block program

Fixed frequency reference value, FREQ1 161TEE

-	Scaling: 0.01 Hz (5000 = 50 Hz)

Fixed frequency reference value, FREQ2 162TEE

-	Scaling: 0.01 Hz (5000 = 50 Hz)

Torque reference value, TORQREF 26T

-	Scaling: 1000 = rated active current (IRE) in the constant flux range.

Speed reference value, SPEEDREF 27T

-	Scaling: 20000 = DRIVESPEEDMAX

Fixed speed reference value, SPEED1 167TEE

-	Scaling: 20000 = DRIVESPEEDMAX

Fixed speed reference value, SPEED2 168TEE

-	Scaling: 20000 = DRIVESPEEDMAX

7.	ACTUAL VALUES

Filtered actual value of the output current active component, IRE_FILT 201T

-	Scaling: 0.1 % (1000 corresponds to the rated value of the inverter's active 	component when COSFIIFACTOR 76TEE is set.)

-	Positive value corresponds to the motor mode, negative to the generator mode.

Filtered actual value of torque, T_ACT 202T

-	Scaling as for the IRE_FILT.

-	When a frequency is below the frequency of the field weakening point (FWP),

the T_ACT is equal to the IRE_FILT.  At a frequency above the field weakening point,

the T_ACT is equal to the IRE_FILT * FWP / FR_ACT.

Filtered actual value of active power, P_ACT 203T

-	Scaling: 0.1 % (P_ACT = IRE_FILT * U_ACT / 1000 )

Filtered actual value of output voltage, U_ACT 204T

-	Scaling: 0.1 % (1000 corresponds to the rated value of the output voltage.)

Filtered actual value of output current, I_TOTFILT 205T

-	Scaling: 0.1 % (1000 corresponds to the rated current of the inverter.)

Asymmetry of the output currents, CURRENTBALANCE 274T

-	Scaling: 0.1 % (100 = the difference between peak values of two phase 	currents is equal to 10 % of the rated inverter current.)

-	The filtering time constant is approx. 200 ms.

Cosphi, COS_PHI 206T

-	Scaling: (870 = cosphi 0.87)

Filtered actual value of the DC intermediate circuit voltage, UC_ACT 207T

-	Scaling: 0.1 % (1000 corresponds to the Uc voltage rated value = 1.35 * rated

supply voltage.)

Filtered actual value of output frequency, FR_ACT 208T

-	Scaling: 0.01 Hz (5000 = 50 Hz)

Indication of the direction of rotation, DIRECTION 209T

-	0 = the motor rotates at the positive frequency reference in the clockwise 	direction.

<>0= the motor rotates at the negative frequency reference in the counter-	clockwise direction.

Filtered actual value of speed, SPEEDACT2 236T

-	Scaling: 20000 = DRIVESPEEDMAX

Inverter fault word FAULTWORD0 210TM

-	Faults detected by the inverter's hardware.

See communication table.

Inverter fault word FAUTLWORD1 211TM

-	Faults detected by the software.

See communication table.

Inverter fault word FAULTWORD2 212TM

-	Diagnostics data reported by the software.

See communication table.

Inverter status data SAMISTATUS 214T

-	See communication table.

Status of the controllers of inverter, SCSTATUS 215T

-	Status Word which provides status data of the controllers.

See communication table.

Figure 7.1.	Actual values (57779400).

8.	FREQUENCY REFERENCE VALUE INTEGRATOR

The acceleration and deceleration rate of the inverter frequency reference value integrator

can be separately set by the parameters FREQINTACC 64TEE and FREQINTDEC 66TEE.

The output of the integrator is limited by the parameters FREQMAX 62TEE and FREQMIN

63TEE.  During a braking without a braking chopper or the line generating unit (LGU), the

power handling capacity of the frequency converter is limited to internal losses (approx. 2 %).

The Uc voltage rises as a result of too short a downward integration time. An overvoltage is

eliminated by the separate Uc control but the real stop speed does not correspond any

longer to the preset deceleration time.

The operation of the frequency reference value integrator is normally softened at the bend

points by means of a so-called S curve. If the integration time required by the drive is short

(<3 s), the softening function begins to increase the integration times significantly.  In that

case the S curve can be eliminated by setting the INTEGMODESEL 91TEE parameter to zero.

8.1	Variable slope function in frequency reference integrator

When the function is activated, the program calculates the integration time using the external computer program execution time TMS 462TEE and the amount of the change of the reference.

Always when the frequency reference is updated, the change of reference is

calculated from the previous updating.

The updating interval is the same as the external computer program execution time TMS 462TEE. Using these information the necessary integration speed is calculated

on 21 ms execution level.

With parameter RATETD 461TEE it is possible to determine the time which has to elapse from the start before the VARIABLE SLOPE activates. During the start period the normal integration parameters FREQINTACC 64TEE and FREQINTDEC 66TEE are used

VARIABLE SLOPE function is not used when STOP command is activated.

8.2	Parameters

Upward integration rate FREQINTACC 64TEE

-	Scaling: from 0 to +100 Hz with 0.1 s step (200 = 20 s)

Downward integration rate FREQINTDEC 66TEE

-	Scaling: from +100 Hz to 0 with 0.1 s step

High limit of the frequency reference value, FREQMAX 62TEE

-	Scaling: 0.01 Hz (6000 = 60 Hz)

Low limit of the frequency reference value, FREQMIN 63TEE

-	Scaling: 0.01 Hz (-6000 = -60 Hz)

Activation of variable slope function, VARSLS 460TEE

-	0 = not activated

-	1 = activated

Time period from the start to the activation, RATETD 461TEE

-	Scaling: 1 = 1s

The updating interval of frequency reference in upper control, TMS 462TEE

-	Scaling: 100 = 100 ms

Figure 8.1.	Block diagram of the frequency reference value integrator. (5777795-8)

9.	FORMATION OF THE OUTPUT VOLTAGE

The output voltage of the inverter is kept in a linear U/f function in the constant flux range.

The function is determined by two parameters: FIELDWEAKPNT 68TEE and

MAXOUTPUTVOLTAGE 67TEE.  A field weakening point frequency is set by means of the

FIELDWEAKPNT 68TEE and a voltage level above the field weakening point frequency by

means of the MAXOUTPUTVOLTAGE 67TEE. The final voltage reference value UREF 230T

is also affected by IR compensation UFIR 287T, running start FLSTARTUREF 288T, Uc

voltage effect UCEMF 282T, flux stabilization UREFSTAB 387T, and external voltage

reference UREFSTEP 218T.  (See block diagram in figure 9.1).

The field weakening point can be set in the range 20...200 Hz.

The maximum voltage can be set in the range 0...120 %.  If 100 % voltage is selected for

the voltage value, the output voltage remains at the rated value also in the field weakening

range even though there might be an overvoltage in the supply line.

9.1	Parameters

Field weakening point FIELDWEAKPNT 68TEE

-	Scaling: 0.01 Hz (5000 = 50 Hz)

Maximum voltage MAXOUTPUTVOLTAGE 67TEE

-	Scaling: (100 = rated voltage)

Figure 9.1.	Formation of the output voltage.  (5777796-6).

10.	UC OVERVOLTAGE CONTROL

A Uc overvoltage control circuit prevents an overvoltage from occurring in the intermediate circuit during motor braking.

10.1	Control operation

The control circuit comprises two P controllers. The reference values for the controllers are determined by the parameters UCHIGH 354TEE (119 %) and UCHIGHREF 355TEE

(116 %).  A filtered Uc value UCAVG 227T is used as the actual value.  When the Uc

voltage has overshot the 116 % level, the lower P control is activated and it seeks to control

the Uc value to the level below the limit by increasing the frequency.

If Uc, nevertheless, rises above the 119 % limit, the high controller is activated and

considerably raises the frequency until the Uc falls below the 119 % limit.  During the high

controller operation the gain factor of the lower controller is set to zero.  This is done in

order to avoid fluctuations of the Uc voltage.  When the Uc voltage drops below the 116 %

limit, the gain factor of the lower controller begins to increase at the rate determined by the

parameter KP_INCREMENT 358TEE towards the basic value.

(See block diagram in figure 10.1.)

10.2	Uc-control parameters

Activation level of the high Uc-limiting controller, UCHIGH 354TEE

-	Scaling: 1000 = rated Uc (1.35 * rated supply voltage)

Activation level of the low Uc-limiting controller, UCHIGHREF 355TEE

-	Scaling: 1000 = rated Uc

Figure 10.1.	Uc overvoltage control circuit diagram.  (5777797-4).

11.	TORQUE LIMIT CONTROL

The torque limit control circuit prevents the motor from running on too high a slip value.

It also limits the phase currents and prevents them from increasing to an excessively high

value for the inverter operation. The principle of control is based on limitation of the active

current component (IRE). The torque developed by the motor in the constant flux range is

proportional to the active component of the current.  For this reason the active current

component limit is also called a torque limit.

Two controllers are installed in the unit, one on the motor side and the other on the generator

side.  The control circuits are limit controllers of the PI type.  When the active current

component IRE 223T rises to the preset limit, the limit controller is activated. The output

frequency decreases on the motor side and increases on the generator side. The control

parameters are common to both controllers; the proportional gain is KP_IRE 351TEE and

the integral action parameter TI_IRE 352TEE.

Owing to the method of computation a high-frequency alternating component occurs in the

IRE signal and the controller seeks to follow the peaks of that component.  For this purpose

we require the functional block which corrects the controller reference value IREMAX 79TEE

so that the alternating component is compensated. The parameter IREMAX1 483T is the

output of the functional block. When the limit control is off, the output of the functional block

is 80 % of the preset current limit (79TEE).  When the control is turned on, the functional

block changes its output (control reference value) so that the filtered IRE value IREFILT

201T does not exceed the maximum limit. (See block diagram in figure 11.1.)

On the generator side, the value of IRE at low frequencies has to be corrected for current

limiting control because the IRE shows too small a torque.  The error is caused by the

increase in the proportion of the stator resistance as the frequency decreases.  When the

frequency on a standard motor is below 5 Hz, the error is so large that the IRE value

cannot any longer be used as a reliable means to determine the torque.

The value of IRE for current limiting control on the generator side is corrected by means of

the parameter STATORRESISTANCE 353TEE. The corrected value is IREC 479TEE.

The basic formula for correction (1) is

(1)

where

U	=	supply voltage

IRE	=	active motor current

I	=	total motor current

E	=	voltage of the motor

R	=	stator resistance of the motor

The factory setting of the stator resistance need not normally be changed.  The scaling is

in internal units of the program and the normal value range is between 1000 and 2500.  As

the value increases also the correction increases, see formula (1).

On the motor side, the value of IRE is not corrected.  If the torque maximization is used,

however, the reference of IREMAX control (normally 79TEE) is increased linearly towards

the zero frequency in the torque maximizing range.  At zero frequency, the reference is

approx. 200 % of the rated inverter current.  This guarantees that IRE control is off in the

torque maximizing range and that current limiting control is effected through a peak current

measurement.  Also the control mode is similarly smoothly changed from peak current

control to IRE control.

11.1	Torque limit control parameters

Torque limit of the motor side, IREMAX 79TEE

-	 Scaling: 0.1 % of the inverter rated active component,

cosphi = 0.87 (1000 = rated value)

Torque limit of the generator side, IREMIN 80TEE

-	 Scaling: 0.1 % of the inverter rated active component,

cosphi = -0.87 (-1000 = rated value)

Stator resistance STATORRESISTANCE 353TEE

- 	Scaling: range between 1000 and 2500

Figure 11.1.	Torque limiting control block diagram.  (5777798-2)

12.	STABILIZERS

The control circuit comprises three stabilizers by means of which current fluctuations in low-load conditions and Uc fluctuation in fast transient states are damped.

(See block diagram in figure 12.1.)

12.1	Torque stabilization

Current fluctuation is damped by means of the torque stabilization. The stabilization utilizes

the derivation principle and affects the frequency reference value. The stabilization effect can

be determined separately for each modulation waveform by means of the parameters

IRESTAB-GAIN_VP1...VP11 359TEE...364TEE. The time constant of the stabilization is

determined by the parameter IRESTABFACTOR 365TEE, which is common to all

modulation waveforms.

Parameters

Torque stabilization gain IRESTABGAIN_VP1 359TEE

-	Frequency range approx. 60...200 Hz

Torque stabilization gain IRESTABGAIN_VP3 360

-	Frequency range approx. 36...60 Hz

Torque stabilization gain IRESTABGAIN_VP5 361TEE

-	Frequency range approx. 25...36 Hz

Torque stabilization gain IRESTABGAIN_VP7 362TEE

-	Frequency range approx. 20...25 Hz

Torque stabilization gain IRESTABGAIN_VP9 363TEE

-	Frequency range approx. 10...20 Hz

Torque stabilization gain IRESTABGAIN_VP11 364TEE

-	Frequency range approx. 0...10 Hz

Torque stabilization time constant IRESTABFACTOR 365TEE

-	Common to all modulation waveforms.

12.2	Uc stabilization

Fluctuation of the intermediate circuit voltage is suppressed by means of the Uc

stabilization.  The stabilization utilizes the derivation principle and affects the frequency

reference value.  A stabilization gain can be determined by the parameter

UCSTABGAIN 370TEE and the time constant of the stabilization is determined by the

parameter UCSTABFACTOR 371TEE.

Uc stabilization parameters

Uc stabilization gain UCSTABGAIN 370TEE

Uc stabilization time constant UCSTABFACTOR 371TEE

12.3	Flux stabilization

During a drive operation with a low load in the frequency range 0...20 Hz, current fluctuates

significantly.  This effect is suppressed by means of the flux stabilization.  The stabilization

utilizes the derivation principle and affects the voltage reference value.  The stabilization

effect is determined by means of the parameter FLUXSTABGAIN 367TEE and the time

constant by the parameter FLUXSTABFACTOR 368TEE. The frequency range is 0...20 Hz.

Flux stabilization parameters

Flux stabilization gain FLUXSTABGAIN 367TEE

Flux stabilization time constant FLUXSTABFACTOR 368TEE

Figure 12.1.	Diagram of stabilization blocks.  (5777799-1)

13.	IR COMPENSATION (TORQUE MAXIMIZATION)

At the low frequencies (0...10 Hz) a significant voltage drop is produced by the stator

resistance of the motor.  The drop is compensated by boosting the output voltage of the

inverter so that the proper magnetization is achieved. The IR compensation is required

when load torque is present beginning from the zero frequency (release torque).

The IR compensation functional block comprises four functions:

-	developing a motor flux,

-	calculation of additional voltage,

-	peak current limiting control,

-	automatic search of maximum compensation.

(See block diagram in figure 13.1.)

13.1	Developing a motor flux

A motor flux has to be developed before a motor can be rotated.  Flux is developed by

means of the PI controller, which is turned on after receiving the START command for the

time determined by the parameter FLUXTIME 414TEE (in normal conditions 3 s).  The PI

controller regulates the total current of the inverter I_TOT 224T with the reference value

defined by the parameter IRCOMPCURRENT 70TEE. After the developing of the flux, the

program stores a voltage reference value used by the controller to the measuring point

IRLEVEL 410T. This value is used by the IR compensation circuit as the voltage reference

at the zero frequency.  The IR compensation gain is therefore selected by means of the

parameter 70TEE.

Tuning of IRCOMPCURRENT 70TEE:

-	Start the drive without load and increase the speed to a frequency that

corresponds to 2/3 of the motor Fn.

-	Read the content of parameter I_TOTFILT 205T and after that set the read

value to parameter IRCOMPCURRENT 70TEE. Normally the value of 70TEE will

be around 150...300.

13.2	Calculation of additional voltage

An additional voltage provided by the IR compensation is produced at the zero frequency on

the basis of the measuring point 410T content. As the frequency increases the additional

voltage is linearly reduced and eliminated at the frequency defined by the parameter

IRCOMPPOINT 69TEE.

An additional voltage is not produced if the drive is in the generator mode.  This is

indicated by the ratio between the active current IDFILT 481T and the reactive current

IQFILT 482T.  When IDFILT > IQFILT, an additional voltage is produced and when IDFILT

< IQFILT/2, an additional voltage is not produced.

The IDFILT...IDFILT/2 is used as a hysteresis of the selection logic. When the frequency

on the generator side drops below the value defined by the parameter GEN_IRCOMPPOINT

406TEE, the additional voltage begins to rise linearly towards the 410T zero frequency

value. This function is particularly important when changing the direction of rotation.

When the drive changes from the generator mode to the motor mode or vice versa, the

rate of rise of the voltage is limited by the parameter IRFLUXSPEED 408TEE.

13.3	Peak current limiting control

When the IR compensation operates at a frequency below the limit defined by the

parameter IRCOMPLIMIT 407TEE (5 Hz), the current limiting control is based on the peak

current measurement. A P-type controller is controlling peakcurrent IPEAK_AD 418T

using parameter IPEAKLIMIT 419TEE as a reference value. Output of the controller

TORQMAXCONTOUT 382T effects on parameter FREQREF2 226T. At frequencies above

5 Hz, the current limiting operates normally on the basis of the IRE.

Setting parameter 419TEE:

-	The initial value 140 is normally suitable.

-	Value of parameter 419TEE can reduce in proportion to currents if the nominal

current of motor is small compare to inverter's nominal current.

13.4	Automatic search of maximum compensation

When the IR compensation requirement of the drive significantly varies, the start-up can be facilitated by switching on the automatic search function.  This is done by setting IRCOMPSEL 85TEE to 3 and LEARNMODE 405TEE to 1. The automatic search circuit in

creases the additional voltage if the drive reaches the peak current limit. The increase of

voltage decreases the frequency reference value by means of the peak current controller

until the drive starts to operate.  If the drive is not able to start, the increase of voltage is

terminated at the slip frequency.

The program stores the value of the additional voltage used by the automatic search circuit to the measuring point AUTOTORQMAX 409T(EE).  This value can be used in a subsequent start-up instead of the automatic search by setting the 405TEE to zero after the first start-up (motor running).

13.5	IR-compensation by using constant voltage addition

IR compensation is given directly as a voltage addition when IRCOMPSEL 85TEE = 1 and IRCOMPVOLTAGE 420TEE <> 0. As the frequency increases, the additional voltage

reduces linearly and is eliminated at the frequency defined by the parameter

IRCOMPPOINT 69TEE.

This mode of IR compensation is used when one SAMI is feeding several motors

that can be switched ON and OFF.

IR compensation for SAMI STAR TF is activated by setting P85 = 9. The program prevents

the additional voltage at 0 Hz. The additional voltage is determined by parameters

IRCOMPVOLTAGE 420TEE and EMFKERROIN 421T. This mode can be used when

SAMI is feeding step up transformer.

13.6	IR compensation parameters

IR compensation selection IRCOMPSEL 85TEE

-	 0 = no IR compensation

- 	1 = IR compensation without automatic search

- 	3 = IR compensation with automatic search

- 	9 = IR compensation with SAMI TF (Step-up transformer) mode

IR compensation operating range IRCOMPPOINT 69TEE

- 	Scaling: 0.01 Hz (3000 = 30 Hz)

IR compensation starting current IRCOMPCURRENT 70TEE

- 	Scaling: 0.1 % of the rated current  (300 = 30 % of the

rated inverter current).

Duration of IR compensation after start-up, TORQMAXTIME 72TEE

- 	0  = IR compensation is on continuously

- 	>0 = IR compensation terminates after a specified number of seconds

from the start-up.

IR compensation with constant voltage addition, IRCOMPVOLTAGE 420TEE

-	 0 = no voltage addition

- 	> 0  voltage addition activated

- 	Scaling: 16125 = 100 %

Figure 13.1.	IR compensation block diagram.  (5777800-8)

14.	DC BRAKING

After STOP command, when DC braking is activated, the motor will be supplied with a

current determined by parameter DCBRAKECURRENT 345TEE on a frequency 0.2 Hz.

The braking capacity of DC braking is about the same as with the braking by using SAMIs

internal losses (UC-overvoltage activated).

DC braking will give a stabile stopping.

The operation of program during the braking:

-	The modulator triggering pulses are taken off for a period

RESTARTDELAY 75TEE.

-	SAMI is started on a frequency 0.2 Hz.

-	Motor will be supplied with a total current which is determined by a

ramp and controller. The reference value is DCBRAKECURRENT 345TEE

and the actual value I_TOT 224T.

-	Motor will be supplied with a current during a time which is determined by

a parameter DCBRAKETIME 346TEE. When time has elapsed SAMI will be

stopped. Time can be changed during the braking.

-	Supplying of the current will be stopped by a fault tripping or if 	SAMI receives

a COAST STOP command.

It is possible to make a application program that determines the braking time as a function

of rotation speed. This will avoid unnecessary supplying of current.

14.1	Parameters of DC braking

Selection of DC braking, DCBRAKESEL 96TEE

-	0 = no DC braking

-	1 = DC braking selected

Current in DC braking, DCBRAKECURRENT 345TEE

-	Scaling: 1000 = rated current of inverter

DC braking period, DCBRAKETIME 346TEE

-	Scaling: 1 = 1s

15.	STALL PROTECTION

The stall protection stops the inverter when the motor is in apparent danger of overheating.

The rotor is either mechanically stalled or the load is otherwise continuously too high.

The stall protection is activated if the inverter's total current exceeds the rated value and/or

the torque limit control is turned on at least for the time defined by the parameter

STALLTIME 83TEE and assuming that the output frequency is below the limit set by the

parameter STALLFREQ 82TEE.

When the inverter stops, the message "MOTOR STALLED" is displayed on control panel

CP2 and the fault code "FL 20" is displayed on control panel CP1.

15.1	Stall protection parameters

Selection of stall protection, STALLPROTECTSEL 86TEE

-	0 = no stall protection

-	1 = stall protection selected

Stall protection activation range STALLFREQ 82TEE

-	Scaling: 0.01 Hz step (1000 = 10 Hz)

Stall protection activation time STALLTIME 83TEE

-	Scaling: 1 s (10 = 10 s)

16.	SLIP COMPENSATION

The slip compensation function corrects a load effect on the motor speed in steady-state

conditions.  A correction proportional to the actual torque (IRE_FILT 201T) and scaled by

the parameter FSLIPSCALE 84TEE is made to the supply frequency of the motor.  The

measuring point FSLIP 229T gives the magnitude of correction.  The slip compensation

does not operate at frequencies below 10 Hz.

16.1	Slip compensation parameters

Selection of slip compensation, SLIPCOMPSEL 89TEE

-	0 = no compensation

-	1 = compensation selected

Slip compensation scaling FSLIPSCALE 84TEE

-	compensation calculation formula:

17.	RUNNING START

When using the running start function, the inverter searches for the frequency

corresponding to the shaft speed of the rotating motor and is synchronized to it.  A search

can also be made when shaft rotates in the direction opposite to the frequency reference.

The search frequencies of the running start are defined in accordance with the parameters

FLYINGFREQMAX 60TEE (positive  frequency reference) and FLYINGFREQMIN 61TEE

(negative frequency reference). A search is not performed in the direction in question if the

absolute value of the parameter is below 3 Hz. The values of parameters 60TEE and

61TEE are limited in the program so that the preset drive maximum speed of rotation

(FREQMAX 62TEE, FREQMIN 63TEE) is not exceeded.

17.1	Running start operation

When the inverter is started, the output frequency is quickly raised to the value defined by

the parameter FLYINGFREQMAX 60TEE or FLYINGFREQMIN 61TEE, depending on the

sign of the frequency reference value FREQREF1 225T.  The  voltage reference is raised

to the value defined by the parameter FLSTARTVOLTAGE 472TEE (typically 15 %). There

after the frequency is brought down at the rate defined by the parameter FLYINGGAIN

474TEE until the shaft frequency is found.  The shaft frequency search is made by testing

the torque actual value (IRE_FILT 201T).  When IRE goes to a value which is below the

value of parameter FLYINGIRELIMIT 475TEE or when it reaches the minimum value

(IRETHRESHOLD 468TEE), the shaft frequency is found.  Finally, the voltage reference is

brought up at the rate defined by the parameter FLYINGFLUXSPEED 470TEE to a value

of the U/f-characteristic that corresponds to the frequency.  The maximum total start-up

time in one direction is about 8 s.

A search in the direction opposite to the frequency reference is started if the shaft

frequency has not been found in the direction corresponding to the frequency reference

and the search frequency has dropped below the value defined by the parameter

FLYINGFREQLIMIT 473TEE (3 Hz).  If the frequency cannot be found in either

direction, the start-up procedure begins at 0 Hz.  (See block diagram in figure 17.1.)

In certain cases, when a running start is to be made at a relatively low speed (5 to 15 Hz),

it may happen that, depending on the motor, the voltage drops to such a low value that the

program cannot find the synchronous frequency.  In that case, additional voltage can be

given to the drive at the zero frequency using parameter ZEROVOLTAGE 469TEE.

Note, however, that too much additional voltage will inevitably lead to an overcurrent trip.  The initialization value of the parameter is 15.

17.2	Running start parameters

Selection of running start, FLYINGSTARTSEL 87TEE

-	0 = no running start

-	1 = running start selected

Positive search frequency FLYINGFREQMAX 60TEE

-	Scaling 0.01 Hz (6000 = 60 Hz)

Negative search frequency FLYINGFREQMIN 61TEE

-	Scaling 0.01 Hz  (-6000 = -60 Hz)

Running start voltage reference FLSTARTVOLTAGE 472TEE

-	Scaling in per cent of the rated value (15 = 15 %)

Running start voltage reference at the zero frequency ZEROVOLTAGE 469TEE

-	Scaling 0.1 % of the rated value (10 = 1 %)

Figure 17.1.	Running start.  (5777801-6)

18.	POWER LOSS CONTROL

The power loss control circuit holds the inverter in operating condition during short (approx.

0.5 s) power failures.  The energy required for operation is then taken from the kinetic

energy available on the drive shaft.  If a power failure lasts longer than one second, the

main contactor control logic will not be able to close the contactor any more even if the

kinetic energy is sufficient.  In that case a backed-up auxiliary voltage should be used for

the relay block.

Loss of the supply voltage is indicated in the inverter by a drop in the intermediate circuit

voltage and by the loss of the auxiliary voltage in the relay block.  This in turn causes the

main contactor to open.  The intermediate circuit voltage drops typically 15 % below the

rated value in one millisecond.  The supply frequency of the motor is brought down at a

rate at which a proper power output is obtained from the motor to keep the intermediate

circuit voltage at its reference value.  The effect of the moment of inertia J on the drive

shaft is set by means of the parameter J_GAIN 81TEE.

18.1	Control operation

When the voltage drops below the limit defined by the parameter PWDN_UCALARM

433TEE, the control is activated.  A decrement proportional to the actual torque IRE_FILT

and defined by the parameter PWDNSLIPGAIN 423TEE is given to the frequency value.

After execution of the decrement, the frequency is integrated downward at a rate defined

by the parameter J_GAIN 81TEE. Control of the intermediate circuit voltage is of the PD

type.  The power loss control is always eliminated after a time defined by the parameter

PWDNTIME 430TEE.  (See block diagram in figure 18.1.)

18.2	Power loss control parameters

Selection of control, NETFAILSEL 88TEE

-	0 = no power loss control

-	1 = power loss control selected

Gain of the drive's moment of inertia, J_GAIN 81TEE

-	A typical value is 300.  If the moment of inertia is especially high, the value

should be reduced.

Figure 18.1.	Power loss control.  (5777802-4)

19.	SPEED MEASUREMENT

The drive's rotational speed is measured by means of a pulse tachometer mounted on the

rotor shaft.  The tachometer supplies two pulse trains, which are used for calculation of the

rotor speed.  The direction of rotation is identified on the basis of the 90 degree phase shift

between the two pulse trains.

The maximum rotational speed of the drive DRIVESPEEDMAX 155TEE is used to scale

the highest rpm speed to correspond to the value 20000.

The SPEEDACT 235T measuring point gives the actual speed.  The numeric range of the

measuring point is -20000 to +20000.  The SPEEDACT2 236T measuring point gives the

filtered actual speed. The filter time constant is determined by means of the data

communications parameters.  The parameter number 236 can be set to any transmission

index and after that the time constant used will be the time interval of the appropriate

transmission index so that 1 = 21 ms, 2 = 42 ms, etc.  If the 236T parameter is not defined

for data communications transmission, the time constant is approx. 200 ms.

The number of tacho pulses per motor revolution is set to the parameter

TACHOPULSENMBR 156TEE.

The pole pair number of the motor is set to the parameter POLEPAIRS 154TEE.

Tacho pulses can be supervised by means of two parameters.  The maximum difference

allowed during running between two consecutive speed measurements can be set to the

memory location TACHORIPPLE 78TEE.  The scaling of 78TEE is the same as for speed

measurement.  Parameter TACHDELAY 174TEE can be used to set the maximum

allowed delay for the tacho pulses generated after start command in multiples of 21 ms.

If a tachometer is used in which the phase shift changes from the 90 degrees as the speed

increases (e.g. a magnetic tachometer), then the parameter TACHOPHASEDISABLE

159TEE must be used to set a speed above which the identification of the direction of

rotation is terminated.

19.1	Speed measurement parameters

Measuring points

Counter of negative tachometer pulses, NEGNTAKO 311T

Counter of positive tachometer pulses, POSNTAKO 312T

Actual speed SPEEDACT 235T

-	20000 corresponds to DRIVESPEEDMAX 155TEE

-	0...+20000

Filtered actual speed SPEEDACT2 236T

-	20000 corresponds to DRIVESPEEDMAX 155TEE

-	0...+20000

Actual speed in hertz, FACT 239T

-	5000 = 50.00 Hz

-	Shaft frequency * POLEPAIRS

Setting parameters

Selection of speed measurement, SPEEDMEASSEL 94TEE

-	0 = no speed measurement

-	1 = speed measurement selected

Maximum shaft speed DRIVESPEEDMAX 155TEE

-	revolutions per minute, rpm

Number of tachometer pulses per motor revolution, TACHOPULSENMBR 156TEE

-	pulses/revolution

Pole pair number of the motor, POLEPAIRS 154TEE

Speed limit above which identification of the direction of rotation is disabled,

TACHOPHASEDISABLE 159TEE

-	0...20000

Tachometer type TACHOTYPE 160TEE

**** NOT AVAILABLE AS STANDARD ****

-	0 = 2-channel tachometer.  A 90 degree phase shift between the

channels.

-	1 = 1-channel tachometer

Maximum permissible difference between two consecutive speed measurements,

TACHORIPPLE 78TEE

-	0 = not in use, the difference value 1...20000

Time interval between tachometer pulses during running, TACHDELAY 174TEE

-	0 = no supervision, 1 = 21 ms, 2 = 42 ms, etc.

Figure 19.1.	Speed measurement.  (5811293-3)

20.	SPEED CONTROL

The scalar control speed controller uses a tachometer signal to eliminate the error caused

in the shaft speed by the slip of the cage induction motor. The slip is dependent on the

load of the motor.  The normal speed control operating range is from 5 Hz to

DRIVESPEEDMAX.

At frequencies below 5 Hz, speed control operates but its control characteristics are slow.

The speed control program includes the following functions:

-	Setting the speed reference

-	Speed reference integrator

-	Rounding function of the speed integrator

-	Acceleration compensation

-	PI control

-	Drooping

When the speed control option is selected, it always activates the setting of the speed

reference and the speed integrator. The control parameter CONTROLSEL 71T can be

used to switch control on and off at any time.

Figure 20.1.	Speed control block diagram.  (5811294-1)

20.1	Setting the speed reference

The speed reference value can be set as required by the User at three addresses.  The

speed reference can be sent direct to the communication table location SPEEDREF 27T.  The drive speed accelerates to speed 27T when the start command is given to the address

START 2T.  The +/- pushbuttons of the control panel CP2 have an effect on the reference

27T through the address DELTASPEEDREF 30T when 71TEE is 1. When the +/-

pushbuttons are pressed the CP2 transmits a speed change reference which is added

to the reference 27T.

The communication table contains two memory locations for presettable speed references

SPEED1 167TEE and SPEED2 168TEE.  These parameters give the reference value

when the given start command is START1_P 24T or START2_P 25T respectively.

When a value other than zero is sent to the memory location STOP 3T, the speed

reference is set to zero and the drive is stopped by means of a speed integrator. A

communication fault can be set to do the same.

The selection logic selects one of the four above-mentioned speed reference values and

sets it to the measuring point SPEEDREF1 232T. The value is limited by SPEEDMAX

51TEE in the positive direction and by SPEEDMIN 52TEE in the negative direction.

After the limiter, the reference signal passes through the speed integrator and the output

obtained is ROWSPEEDREF2 295T.  The integrator acceleration and deceleration times

are set using parameters SPEEDINTACC 53TEE and SPEEDINTDEC 54TEE.

20.2	Rounding function of the speed integrator

Changes occurring in the speed integrator output ROWSPEEDREF2 295T at the beginning and end of integration can be "softened" by a low-pass filter.  The effect of the filter is adjusted by means of the parameter SPEEDSOFTENTIME 58TEE.  The output obtained is the SPEEDREF2 233T which is the speed controller reference.  Parameter 58TEE gives the duration of the rounding function in units of 0.1 s.

20.3	Integrator control in running start

In running start, the measured actual speed SPEEDACT 235T is set to the speed

integrator output ROWSPEEDREF2 295T and the measuring point SPEEDREF2 233T.

Integration after start-up towards the reference value then begins at the actual shaft speed

of the start-up moment.

20.4	Acceleration compensation

Acceleration compensation may sometimes be necessary during the acceleration stage.

The magnitude of acceleration compensation is determined by means of the parameter

KPSD TIME 59TEE.  The parameter 59TEE gives the time (in seconds) which the process

requires to accelerate from 0 speed to 20000 (DRIVESPEEDMAX) speed with a torque

requirement equal to the 0.5 Hz slip on the motor. The time is determined by accelerating

the drive when it is under speed control and observing the speed controller output

FSLIPREF 240T. The magnitude of compensation is correct when, during acceleration, the

speed controller output remains approximately at the same level as it would be when

running at a constant speed.

The measuring point ACC_COMP 297T gives the magnitude of compensation in units of

0.01 Hz.  The compensation is calculated only when the drive is speed controlled.

Figure 20.2.	Speed reference setting.  (5811295-0)

20.5	PI control

The value SPEEDREF2 233T is used as the speed control reference and the SPEEDACT

235T is the actual speed. The difference between these two speed values can be filtered

by means of two consecutive low-pass filters, the filter time constants of which (in

milliseconds) are FRS 55TEE and FRS1 74TEE.  The filters are bypassed by setting the

time constants to zero.

The proportional gain KPS 57TEE and the integral action parameter TIS 56TEE are the

speed control parameters.  The controller output produced is a frequency reference which

is equal to the motor slip. The output is limited by the positive limit SPEEDSLIPMAX 300TEE

and the negative limit SPEEDSLIPMIN 301TEE.  Since these parameters limit the motor slip,

they also function as current limits.  The initialization value for the parameters is 1.5 Hz.

If the motor slip exceeds this value the limits must be adjusted equal to the motor slip,

otherwise the drive will not give full torque.

The set limits are used in the constant flux range. In the field weakening range, the set

limits are increased according to the 1/f characteristic.

The control parameters can be adjusted to some extent to various operating conditions

using parameters KPSMIN 152TEE and KPSWEAKPNT 153TEE.  KPSMIN is the

proportional gain of the controller when the controller output is zero.  As the controller

output increases, the proportional gain changes linearly towards the gain KPS 57TEE.

When the controller output exceeds the value of parameter KPSWEAKPNT 153TEE,

the proportional gain is determined by parameter KPS 57TEE only.

Scaling of the controller:

When KPS = 100 and the reference value changes from 0 to 20000, the output changes

from 0 to 50 (0.5 Hz).

TIS = integral action time in milliseconds 1000 = 1 s.

Figure 20.3.	PI control.  (5811296-8)

20.6	Drooping

When certain amount of speed decrease caused by the load is to be accepted, a drooping can be set using parameter KPSP 50TEE.  The measuring point DROOPING 296T gives

the magnitude of drooping in a unit of speed.

Scaling of KPSP:

The decrease of speed in units of 0.1 % when the drive operates under maximum load.

20.7	Speed control parameters

Selection of the speed control option, SPEEDCONTSEL 92TEE

-	0 = no speed control

-	1 = speed control selected

Selection of control mode, CONTROLSEL 71T

-	0 = frequency control

-	1 = speed control

-	2 = torque control

Filters FRS 55TEE and FRS1 74TEE

-	Scaling: millisecond

Control output limits SPEEDSLIPMAX 300TEE and SPEEDSLIPMIN 301TEE

-	Scaling: 150 = 1.5 Hz

Proportional gain for speed control KPS 57TEE

-	Scaling: % (when KPS is 100 and the difference value changes from

0 to 20000, the output changes from 0 to 50)

Integral action time for speed control TIS 56TEE

-	Scaling: millisecond

Reference values

Direct external speed reference SPEEDREF 27T

-	0...+20000, 20000 = speed DRIVESPEEDMAX 155TEE

Fixed speed reference 1, SPEED1 167TEE

-	0...+20000

Fixed speed reference 2, SPEED2 168TEE

-	0...+20000

Change in the speed reference, DELTASPEEDREF 30T

-	-1000...+1000

Measuring points

Speed reference after the selection logic, SPEEDREF1 232T

-	0...+20000

Speed reference after the integrator, ROWSPEEDREF2 295T

-	0...+20000

Speed reference to the speed controller, SPEEDREF2 233T

-	0...+20000

Speed controller output FSLIPREF 240T

-	Scaling: 50 = 0.5 Hz

Frequency reference produced by the speed controller, FREQREF3 234T

-	Scaling: 5000 = 50 Hz

21.	TORQUE CONTROL

The torque controller of scalar control is a PI controller.  By varying the frequency the

controller tries to keep the value of the active current IRE at the set point determined by the

parameter TORQREF 26T.

Torque control is automatically switched off when the supply frequency decreases below

5 Hz.The program then sets value 0 to the parameter 71T and the control mode is changed

to frequency control.

Above the field weakening point, the IRE reference is increased according to the 1/f

characteristic.  Then, as the frequency increases, the value of IRE increases but the torque

T_ACT 202T follows the reference TORQREF 26T.

When a STOP command is given in torque control, the drive shifts to frequency control and

stops by means of a frequency ramp.

21.1	Torque control parameters

Selection of the torque control option, TORQCONTSEL 90TEE

-	0 = no torque control

-	1 = torque control selected

Selection of control mode, CONTROLSEL 71T

-	0 = frequency-controlled inverter

-	1 = speed-controlled inverter

-	2 = torque-controlled inverter

Torque control reference TORQREF 26T

-	Scaling: scaling of IRE

Actual torque T_ACT 202T

-	Scaling: scaling of IRE

22.	CHANGE OF THE CONTROL MODE

The scalar control program includes three control mode options: frequency, speed or

torque control.  Selection of speed and torque control requires that the appropriate option

be activated at the factory and the selection flag be set.

Change of the control mode is made by means of the parameter CONTROLSEL 71T:

71T = 0	frequency control

71T = 1	speed control

71T = 2	torque control

A change from one control mode to another can be made whenever required. At

frequencies below 5 Hz and when a STOP command is given, torque control is

automatically changed to frequency control.

23.	DROOPING BASED ON IRE

Parameter FREQDROOPING 73TEE is used to determine the decrease in frequency

reference caused by the load.

The magnitude of a frequency droop is the product of IRE and parameter

FREQDROOPING calculated from the following formula:

The sign is determined by the direction of rotation so that when IRE is a positive value the

output always has a decreasing effect on the absolute value of the frequency.

So with a positive direction of rotation the magnitude of drooping is -0.5 Hz when IRE is

1000 and FREQDROOPING is 1000.

Parameter FREQDROOPING 73TEE should only be used with the frequency control mode.

24.	TREND BUFFERS

The inverter software contains 8 sampling buffers with 100 samples capacity.  The buffers

can be used to acquire data showing behaviour of the measuring points.

Selecting the trend buffer option, TRENDBUFSEL 93TEE

-	0 = no trend buffers

-	1 = trend buffers selected

A sampling interval can be selected in a range which corresponds to time interval 4 ms to

262 s/sample.

A triggering condition can be set for the first trend buffer which stores status data to the

memory for a closer analysis.

Trends can be examined in analog form by monitoring a desired trend buffer content using

the D/A converter or watching trend numeric values on the control panel.

Selecting the memory addresses to be monitored

Set the measuring point number to the trend control address that you are going to use.

The trend control addresses are:

191TEE	Trend buffer 1 connecting point

192TEE	Trend buffer 2 connecting point

193TEE	Trend buffer 3 connecting point

194TEE	Trend buffer 4 connecting point

195TEE	Trend buffer 5 connecting point

241TEE	Trend buffer 6 connecting point

242TEE	Trend buffer 7 connecting point

243TEE	Trend buffer 8 connecting point

Selecting a sampling interval

A sampling interval can be selected by means of the parameter TRENDIVAL 196TEE.

196TEE 	= 0  sampling is synchronized to the modulator

= 1  3 ms interval sampling

= 2  6 ms interval sampling

= 3  9 ms interval sampling, etc.

Selecting a triggering condition

A trend triggering occurs every time the inverter detects a fault, irrespective of the

triggering condition. The trend triggering point then lies 80 samples before the fault instant

and 20 samples after it.

Figure 24.1.	Trend triggering caused by a fault.  (57778199)

A triggering condition is set for the first trend buffer by means of the parameter

TRENDTRIG 197TEE.

197TEE 	= -1 triggering caused by a fault only

= <>-1 	triggering occurs when the deviation of two successive samplings

exceeds the value set at this location.

A triggering can also be initiated manually by setting TREND_SAVE 199T parameter value

to <> 0.  The trend values of the triggering instant are then saved. The 199T content is

automatically set to zero.

Figure 24.2.	A conditional or manual triggering.  (57778199)

Monitoring the trend triggering

The content of the TRIGCOUNT 200T measuring point is incremented every time a trend

triggering occurs.  This can be used to control that the triggering condition is satisfied.

Trend content D/A conversion

The 4-channel D/A converter SAFT 154 DAC or the I/O card's own converters can be used

for the trend content D/A conversion.  Each trend buffer has an address which is used by

the D/A converter to convert trend discrete data to the analog form.  The converter should

be scaled to the monitored signal magnitude.

The addresses are:

320T		Trend buffer 1

321T		"       "    	2

322T		"       "    	3

323T		"       "    	4

324T		"       "    	5

325T		"       "    	6

326T		"       "    	7

327T		"       "    	8

The sample conversion interval is 210 ms/sample.  The sampled data contain a

synchronizing pulse which identifies a trend's start instant.

Figure 24.3.	An analog representation of a trend buffer discrete content.  (57778199)

Monitoring the numeric content of the trends on the control panel

The numeric values of the trends can be monitored at the measuring points 500TM to 1299TM as follows:

500TM... 599TM		Trend buffer 1

600TM... 699TM		Trend buffer 2

700TM... 799TM		Trend buffer 3

800TM... 899TM		Trend buffer 4

900TM... 999TM		Trend buffer 5

1000TM...1099TM		Trend buffer 6

1100TM...1199TM		Trend buffer 7

1200TM...1299TM		Trend buffer 8

The measuring points 320T to 327T can also be used on control panel CP1.  The content

of these memory locations provide a general view of the trend development.

25.	D/A CONVERTER

The 4-channel SAFT 154 DAC D/A converter can be connected to the SAFT 187 CON

control card of the inverter to provide D/A conversion of the content of the measuring

points.  Figure 24.1 shows the block diagram of the D/A converter.

Selection of the D/A converter option, DATRANSFSEL 95TEE

-	0 = no D/A converter

-	1 = D/A converter selected

Figure 25.1.	Block diagram of the D/A converter.  The figure shows the

measuring points and parameters of channel 1. (57778202)

Use of the D/A converter

The SAFT 154 DAC card includes four separate D/A conversion channels.  Every channel

has four control adjusting parameters.  The programmable updating interval of one

channel is 6 ms.

Selecting the monitored data (channel 1)

The monitored measuring point is defined by the parameter DA1ADDR 187TEE and the

reference measurement point by the parameter DA1REFADDR 186TEE.

Sign selection (channel 1)

Positive numbers are selected by setting the content of DA1MODE 189TEE to zero. In that

case the numeric range of the D/A converter is as follows:

0 = -5 V

255 = +5 V

Signed numbers are selected by setting the content of DA1MODE 189TEE to a value

other than 0.  In that case the numeric range of the D/A converter is as follows:

-128 = -5 V

0 =  0 V

+127 = +5 V

Scaling is executed by means of parameter DA1SCALE 188TEE as follows:

188TEE	=	0	No scaling

=	1	OUTPUT = INPUT/2

=	2	OUTPUT = INPUT/4

=	3	OUTPUT = INPUT/8

=	4	OUTPUT = INPUT/16

=	5	OUTPUT = INPUT/32

=	6   	OUTPUT = INPUT/64

=	7	OUTPUT = INPUT/128

=	8	OUTPUT = INPUT/256

=  256   	OUTPUT = INPUT * 2

=  512	OUTPUT = INPUT * 4

=  768	OUTPUT = INPUT * 8

=1024	OUTPUT = INPUT * 16

=1280   	OUTPUT = INPUT * 32

=1536	OUTPUT = INPUT * 64

=1792	OUTPUT = INPUT * 128

Channel-related parameters of the D/A converter

Channel 1

-	measuring point to be monitored	DA1ADDR	187TEE

-	reference measuring point	DA1REFADDR	186TEE

-	scaling				DA1SCALE	188TEE

-	mode of operation			DA1MODE	189TEE

Channel 2

-	measuring point to be monitored   	DA2ADDR	253TEE

-	reference measuring point         	DA2REFADDR	252TEE

-	scaling				DA2SCALE	254TEE

-	mode of operation		  	DA2MODE	255TEE

Channel 3

-	measuring point to be monitored	DA3ADDR	453TEE

-	reference measuring point	DA3REFADDR	452TEE

-	scaling				DA3SCALE	454TEE

-	mode of operation		  	DA3MODE	455TEE

Channel 4

-	measuring point to be monitored   	DA4ADDR	457TEE

-	reference measuring point	DA4REFADDR	456TEE

-	scaling				DA4SCALE	458TEE

-	mode of operation		  	DA4MODE	459TEE

Example of the D/A converter use

A D/A converter is used to monitor a difference between a frequency reference value and a

frequency actual value in channel 1.

The content of the measuring point FRREF 231T is set to the address 187TEE.

FRREF 231T is the frequency reference value of the modulator.

The content of the measuring point FREQREF 29T is set to the address 186TEE.

FREQREF 29T is the frequency reference of the inverter.

Conversion of the difference between the contents of two selected measuring points is

executed.  If, for example, the content of 231T is 3452 and that of 29T is 5000

,

a conversion of the difference 3452 -5000 = -1548 is executed.

Since the number has a sign, the content of 189TEE is set to <>0.

Since the number is not in the converter's numerical range, it is scaled by setting

188TEE = 4. The conversion of the number -96 (-1548/16) which is in the D/A converter's

numerical range (-128 to +127) is then executed.

If, after the scaling, the measured variable exceeds the converter's numerical range,

an overflow occurs.  (-128 to +127 or 0 to 255.)

26.	MOTOR THERMAL MODEL

The thermal model is a one way to indicate the motor temperature.The model uses

the total motor current I_TOTFILT 205T for calculation of the motor's temperature rise.

The angle points of the motor's load capacity curve are given to the model as torque

values (1000 = TN) ,see the figure below.The model transforms the load torque curve

to a load current curve by means of motor rating plate data. It also takes into account

the changes in the motor's temperature time constant as a function of the frequency.

The result of the calculation is used for overload protection of the motor.

Figure 26.1. Motor load curve. (6111375-4)

Basic equations of the program:

-	 = temperature rise

-	1 = temperature rise (heating)

-	2 = temperature rise for the last calculation minus cooling of the motor in

time of the IVAL (820ms)

-	 n = nominal thermal time constant of the motor

-	N = nominal value of the motor's temperature rise with selected load

capacity

-	K = effec of frequency on the thermal time constant

-	Kf = effec of frequency on the loadability curve

Figure 26.2.  Behaviour of the K and the Kf as a function of frequency.

(61113789)

The thermal time constant of the motor is given by the parameter MOT_THERM_TC(394TEE).

It is the time at which the temperature rises to 63% of the nominal value with nominal

current. Table 1 lists the time constants of the ABB's HXR squirrel cage motors.

The maximum value of the time constant MOT_THERM_TC(394TEE) in the program is 6000 s.

Figure 26.3.  Motor thermal time

|  | Number of poles |
| --- | --- |
|  | 2 | 4 | 6 |
| Pn (kW) | t (s) | t (s) | t (s) |
| 18.5 | 1260 | 1860 | 2340 |
| 22 | 1380 | 2040 | 2760 |
| 30 | 1680 | 2220 | 2940 |
| 37 | 1860 | 2460 | 3180 |
| 45 | 2040 | 2640 | 3420 |
| 55 | 2220 | 2820 | 3660 |
| 75 | 2400 | 3120 | 3920 |
| 90 | 2640 | 3300 | 4320 |
| 110 | 2820 | 3600 | 4680 |
| 132 | 3120 | 3960 | 5100 |
| 160 | 3420 | 4320 | 5700 |
| 200 | 3780 | 4740 | 6420 |
| 250 | 3780 | 4740 | 6420 |
| 315 | 3780 | 4740 | 6420 |

Table 1. Time constants of the ABB's HXR squirrel cage motors

The tripping and alarm limits are be set as per cent values of the nominal temperature

rise, 100 = 100%. The alarm limit is given by the parameter

CALC_MOT_TEMP_ALARM_LIM (399TEE) and the tripping limit is given by the parameter

CALC_MOT_TEMP_TRIP_LIM (400TEE).

E.g.Let us assume that ambient temperature is 20 C,MOT_THER_TORQ_0Hz (395TEE)

is 400 = 40% and MOT_THER_TORQ (396TEE) is 900 = 90%. The alarm limit is 110 C

and the tripping limit is 120 C. The per cent value of the temperature rise is calculated as

follows:

= Tlimit - Tenviroment

100 C = 120 C - 20 C

The figure 26.4 gives for 100 C and 0.9*Tn 112% on the vertical axis.

According to this the value of the parameter CALC_MOT_TEMP_TRIP_LIM (400TEE) should be set to 112 %.

The presumption is that the final temperature rise of the motor with 0.9*Tn torque is 90 C!

In the model 90 C corresponds to a temperature rise of 100 %. This value is normally set

into CALC_MOT_TEMP_ALARM_LIM(399TEE)

26.1	The effect of different loads on temperature rise

It is important to observe different thermal behaviours of different motors. Some motors

may have the same temperature rise with lower torque. Figure 26.4 illustrate thermal

behaviour of typical motor.

Alarm and tripping limit values can be read from curve T = 0.9 * Tn.

Calculated temperature rise ( C ) of the torque at the nominal speed of motor can be

read from the intersection point of curves T = 0.7 * Tn ....T = 1.0 * Tn and  = 100 %.

Figure 26.4.  The characteristic of the temperature rise.

The actual value of the temperature rise can be read from the parameter CALC_MOT_TEMP

(401T), 100 = 100% of nominal motor temperature rise.

The calculation of the temperature rise starts from the beginning (i.e.situation of the cold

motor) every time the auxiliary voltages are connected.

In case of multi-motor drive individual motors temperature cannot be indicated with the thermal model.

26.2	Thermal model panel indications

When the temperature exceeds the limits,the alarm is displayed on CP 1 and CP 2.

| Limit | CP 1 | CP 2 | Signal |
| --- | --- | --- | --- |
| Alarm | SA 60 | MOT OVERTEMP ALM |

FAULTWORD2 (212TM)

| Bit 8 = 1 |
| --- |
| Tripping | FL 29 | MOT OVERTEMP FLT |

FAULTWORD1 (211TM)

Bit 5 = 1

26.3	Thermal model setting parameters

The thermal model is activated by means of the following parameters. If any value

different from 0 is set to any of these parameters, then thermal model will be active.

MOT_THERM_TC 394TEE

MOT_THER_FREQ 398TEE

MOT_TEMP_TRIP_LIM 400TEE

Thermal time constant of the motor, MOT_THERM_TC 394TEE

-	Scaling: 1 = 1 second

Maximum continuous torque at 0 Hz, MOT_THER_TORQ_0Hz 395TEE

-	Scaling: 1000 = Tn

Maximum torque at the frequency of 398TEE, MOT_THER_TORQ 396TEE

-	Scaling: 1000 = Tn

Frequency limit below which the cooling ability of a self ventilated motor decreases,

MOT_THER_FREQ 398TEE

-	Scaling: 100 = 1 Hz

Alarm limit of calculated motor temperature, CALC_MOT_TEMP_ALARM_LIM 399TEE

-	Scaling: 100 = 100%

Tripping limit of calculated motor temperature, CALC_MOT_TEMP_TRIP_LIM 400TEE

-	Scaling: 100 = 100%

26.4	Input signals:

Filtered actual value of the total current, I_TOTFILT 205T

-	Scaling: 1000 = nominal SAMI current

Filtered actual value of the output frequency, FR_ACT 208T

-	Scaling: 1000 = 10 Hz

26.5	Output signals:

Calculated temperature of the motor, CALC_MOTOR_TEMP 401T

-	Scaling: 100 = 100% rise of the nominal motor temperature

Nominal motor current, IMOT_N 402T

-	Scaling: 1000 = nominal SAMI current

The highest continuous current at 0 Hz which the motor can withstand thermally.

The control program calculates the current according the nominal values and P395TEE,

MOT_THER_CURR_0Hz 403T

-	Scaling: 1000 = nominal motor current

Fault indication, FAULTWORD1 211TM

-	Bit 5 = 1, motor overtemperature fault

Fault indication, FAULTWORD2 212TM

-	Bit 8 = 1, motor overtemperature alarm

27.	COMMUNICATION TABLE

Each table location provides data in accordance with the following header:

TYP	D	H	High Limit   Low Limit   Init   Explanation

TYP = T	if the value is saved only in the RAM memory and is not protected against 	power failures,

TEE	if the value is stored in the EEPROM memory,

TM	if the value is stored to the battery-backed up RAM memory.

D =	Decimal address.

H =	Hexadecimal address.

High Limit =	The largest number that can be stored at the given address.  (The program does not accept a number with a value above this limit and displays the "PARAM TOO HIGH" message on control panel CP2 and "SA 54" on control panel CP1.)  If a number is not specified, the high limit is assumed to be +32767.

Low Limit =	The smallest number that can be stored at the given address (as for High Limit value but in this case messages "PARAM TOO LOW" on control panel CP2 and "SA 53"

on control panel CP1 are displayed). If a number is not specified, the low limit is assumed to be -32768.  If both limits have been set to zero, the parameters cannot be stored to this memory location.  After an attempt to save to memory location with zero limits, the "ILLEGAL PARAM" message is displayed on  control panel CP2 and "SA 55" is displayed on control panel CP1.

Init. =	Initialization value which is stored to the memory location when an empty EEPROM is installed on the card.  The value is equal to 0 if the initialization value is not given.

Explanation = 	Explanation. If not presented the parameter has no meaning in the given program version.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	1	001				SELMABLOCKS0/

SAMINODECOMM

Parameters can have two

meanings:

A:

No ABB Master Fieldbus interface:

Selma can send control commands to this location. Stored commands are used as input data for a functional block.  E.g. for a start-up request or as a frequency reference.

B:

ABB Master Fieldbus interface:

If the connection between Master and SamiNode is interrupted, parameter will have a value 1. If the connection between SAMI and SamiNode is interrupted, parameter will have a value 2. SAMI acts according to mode selection SAMINODE_CONT 2351TEE

T	2	002				START.

Start-up request.  When the given value is <> 0, the inverter starts up at a frequency defined by 29T or at a speed defined by 27T, depending on the selection made by 71T.

T	3	003				STOP.

Stop request. When the given value is <> 0, the inverter integrates the frequency towards 0 and stops when the frequency falls below the 77TEE parameter value.

T	4	004				SELMABLOCKS1

Selma can send control commands to this location. Stored commands are used as input data for a functional block. E.g. for a start-up request or as a frequency reference.

T	5	005				SELMABLOCKS2

See 4T.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	6	006				SELMABLOCKS3/

FAULTMSGES

Parameters can have two

meanings:

A:

No ABB Master Fieldbus interface:

Selma can send control commands to this location. Stored commands are used as input data for a functional block. E.g. for a start-up request or as a frequency reference.

B:

ABB Master Fieldbus interface:

Counter for error messages in SamiNode.

T	7	007 				LOCKPANEL

T	8	008 			1	EEPROMLOCK

When the given value is 1,

parameters are stored to the

EEPROM memory.

T	9	009				TBCTRANSMIT1

Control Word used to determine

transmission intervals of the SAFT

188 IOC card's I/O input signals.

T	10	00A				TBCTRANSMIT2

As in the above.

T	11	00B				Reserved

T	12	00C				RESET

Fault reset.  When set to a <> 0

value, the faults of the inverter are

reset.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	13	00D				STATUS_CMD

Control Command code packed to

one parameter.  Each bit of the

word corresponds to a certain

function of the device as follows:

Bit

0 = STOP by ramp

1 = STOP by current limit (speed

control)

2 = COAST STOP

3 =

4 =

5 =

6 = START at 27T/29T speed

7 = START at 161T/167T speed

8 = START at 162T/168T speed

9 = RESET

10 = Bypass of the speed

integrator (speed control).

11 =

12 =

13 =

14 =

15 =

RESET sets STATUS_CMD to zero.

When STATUS_CMD is in use,

instructions from other Control

Words are not accepted.

T	14	00E				CP2_ANALOG

At this location Control Panel CP2

saves its analog input data.

Application functional block input.

T	15	00F				ANAOUT2

T	16	010				ANAOUT3

T	17	011

T	18	012

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	19	013				CP1_BUTTONS

The SAFT 188 IOC interface card sends CP1 pushbutton signals in the packed bit form to this address. The content of this location is unpacked in the CP1 BUTTONS application block to the separate locations.

T	20	014			0	SELMASTOPC

The content of this counter is

incremented by 1 after each stop

command (2T) received from the

serial data communications

channel.

T	21	015			0	DRIVESTOPC

The content of this counter is

incremented by 1 after each stop

command initiated by the inverter

(e.g. a fault stop).

T	22	016 				COAST_STOP

Stop command.  When <> 0, the

inverter is stopped immediately.

T	23	017				BUTTONSWORD

CP2's pushbutton signals in

packed bit form. Input to an

application block.

T	24	018				START1_P

Start-up request.  When the given

value is <> 0, the inverter is started

at the 161TEE frequency reference

or at the 167TEE speed reference,

depending on the selection made

by 71T.

T	25	019				START2_P

Start-up request.  When the given

value is <> 0, the inverter is started

at the 162TEE frequency reference

or at the 168TEE speed reference,

depending on the selection made

by 71T.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	26	01A	+1400	-1400		TORQREF

Signed torque reference. Scaling

according to IRE, 1000 = rated

value.

T	27	01B	+20000	-20000		SPEEDREF

Signed speed reference. (Speed

control) 20000 = DRIVESPEEDMAX.

T	28	01C

T	29	01D	+20000	-20000		FREQREF

Signed frequency reference.

100 = 1.00 Hz.

T	30	01E	1000	-1000		DELTASPREF

CP2 sends to this address an

increment value which is summed

with the content of location 29T.

There after it is automatically set

to 0. When speed control is

selected, the increment value is

summed with the content of 27T.

T	31	01F 	1000 	-1000		DELTASPREF1

CP2 sends to this address an

increment value which is summed

in a functional block. Thereafter it

is automatically set to 0.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	32	020				This location is reserved for saving

display messages transmitted

between Control Panels and the

inverter.

T	33	021						- " -

T	34	022						- " -

T	35	023						- " -

T	36	024						- " -

T	37	025						- " -

T	38	026						- " -

T	39	027						- " -

T	40	028						- " -

T	41	029						- " -

T	42	02A						- " -

T	43	02B						- " -

T	44	02C						- " -

T	45	02D						- " -

T	46	02E				SELMABLOCKS4

See 4T.

T	47	02F				SELMABLOCKS5

See 4T.

TEE	48	030  			1	SCALARCONTROL

Bypass of controllers.

<>0= control connected

0= no control

TEE	49	031				FRSSPEEDSTEP

If = 0, a 238T parameter value is

summed with a speed reference

value prior to filtering of the

difference value (55TEE and

74TEE).

If <>0, a 238T parameter value is

summed with a speed reference

value after filtering (speed control).

TEE	50	032	200		0	KPSP

Drooping (speed control). Scaling:

10 = 1 % decrease of the rated

speed under rated load.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	51	033	20000	0	20000	SPEEDMAX

Signed high limit of a speed

reference value.

E.g. if DRIVESPEEDMAX

(155TEE) is set to 1500 (= 1500

rpm) the speed corresponds to the

actual value of 20000. If 51TEE is

now set to 10000, the drive can

only have 750 rpm (speed control).

TEE	52	034	0      	-20000  	-20000	SPEEDMIN

Signed low limit of the speed

reference value. It has the same

meaning as the 51TEE but in the

negative direction. (Speed control)

TEE	53	035	600	1	20	SPEEDINTACC

The acceleration time of the

speed reference from 0 to the

value defined by 155TEE

(DRIVESPEEDMAX).

1 = 1 s (speed control).

TEE	54	036	600	1	20	SPEEDINTDEC

The deceleration time of the speed

reference from the speed defined by

155TEE (DRIVESPEEDMAX) to 0.

1 = 1 s (speed control).

TEE	55	037	1000	0		FRS

The time constant of the first filter

expressed in ms. The lowest value

that can be used is 10 ms.

0 = filter is bypassed (speed control)

TEE 	56	038	30000	0	1500	TIS

Control parameter for adjustment of

the integral action of the speed

controller.

1000 = 1 s.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	57	039	30000	0	2000	KPS

Control parameter for adjustment of

the proportional gain of the speed

controller.

TEE 	58	03A	300		0	SPEEDSOFTENTIME

Duration of the rounding function to

soften the changes occurring in the

speed reference. Scaling: 10 = 1 s.

TEE	59	03B	600		0	KPSDTIME

Acceleration compensation factor.

The KPSDTIME is the time required

by the drive to accelerate to the

rated speed with the rated torque.

TEE 	60	03C	10000	5	6000	FLYINGFREQMAX

Running start search frequency in

the positive direction.10000=100 Hz.

TEE	61	03D	-10000	-5	-6000	FLYINGFREQMIN

Running start search frequency in

the negative direction.

-10000 = -100 Hz.

TEE	62	03E	20000	-20000	6000	FREQMAX

High limit of the frequency reference

value.

10000 = 100 Hz.

TEE	63	03F	20000	-20000	-6000	FREQMIN

Low limit of the frequency reference

value.

-10000 = -100 Hz.

TEE	64	040	6000	10	200	FREQINTACC

The acceleration time of the

frequency reference value integrator

from 0 to +100 Hz.

10 = 1 s.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	65	041		0	380	SAMI_AC_RATEDVOLTAGE

The rated supply voltage of the

frequency converter expressed in

volts. It is used for the Uc

measurement calibration and for

current limit scaling of 415 V units.

TEE	66	042	6000	10	200	FREQINTDEC

The deceleration time of the

frequency reference value integrator

from +100 Hz to 0.

10 = 1 s.

TEE	67	043	120	0	100	MAXOUTPUTVOLTAGE

Maximum output voltage of the

inverter.

100 = rated output voltage.

TEE	68	044	20000	2000	5000	FIELDWEAKPNT

Field weakening point frequency

expressed in 0.01 Hz.  At this

frequency the output voltage

reaches a value of 67TEE when Uc

has the rated value.  It specifies the

slope of the U/f linear function plot

together with the 67TEE parameter.

5000 = 50 Hz.

TEE	69	045	20000	0	3000	IRCOMPPOINT

IRCOMPPOINT defines the

frequency at which the IR

compensation effect is terminated.

1000 = 10 Hz.

TEE	70	046	1200	0	300	IRCOMPCURRENT

An initial current of the IR

compensation.

1000 = rated output

current of the inverter.

T	71	047	2	0		CONTROLSEL

Control mode selection.

0 = Frequency control

1 = Speed control

2 = Torque control

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	72	048	180	0		TORQMAXTIME

An IR compensation effect time

after start-up. 10 = 10 s.

0 = IR compensation is continuously

connected.

TEE	73	049	5000	0		FREQDROOPING

Drooping based on IRE.

TEE	74	04A	1000	0		FRS1

The time constant of the second

filter of the speed controller,

expressed in ms. The lowest value

is 10 ms.

0 = filter is bypassed.(Speed control)

TEE	75	04B	20000	0	3000	RESTARTDELAY

Restart delay.  1000 = 1 s.

TEE	76	04C	1000	300	870	COSFIIFACTOR

Motor power factor. 870 = 0.87

TEE	77	04D	20000	0	100	STOP_FREQ

Absolute value of the frequency

below which the inverter is stopped

after a stop command (ceases

modulation).  100 = 1 Hz.

TEE	78	04E	20000	0		TACHORIPPLE

0 = Not in use.  If the difference

between two successive speed

measurements (21 ms) is greater

than the content of parameter

78TEE, the drive is stopped and

a tachometer fault is reported.

TEE	79	04F	1400	300	1000	IREMAX

Torque limit in motor operation

(active current component).

1000 = active component

corresponding to the rated inverter

current when COSFIIFACTOR

76TEE is given.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	80	050	-300	-1400	-1000	IREMIN

Torque limit in generator operation.

Scaling as in the above.

TEE	81	051	2000	0	300	J_GAIN

Effect of the moment of inertia

J in power loss control.

TEE	82	052	3000	10	1000	STALLFREQ

High limit for the stall protection

activation frequency.

1000 = 10 Hz.

TEE	83	053	180	1	10	STALLTIME

Stall protection activation time.

1 = 1 s.

TEE	84	054	500	0	50	FSLIPSCALE

Slip compensation scaling. The

drive frequency is corrected by

means of the slip compensation in

such a way that the motor's actual

RPMs correspond to the frequency

reference value.

Scaling:

TEE	85	055				IRCOMPSEL

IR compensation selection:

0 =	no IR compensation.

1 =	IR compensation without

an automatic search.

3 =	IR compensation with an

automatic search.

9 =	SAMI STAR TF mode.

TEE	86	056				STALLPROTECTSEL

Stall protection selection:

0 =	no stall protection

1 =	stall protection selected.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	87	057				FLYINGSTARTSEL

Running start selection:

0 =	no running start

1 =	running start selected.

TEE	88	058				NETFAILSEL

Power loss control selection:

0 =	no power loss control

1 =	power loss control selected.

TEE	89	059				SLIPCOMPSEL

Slip compensation 	selection:

0 =	no compensation

1 =	compensation selected.

TEE	90	05A				TORQCONTSEL

Torque control selection:

0 =	no torque control

1 =	torque control selected.

TEE	91	05B			1	INTEGMODESEL

Selection of the integrator S curve:

0 =	no S curve

1 =	S curve is selected.

TEE	92	05C				SPEEDCONTSEL

Speed control selection:

0 =	no speed control

1 =	speed control selected.

TEE	93	05D			1	TRENDBUFSEL

Trend buffers selection:

0 =	no trend buffers

1 =	trend buffers selected.

TEE	94	05E				SPEEDMEASSEL

Speed measurement selection:

0 =	no speed measurement

1 =	speed measurement

selected.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	95	05F				DATRANSFSEL

Selection of SAFT 154 DAC D/A

converter:

0 =	no D/A converter

1 =	D/A converter selected.

T	96	060				DCBRAKESEL

Selection of DC braking

0 =  no DC braking

1 =  DC braking selected

T	97	061

T	98	062

TEE	99	063				SIGN

Sign of numbers displayed on the

left and in the middle of the CP2.

0 =	sign is the same as that of

the quantity to be displayed

1 =	reversed sign

TEE	100	064	30000	1	1	DISPMUL0

Scaling factor of the CP2 left

display.

TEE	101	065	30000	1	10	DISPDIV0

Divider of the CP2 left display.

TEE	102	066	3	0	1	DISPPNT0

Number of decimal fractional digits

on the CP2 left display.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	103	067	2224	0	29	DISPSRC0

An address of the table location

displayed on the left is saved at

this address.

A left display is achieved when

content of a location addressed by

103TEE is multiplied by the content

of 100TEE and divided by the

content of 101TEE. The decimal

point position of an obtained integer

number is determined so that the

number of fractional digits

corresponds to the number defined

by 102TEE.

TEE	104 	068	30000	1	1	DISPMUL1

Scaling factor of the CP2 central

display.

TEE	105	069	30000	1	10	DISPDIV1

Divider of the CP2 central display.

TEE	106	06A	3	0	1	DISPPNT1

Number of decimal fractional digits

on the CP2 central display.

TEE	107	06B	2224	0	208	DISPSRC1

An address of the table location

displayed in the CP2 central display

is saved at this address.

A display read-out is developed as

for the 103TEE.

TEE	108	06C	30000	1	1	DISPMUL2

Scaling factor of the CP2 right

display.

TEE	109	06D	30000	1	10	DISPDIV2

Divider of the CP2 right display.

TEE	110	06E	3	0	0	DISPPNT2

Number of decimal fractional digits

on the CP2 right display.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	111	06F	2224	0	205	DISPSRC2

An address of the table location

displayed in the CP2 right display is

saved at this address.

A display read-out is developed as

for the 103TEE.

TEE	112	070	2224	0		REQUESTMSGE

Parameter request.  A number of a

parameter to be requested for the

inverter is saved at this address.

TEE	113	071				ANSWERMSGE

Parameter response. The inverter

answers the request by using this

location and saves as a data the

content of the requested address.

When the inverter receives a

message with address 113, it saves

the obtained value to the table

location which was last requested

by address 112T.

TEE	114	072	30000	0	10	IVAL0

The interval at which the inverter

transmits the content of the table

location determined in 115TEE.

1 = 21 ms

The inverter does not accept the

values of IVAL0...7 which overload

the communications channel.

TEE	115	073	255	0	247	IX0

The address of the parameter which

is to be transmitted at an interval

determined by 114TEE.

TEE	116	074	30000	0	9	IVAL1

Transmission interval.  As 114TEE.

TEE	117	075	255	0	248	IX1

A quantity to be transmitted.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	118	076	30000	0	9	IVAL2

TEE	119	077	255	0	249	IX2

TEE	120	078	30000	0	8	IVAL3

TEE	121	079	255	0	15	IX3

TEE	122	07A	30000	0	8	IVAL4

TEE	123	07B	255	0	16	IX4

TEE	124	07C	30000	0		IVAL5

TEE	125	07D	255	0		IX5

TEE	126	07E	30000	0		IVAL6

TEE	127	07F	255	0		IX6

TEE	128	080	30000	0		IVAL7

TEE	129	081	255	0		IX7

TEE	130	082	30000	0	1	NORMALMSGE

Transmission interval of CP2 normal

display messages.

1 = 420 ms

2 = 840 ms, etc.

TEE	131	083	30000	0	10	DIAGNMSGE

Transmission interval of CP2 fault

display messages.

1 =	420 ms

2 =	840 ms, etc.

T	132	084	2500	0		REQUESTMSGE_BOX2

Parameter request.

An address of a parameter to be

requested from the inverter is

written to this address.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	133	085				ANSWERMSGE_BOX2

Parameter response.

The inverter answers the request by

using this location and saves as a

data the content of the requested

address.

When the inverter receives a

message with address 133, it saves

the obtained value to the table

location which was last requested

by address 132T.

TEE	134	086	30000	0	10	IVAL0-2

The same as 114TEE for serial data

communications channel 2.

TEE	135	087	255	0	213	IX0-2

The same as 115TEE for serial data

communications channel 2.

TEE	136	088	30000	0	21	IVAL1-2

As in the above.

TEE	137	089	255	0	214	IX1-2

As in the above.

TEE	138	08A	30000	0		IVAL2-2

TEE	139	08B	255	0		IX2-2

TEE	140	08C	30000	0	50	IVAL3-2

TEE	141	08D	255	0	210	IX3-2

TEE	142	08E	30000	0		IVAL4-2

TEE	143	08F	255	0		IX4-2

TEE	144	090	30000	0		IVAL5-2

TEE	145	091	255	0		IX5-2

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	146	092	30000	0		IVAL6-2

TEE	147	093	2224	0		IX6-2

TEE	148	094	255	0		IXS6-2

The same as in the above with the

exception that the content of the

location defined by 147TEE is sent

using the address given here.

TEE	149	095	30000	0		IVAL7-2

TEE	150	096	2224	0		IX7-2

TEE 	151	097	255	0		IXS7-2

The same as 148TEE.

TEE	152	098	32767	0	0	KPSMIN

Proportional gain of a speed

controller with a zero output.

TEE	153	099	500	0		KPSWEAKPNT

When the absolute value of the

speed controller output overshoots

this limit, the proportional gain is

determined by parameter 57TEE.

TEE	154	09A	36	1	2	POLEPAIRS

The pole pair number of the motor.

TEE	155	09B	16000	100	1800	DRIVESPEEDMAX

Maximum speed of the drive, RPMs

(speed control). At the given speed,

the numerical actual value of speed

is 20000.

TEE	156	09C	6000	10	1024	TACHOPULSENMBR

The number of tacho pulses per

revolution.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	157	09D	30000	0		COMM_TIMEOUT2

Supervision of serial data

communications on channel 2:

Time elapsed from reception of the

previous acknowledged message so

that the communication link is

considered to be disconnected.

The scaling is 21 ms per unit. E.g.

1000 = 21 s.

The functions following  the

communication break are defined

in 171TEE.

TEE	158	09E	10	2	6	CHARGETIME

The charge time of the chopper of

the GTO inverter.  1 = 100 ms.

TEE	159	09F	20000	0	5000	TACHOPHASEDISABLE

When the speed actual value (235T)

overshoots this limit, only one

tachometer channel is used for

speed measurement.

TEE	160	0A0				TACHOTYPE

Selection of the tachometer type:

0 =	two-channel tachometer.

The phase shift between the two

channels is 90°.

1 =	single-channel tachometer.

(In this option a hardware change is

required on the control card.)

TEE	161	0A1	20000	-20000		FREQ1

The fixed frequency reference 1.

The inverter is started to this

reference value by means of the

24T command.

Scaling: 1000 = 10 Hz.

TEE	162	0A2	20000	-20000		FREQ2

The fixed frequency reference 2.

In this case the inverter is started up

by means of the 25T command.

Scaling: 1000 = 10 Hz.

T	163	0A3

TEE	164	0A4	0	0		MASTERSLAVE

Mode of operation of the serial data

communications channel 2.

0 =	opera tion in accord ance

with the serial data communications

protocol.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	165	0A5

TEE	166	0A6				SCDRIVETYPE

Drive type. Control Word in packed

bit form. Each bit initiates functions

as follows:

Bit

0 =	IR compensation

1 =	automatic search of IR

compensation

2 =	stall protection

3 =

4 =	running start

5 =	power loss control

6 =	slip compensation

7 =	torque control

8 =	S curve of integrator

9 =

10 =	speed control

11 =	trend buffers

12 =	speed measurement

13 =	DC braking

14 =

15 =	D/A converters (SAFT 154

DAC)

TEE	167	0A7	20000	-20000		SPEED1

The fixed speed reference 1.

The inverter is started to this

reference value by means of the

24T command when 71T is 1.

Scaling: 20000 = 155TEE

DRIVESPEEDMAX

TEE	168	0A8	20000	-20000		SPEED2

The fixed speed reference 2. In

this case the inverter is started up

by means of the 25T command

when 71T is 1.

Scaling: 20000 = 155TEE

DRIVESPEEDMAX

T	169	0A9

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	170	0AA	9600	110	4800	CH2BAUDRATE

Baud Rate of the inverter's serial

data communications channel 2.

The procedure for changing a

transmission rate is as follows:

-	Set 8T = 1.

-	Change 170TEE.

-	Wait for the message

"STORED TO BACKUP/SA 51"

on the control panel.

-	Switch off the power from

the control card for 10 s.

-	Switch on the power again.

At this point the communications

channel 2 will transmit messages

at the new set rate.

TEE	171	0AB	3	0	3	SELMACONT

Action after a communication break:

0 =	no action.

1 =	message to the control

panel.

2 =	message to the control

panel and inverter stopped by

integrator.

3 =	message to the control

panel and inverter shut down

immediately.

TEE	172	0AC	30000	0	238	COMM_TIMEOUT

Supervision of serial data

communications on channel 1:

Time elapsed from reception of the

previous acknowledged message so

that the communication link is

considered to be disconnected.

The functions following the

communication break are defined

in 171TEE.

TEE	173	0AD	3	0	3	COMMUNICATIONTYPE

Selection of the acknowledgement

message:

0 =	no message.

1 =	acknowledgement

message to channel 1.

2 =	acknowledgement

message to channel 2.

3 =	acknowledgement

message to both channels.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	174	0AE	3000		0	TACHDELAY

Control of tacho pulse train. After

a start-up command, tacho pulses

are generated within an interval

defined by this parameter.  If a

tacho pulse is not received,

a failure alarm is given.

0 =	no control

1 =	21 ms

2 =	42 ms

3 =	63 ms, etc.

T	175	0AF

TM	176	0B0				FLT_QUEUE

TM	177	0B1				Fault buffer.  When a

TM	178	0B2				fault occurs, the content of the

TM	179	0B3				buffer is decremented by 1 and

TM	180	0B4				the new fault message is

TM	181	0B5				transferred to 176TM.

The RESET button sets -1 to the

fault queue (176TM) so that faults

received at different times are

separated.

Fault messages:

1 =	FL1  CHOP UNDERVOLT

2 =	FL2  CHOP OVERVOLT

3 =	FL3  AUX UNDERVOLT

4 =	FL4  OVERTEMPERATURE

5 =	FL5  OVERCURRENT

6 =	FL6  DC OVERVOLT

7 =	FL7  DC UNDERVOLT

8 =

9 =	FL9  U1 FAULT

10 =	FL10 U2 FAULT

11 =	FL11 V1 FAULT

12 =	FL12 V2 FAULT

13 =	FL13 W1 FAULT

14 =	FL14 W2 FAULT

15 =	FL15 SHORT CIRC/EFLT

16 =

17 =	FL17 COMMUNIC FAULT

18 =	FL18 TACHO LOSS

19 =	FL19 I MEAS FAULT

20 =	FL20 MOTOR STALLED

21 =	FL21 MATCH CARD FAULT

22 =	FL22 PROCESSOR FAULT

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	182	0B6				OKMSGES1

Number of accepted messages

received on channel 1. Incremented

by 1 on every received message.

T	183	0B7				FAULTMSGES1

Number of rejected messages on

channel 1. The content of this

location should be 0. Continuous

increasing of the content indicates

that there are disturbances in the

communication link.

T	184	0B8				OKMESGES2

The same as 182T for channel 2.

T	185	0B9				FAULTMSGES2

The same as 183T but for the

channel 2.

TEE	186	0BA				DA1REFADDR

Address of the reference voltage

code of the D/A-converter

(SAFT 154 DAC) channel 1.

TEE	187	0BB			223	DA1ADDR

Address of a variable monitored by

the D/A-converter channel 1.

TEE	188	0BC			4	DA1SCALE

Scaling of a variable before

converting to an 8-bit code.

Channel 1.

TEE	189	0BD			1	DA1MODE

Mode of operation of the D/A-

converter channel 1.

TEE	190	0BE	100	0	50	CURRENTOFFSET

Current measurement zero point

error expressed in 0.1 % of the

rated value of the fundamental

wave. If the error is greater than the

value given here, the inverter is not

started but reports the fault message

"FL19/I MEAS FAULT".

TEE	191	0BF			223	TREND1

Address of the variable monitored in

trend buffer 1.

TEE	192	0C0			224	TREND2

Address of the variable monitored

in trend buffer 2.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	193	0C1			225	TREND3

Address of trend 3.

TEE	194	0C2			226	TREND4

Address of trend 4.

TEE	195	0C3			215	TREND5

Address of trend 5.

TEE	196	0C4			1	TRENDIVAL

Sampling interval of trend buffer

expressed in 3 ms units.

TEE	197	0C5			-1	TRENDTRIG

Trend triggering condition:

-1 =	fault triggering only

>1 =	triggering takes place if the

difference between two consecutive

values in trend 1 is greater than

the value set in this loca tion.

T	198	0C6

T	199	0C7				TRENDSAVE

Manual trend triggering.  When set

to <>0, causes triggering and saving

of the trends.

T	200	0C8				TRIGCOUNT

Triggering counter.

T	201	0C9	0	0		IRE_FILT

A filtered actual value of the active

current component. A positive value

represents the motor mode of

operation and a negative value

stands for the generator mode.

1000 = active current component

corresponding to the rated current

when COSFIIFACTOR 76TEE is

given.

T	202	0CA	0	0		T_ACT

A filtered torque actual value. When

the frequency is below the field

weakening point (FWP), T_ACT =

IRE_FILT. At a frequency higher

than FWP,

T_ACT = IRE_FILT*FWP/FR_ACT.

T	203	0CB	0	0		P_ACT

A filtered value of the active power.

1000 = rated output.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	204	0CC	0	0		U_ACT

A filtered actual value of the output

voltage.1000 = rated output voltage.

T	205	0CD	0	0		I_TOTFILT

A filtered value of the total output

current.1000 = rated value.

T	206	0CE	0	0		COS_PHI

The power factor of the output. 870

corresponds to a factor of 0.87.

T	207	0CF	0	0		UC_ACT

An actual value of the Uc voltage.

1000 = rated value.

T	208	0D0	0	0		FR_ACT

The filtered actual value of the

output frequency. 1000 = 10 Hz.

T	209	0D1	0	0		DIRECTION

Direction of rotation word.

0 =	positive, motor rotates in

clockwise direction at the positive

frequency.

>0 =	negative.

TM	210	0D2	0	0		FAULTWORD0

Diagnostic bits generated by the

inverter's H/W. Fault bits are

presented in the packed form. The

meaning of each bit is as follows:

("No" is the number corresponding

to the type of fault in 176TM and on

the CP1).

No	Bit

1   	0 = CHOP UNDERVOLT

2   	1 = CHOP OVERVOLT

3   	2 = AUX UNDERVOLT

4   	3 = OVERTEMPERATURE

5   	4 = OVERCURRENT

6   	5 = Uc OVERVOLT

7   	6 = Uc UNDERVOLT

7 =

9   	8 = U1 FAULT

10   	9 = U2 FAULT

11  	10 = V1 FAULT

12  	11 = V2 FAULT

13  	12 = W1 FAULT

14  	13 = W2 FAULT

14 =

15 =

TYP	D	H	High Limit	Low Limit	Init	Explanation

TM	211	0D3	0	0		FAULTWORD1

Faults detected by the software.

Fault data is presented in the

packed bit form word.The meaning

of each bit is as follows:

No Bit

19  0 	= current measurement fault

21  1 	= match card fault

22  2 	= processor fault

3 	=

15  4 	= short circuit/ earth fault

29  5 	= motor overload

6 	=

7 	=

25  8 	= external fault 1

26  9 	= external fault 2

10 	=

28 11 	= SamiNode fault

17 12 	= fault in serial data

communications ch 1

17 13 	= fault in serial data

communications ch 2

20 14 	= motor stall

18 15 	= tachometer fault

TYP	D	H	High Limit	Low Limit	Init	Explanation

TM	212	0D4	0		0	FAULTWORD2

Diagnostics data reported by the

software.  Bits under numbers

marked with an "*" inhibit start-up of

the inverter.

No	Bit

50*	0 	= empty EEPROM

51	1 	= saving to the EEPROM

52	2 	= writing to the EEPROM is

53	= parameter

54	value is too large

55	4 	= writing to an illegal address

57*	5 	= insufficient AC/DC voltage

59	6 	= system restart

58*	7 	= start-up inhibited

60	8 	= motor overloaded

9 	=

10	=

11	=

12	= running at the frequency

limit

56	13	= no battery backup

14	=

15	=

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	213	0D5				IOWORD

T	214	0D6	0	0		SAMISTATUS

Inverter Status Word. The meaning

of the bits is as follows:

Bit

0 = running

1 = ready

2 = fault

3 = local/remote

4 =

5 = false start inhibit

T	215	0D7	0	0		SCSTATUS

Status Word of the inverter

controllers' operation state.

Meaning of the bits:

Bit

0 = quiescent state

1 = power loss control

2 = running start

3 = frequency integrator

4 = IREHIGH controller

5 = IRELOW controller

6 = UCHIGH controller (119 %)

7 = UCHIGH controller (116 %)

8 = IR compensation functioning

9 =

10 =

11 = running at the frequency limit

12 = flux forming (IR compensation)

13 = torque control

14 = IR compensation increases

the voltage in mode 85TEE = 3

15 = DC braking active

T	216	0D8				SAMIADDR

Debugging address.

(4096+2*address)

T	217	0D9				SAMIDATA

Debugging data.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	218	ODA	16125	-16125		UREFSTEP

Voltage step reference for the

modulator.

16125 = 100 % voltage reference.

T	219	0DB	0	0		IR

R-phase output current

instantaneous value.

1000 = peak value of rated inverter

current

T	220	0DC	0	0		IS

S-phase output current

instantaneous value.

1000 = peak value of rated inverter

current

T	221	0DD	0	0		ID

Inverter output current component in

the same vector direction as the

voltage (active current).

1000 = rated value.

T	222	0DE	0	0		IQ

Inverter output current component

perpendicular to the voltage.

1000 = rated value.

T	223	0DF	0	0		IRE

Unfiltered actual value of the active

current component.

1000 = rated value when

COSFIIFACTOR 76TEE is given.

T	224	0E0	0	0		I_TOT

Unfiltered total current value of the

inverter output.

1000 = rated value.

T	225	0E1	0	0		FREQREF1

Frequency reference value

preceding integration.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	226	0E2	0	0		FREQREF2

Frequency reference value after

integrator. The value is also

affected by the limiting controllers.

1000 = 10 Hz.

T	227	0E3	0	0		UCAVG

Uc filtered actual value.

1000 = rated value.

T	228	0E4	0	0		ABSFREQ

Unsigned frequency value.

1000 = 10 Hz.

T	229	0E5	0	0		FSLIP

Slip compensation block output.

1000 = 10 Hz.

T	230	0E6	0	0		UREF

Voltage reference of the modulator.

16125 = rated output voltage.

T	231	0E7	0	0		FRREF

Frequency reference for the

modulator.

1000 = 10 Hz.

T	232	0E8	0	0		SPEEDREF1

Speed reference value for the

speed integrator after the selection

logic. (Speed control)

T	233	0E9	0	0		SPEEDREF2

Speed reference value after the

speed integrator.

20000 = DRIVESPEEDMAX (speed

control).

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	234	0EA	0	0		FREQREF3

Frequency reference value produced

by the speed control circuit.

1000 = 10 Hz.

T	235	0EB	0	0		SPEEDACT

Unfiltered speed actual value.

20000 = DRIVESPEEDMAX.

T	236	0EC	0	0		SPEEDACT2

Filtered speed actual value.

20000 = DRIVESPEEDMAX.

T	237	0ED	5000	-5000		TORQSTEP

Frequency step reference for the

modulator expressed in 0.001 Hz.

(1000 = 1 Hz)

T	238	0EE	20000	-20000		SPEEDSTEP

Speed step for the speed controller.

The step magnitude is selectable

before or after the filters by means

of the parameter 49TEE. (Speed

control)

T	239	0EF	0	0		FACT

Stator frequency value calculated in

the speed measuring circuit in 0.01

Hz. (Shaft frequency * the pole pair

number.)

T	240	0F0	0	0		FSLIPREF

Output of the speed controller in

0.01 Hz.

TEE	241	0F1			227	TREND6

Address of the variable monitored in

trend buffer 6.

TEE	242	0F2			230	TREND7

Address of the variable monitored in

trend buffer 7.

TEE	243	0F3			231	TREND8

Address of the variable monitored in

trend buffer 8.

T	244	0F4	0	0		IPEAK

Current peak value.

2300 = overcurrent limit.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	245	0F5				DIG_INPUTS

At this address, the Interface card

saves the Status Word of the digital

inputs in packed form. The DIGITAL

INPUTS application block input.

T	246	0F6				ANAIN0

The ANALOG INPUT 0 application

block input from the Interface card.

T	247	0F7				DIG_OUTPUTS

The DIGITAL OUTPUTS application

block output to the Interface card.

T	248	0F8				ANAOUT0

The ANALOG OUTPUT 0 application

block output to the Interface card.

T	249	0F9				ANAOUT1

The ANALOG OUTPUT 1 application

block output to the Interface card.

T	250	0FA				ANAIN1

The ANALOG INPUT 1 application

block input from the I/O card.

T	251	0FB				ANAIN2

The ANALOG INPUT 2 application

block input from the I/O card.

TEE	252	0FC			355	DA2REFADDR

Channel 2 reference voltage

address of the D/A converter

(SAFT 154 DAC).

TEE	253	0FD			227	DA2ADDR

Address of the variable monitored

by the D/A-converter channel 2.

TEE	254	0FE			2	DA2SCALE

Scaling of the variable before

conversion to an 8-bit code.

Channel 2.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	255	0FF			1	DA2MODE

Mode of operation of the

D/A-converter channel 2.

TEE	256	100	1150	850	1000	I_MULTIPLY

Scaling factor of current measurement.

1000 = 1.

| TYPE | IMULTIPLY 256TEE |
| --- | --- |
| SAMI 1100 F 380 | 1145 |
| SAMI 1500 F 380 | 1053 |
| SAMI 1100 F 400 | 1145 |
| SAMI 1600 F 400 | 1039 |
| SAMI 1100 F 415 | 1145 |
| SAMI 1650 F 415 | 1046 |
| SAMI 1230 F 440 | 1139 |
| SAMI 1750 F 440 | 1045 |
| SAMI 1300 F 460 | 1123 |
| SAMI 1850 F 460 | 1034 |
| SAMI 1400 F 500 | 1143 |
| SAMI 2000 F 500 | 1039 |
| SAMI 1550 F 575 | 1123 |
| SAMI 2200 F 575 | 1086 |
| SAMI 1800 F 660 | 1111 |
| SAMI 2500 F 660 | 1097 |
| SAMI 1800 F 690 | 1111 |
| SAMI 2500 F 690 | 1147 |
| SAMI 1000 F 500 | 1039 |
| SAMI 1370 F 690 | 1047 |

T	257	101	0	0		UCVOLTAGE

DC voltage (in volts) measured by

the inverter.

TEE	258	102	3000	0		UCMEASURED_ON_BUS

A DC intermediate circuit voltage

(in volts) measured by a voltmeter

is set to this address in calibrating

the Uc meas urement.

T	259	103	0	0		UCNOMINAL

The DC voltage rated value

expressed in volts.

Start-up of the Uc-voltage

calibration.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	260	104				FIND_UC_OFFSET

0 = no calibration

1 = calibrates Uc measurement.

Automatically reset after the

calibration.

T	261	105	0	0		UCOFFSET

Offset computed by the Uc

calibration circuit.

100 = 1 %.

T	262	106	0	0		IROFFSET

Offset computed by the current

measurement calibration circuit.

10 = 1 %.

T	263	107	0	0		ISOFFSET

Offset computed by the current

measurement calibration circuit.

10 = 1 %.

T	264	108	0	0		L1STATUS

H/W status word of  serial data

communications channel 1.

T	265	109	0	0		L2STATUS

H/W status word of  serial data

communications channel 2.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	266	10A	0	0		HWFAULTS1

Counter of parity check error

messages in serial data

communications channel 1.

T	267	10B	0	0		HWFAULTS2

Counter of parity check error

messages in serial data

communications channel 2.

T	268	10C	0	0		BCCERRORS1

Counter of BCC error messages in

serial data communications

channel 1.

T	269	10D	0	0		BCCERRORS2

Counter of BCC error messages in

serial data communications

channel 2.

T	270	10E	0	0		FORMATERRORS1

Counter of format error messages in

serial data communications

channel 1.

T	271	10F	0	0		FORMATERRORS2

Counter of format error messages in

serial data communications

channel 2.

T	272	110	0	0		EEPROMSUCCES

Counter of the EEPROM circuit

number of updatings.

T	273	111	0	0		EEPROMFAILED

Counter of the EEPROM circuit

number of failed updatings.

T	274	112	0	0		CURRENTBALANCE

Asymmetry of output currents.

10 = 1 %.

TEE	275	113	3000	50	150	E_S_LIMIT

Triggering limit for short-circuit and

earth-fault tests.

1000 = rated current.

TEE	276	114	1000	0	50	UCFILT_FTR

Uc measurement filter time constant

expressed in ms.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	277	115	0	0		UCFILT

Filtered actual value of Uc

measurement. 1000 = rated value.

T	278	116	0	0		UC

Uc measurement result from A/D

converter. 178 = rated value.

T	279	117	0	0		IA

Current in X-Y coordinates.

T	280	118	0	0		IB

Current in X-Y coordinates

T	281	119	0	0		INTDIRECTION

Direction of integration process.

0 = no integration

1 = increase of frequency

absolute value

2 = decrease of frequency absolute

value

T	282	11A	0	0		UCEMF

Correction of the Uc voltage

comparative voltage reference.

T	283	11B	0	0		UFIRUREF

Output of the voltage reference

maximum selector.

T	284	11C	0	0		NORMALUREF

Output of the voltage reference

minimum selector.

T	285	11D	0	0		SCALEDMAXVOLTAGE

Maximum voltage reference of the

modulator.

16125 = 100 %.

T	286	11E	0	0		EMFVECTOR

Fundamental voltage reference

value. 16125 = 100 %.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	287	11F	0	0		UFIR

Voltage reference value computed

by the IR compensation circuit.

16125 = 100 %.

T	288	120	0	0		FLSTARTUREF

Voltage reference value computed

by the running start circuit.

16125 = 100 %.

T	289	121

TEE	290	122	20000	0	1500	BAL_FREQ_LIMIT

Above this frequency limit the

current unsymmetry

CURRENTBALANCE 274T will be

calculated.

1000 = 10 Hz

T	291	123

T	292	124

T	293	125

T	294	126

T	295	127	0	0		ROWSPEEDREF2

Output of the speed integrator

before the rounding function.

Scaling: 20000 = DRIVESPEEDMAX

T	296	128	0	0		DROOPING

Output of the speed controller

drooping. Scaling: 200 = 1 %.

T	297	129	0	0		ACC_COMP

Output of the speed control

acceleration compensation.

Scaling: 50 = 0.5 Hz.

T	298	12A	0	0		FREQDROOP

Output of the frequency control

drooping.

Scaling: 10 = 0.1 Hz.

T	299	12B

TEE	300	12C	500	0	150	SPEEDSLIPMAX

High limit for speed controller

output.

Scaling: 80 = 0.8 Hz.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	301	12D	0	-500	-150	SPEEDSLIPMIN

Low limit for speed controller output.

-80 = -0.8 Hz.

T	302	12E

T	303	12F	0	0		SAMIDATA

The latest received data in serial

data communications channel 1

having a proper format.

T	304	130	0	0		SAMIADDR

Address of the above.

T	305	131	0	0		SAMIDATA1

The latest received, checked and

accepted data in serial data

communications channel 1.

T	306	132	0	0		SAMIADDR1

Address of the above.

T	307	133	0	0		SAMIDATA2

As for 303T, but in channel 2.

T	308	134	0	0		SAMIADDR2

As for 304T, but in channel 2.

T	309	135	0	0		SAMIDATA3

As for 305T, but in channel 2.

T	310	136	0	0		SAMIADDR3

As for 306T, but in channel 2.

T	311	137	0	0		NEGNTACHO

Counter of negative tachometer

pulses.

T	312	138	0	0		POSNTACHO

Counter of positive tachometer

pulses.

T	313	139

T	314	13A

T	315	13B

T	316	13C

T	317	13D

T	318	13E

T	319	13F

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	320	140	0	0		TREND1_FETCH

All 100 samples of trend 1 are

sequentially circulated through this

memory location so that the trend

content can be fed to the D/A

converter, for example. The sample

storage time in memory is 210 ms.

T	321	141	0	0		TREND2_FETCH for trend 2

T	322	142	0	0		TREND3_FETCH for trend 3

T	323	143	0	0		TREND4_FETCH for trend 4

T	324	144	0	0		TREND5_FETCH for trend 5

T	325	145	0	0		TREND6_FETCH for trend 6

T	326	146	0	0		TREND7_FETCH for trend 7

T	327	147	0	0		TREND8_FETCH for trend 8

T	328	148

T	329	149

T	330	14A	0	0	30	DEVICETYPE

Drive type:

21 = vector control

30 = scalar control

T	331	14B	0	0	404	REVISION

Software version number.

404 corresponds to version 4.04.

T	332	14C	0	0	5602	ERPOM-D17

Four most significant digits of the

storage code.

T	333	14D	0	0	0322	EPROM-D17

Four least significant digits of the

storage code.

T	334	14E	0	0	5602	ERPOM-D18

Four most significant digits of the

storage code.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	335	14F	0	0	0331	EPROM-D18

Four least significant digits of the

storage code.

T	336	150 	0	0		PARCOUNT

The highest address + 1 used by

the functional block software.

T	337	151	2	0	(1)	CP2_SERIAL_CH

Serial channel which is used to send

CP2 normal messages.

0 = not send

1 = channel 1

2 = channel 2

T	338	152

T	339	153

T	340	154

T	341	155

T	342	156

T	343	157

T	344	158

T	345	159	1000	0	900	DCBRAKECURRENT

Total current used in DC braking.

1000 = inverter rated current.

T	346	15A	600	1	60	DCBRAKETIME

Period time of DC braking.

1 = 1 s.

T	347	15B

T	348	15C

T	349	15D

T	350	15E

TEE	351	15F	2000	0	500	KP_IRE

Proportional gain of the torque

limiting controller.

TEE	352	160	1000	0	500	TI_IRE

Integral action term of the torque

limiting controller.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	353	161	10000	0	2000	STATORRESISTANCE

IRE correction factor for current

limiting control(generator operation).

TEE	354	162	1500	1100	1190	UCHIGH

High operation limit of the

Uc-overvoltage controller.

1000 = rated voltage.

TEE	355	163	1500	1100	1160	UCHIGHREF

Low operation limit of the

Uc-overvoltage controller.

1000 = rated voltage.

TEE	356	164	32000	0	2000	KP_UCHIGH

Gain of the high Uc-overvoltage

controller.

TEE	357	165	32000	0	400	KP_UCHIGHREF

Gain of the low Uc-overvoltage

controller.

TEE	358	166

TEE	359	167	4000	-4000	1600	IRESTABGAIN_VP1

Torque stabilization factor in the

range of approx. 60...200 Hz.

TEE	360	168	4000	-4000	1100	IRESTABGAIN_VP3

Torque stabilization factor in the

range of approx. 36...60 Hz.

TEE	361	169	4000	-4000	1600	IRESTABGAIN_VP5

Torque stabilization factor in the

range of approx. 25...36 Hz.

TEE	362	16A	4000	-4000	1600	IRESTABGAIN_VP7

Torque stabilization factor in the

range of approx. 20...25 Hz.

TEE	363	16B	4000	-4000	1600	IRESTABGAIN_VP9

Torque stabilization factor in the

range of approx. 10...20 Hz.

TEE	364	16C	4000	-4000	1600	IRESTABGAIN_VP11

Torque stabilization factor in the

range of approx. 0...10 Hz.

TEE	365	16D	998	0	960	IRESTABFACTOR

Time constant factor of the torque

stabilization.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	366	16E

TEE	367	16F	2000	0	1000	FLUXSTABGAIN

Flux stabilization gain in the range of

0...20 Hz.

TEE	368	170	998	0	960	FLUXSTABFACTOR

Time constant factor of the flux

stabilization.

T	369	171

TEE	370	172	10000	0	2000	UCSTABGAIN

Gain of the Uc stabilization.

TEE	371	173	998	0	960	UCSTABFACTOR

Time constant factor of the Uc

stabilization.

T	372	174

T	373	175

T	374	176

T	375	177

T	376	178

T	377	179

T	378	17A

T	379	17B	0	0		TORQCONTOUT

Torque controller output.

T	380	17C	0	0		IRECONTOUT

Output of the torque limiting

controller.

T	381	17D	0	0		UCCONTOUT

Output of the Uc-overvoltage

controller.

T	382	17E	0	0		TORQMAXCONTOUT

Output of the torque maximization

controller.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	383	17F	0	0		NETFAILCONTOUT

Output of the power loss controller.

T	384	180	0	0		FLYINGCONTOUT

Output of the running start block.

T	385	181	0	0		FREQIRESTAB

Output of the torque stabilization.

T	386	182	0	0		FREQUCSTAB

Output of the Uc stabilization.

T	387	183	0	0		UREFSTAB

Output of the flux stabilization.

T	388	184

T	389	185

TEE	390	186	2000	0	250	KP_TORQUE

Proportional gain of the torque

controller.

TEE	391	187	10000	0	150	TI_TORQUE

Integral action time of the torque

controller.

TEE	392	188	3000	12	40	SINUN_KVA

TEE	393	189	3000	1	58	IMOTN_A

TEE	394	18A	6000	0	0	MOT_THERM_TC

Thermal time constant of motor

TEE	395	18B	1000	0	400	MOT_THER_TORQ_0HZ

Max. continuous torque at 0Hz

TEE	396	18C	1000	0	900	MOT_THER_TORQ

Max. torque at 398TEE

T	397	18D			0	IPEAKCOUNT

Counter of hardware executed

short-time overcurrent releases.

TEE	398	18E	20000	0	4500	MOT_THER_FREQ

Limit of self ventilated motor which

below cooling ability decreases.

TEE	399	18F	130	0	120	CALC_MOT_TEMP_ALARM_LIM

Alarm limit of calculated mot.temp.

TEE	400	190	130	0	130	CALC_MOT_TEMP_TRIP_LIM

Tripping limit of calculated mot.temp.

T	401	191	0	0		CALC_MOTOR_TEMP

Calculated temperature of motor

T	402	192	0	0		IMOT_N

T	403	193	0	0		MOT_THER_CURR_0HZ

The highest continuous current at

0 Hz.

T	404	194

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	405	195			1	LEARNMODE

Definition of the IR-compensation

automatic search.

1 = search in each start-up. The

start-up current value is stored in

the memory.

0 = current value stored in the

memory is used in the start-up

process.

TEE	406	196	800	0	300	GEN_IRCOMPPOINT

Limit frequency below which the

voltage reference begins to rise

when the drive is in the generator

mode. GEN_IRCOMPPOINT

corresponds to the motor mode limit

IRCOMPPOINT 69TEE.

TEE	407	197	20000	0	500	IRCOMPLIMIT

High limit frequency for peak current

control of the IR compensation.

500 = 5 Hz.

TEE	408	198	10	1	1	IRFLUXSPEED

Rate of change of the voltage

reference value in the IR

compensation process.

T	409	199	0	0		AUTOTORQMAX

An additional voltage computed by

the automatic search of the

IR compen sation.

T	410	19A	0	0		IRLEVEL

Flux developing voltage in the

IR compensation.

161 = 1 %.

TEE	411 	19B	500	0	80	SLIPFREQ

Motor slip frequency.

80 = 0.8 Hz.

T	412	19C	0	0		IRCOMP

A voltage required by the

IR compensation at the zero

frequency. 161 = 1 %.

T	413	19D	0	0		IRCOMP2

A voltage required by the

IR compensation at the zero

frequency after limitation of the rate

of change. 161 = 1 %.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	414	19E	10	1	3	FLUXTIME

Flux developing time expressed in

seconds.

TEE	415	19F	5000	50	500	KP_IRCOMP

Proportional gain of the flux control

of the IR compen sation.

TEE	416	1A0	1000	10	100	TI_IRCOMP

Integral action term of the flux

control of the IR compensation.

TEE	417	1A1	30000	100	2000	TORQMAX_P

Proportional gain of the current

limiting control in the

IR compensation.

T	418	1A2	0	0		IPEAK_AD

Measured peak current value from

the A/D converter. Overcurrent limit

= approx. 200.

TEE	419	1A3	200	100	140	IPEAKLIMIT

A reference value of the current limit

control of the IR compensation.

T	420	1A4	8000	0		IRCOMPVOLTAGE

IR compensation is given directly as

an addition to voltage reference

when 420TEE <> 0

16125 = 100%

TEE	421	1A5	400	0	0	EMFMULTIPLY

T	422	1A6

TEE	423	1A7	400	0	70	PWDNSLIPGAIN

Gain factor for slip reduction in the

power loss control mode.

T	424	1A8	0	0		PWDNSLIPREDUCE

Slip reduction in the power loss

control mode.

T	425	1A9

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	426	1AA	30000	10	10000	PWDNFREQDEC

Basic ramp down time in the power

loss control mode.

TEE	427	1AB	5000	0	2000	PWDN_UCCONTROL_GAIN

Proportional gain of the Uc control

during power loss control mode.

TEE	428	1AC	10000	0	4000	PWDN_DGAIN

Derivative gain of the Uc control

during power loss control mode.

TEE	429	1AD	999	0	850	PWDN_FACTOR

Time constant factor of the

derivative action gain of the Uc

control during power loss

control mode.

TEE	430	1AE	30000	100	1100	PWDNTIME

Operating time of the power loss

control.

1000 = 1 s.

TEE	431	1AF	5000	0	2200	PWDNPOWEROFF

Power off factor at the beginning of

the power loss control mode.

TEE	432	1B0	1000	10	60	UCTHRESHOLD

Maximum rate of rise of the Uc at

mains supply recovery.

TEE	433	1B1	1100	700	825	PWDN_UCALARM

Power loss control mode activation

level.

1000 = rated voltage.

T	434	1B2	0	0		PWDN_UCREF

Uc-voltage reference value in the

power loss control mode.

T	435	1B3	0	0		PWDNACTIVE

Status of power loss control.

0 = no control

<>0 = control ON

T	436	1B4	0	0		PWDN_UCALARM_TO_AD

Power loss control mode activation

level at the A/D converter.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	437	1B5

T	438	1B6	0	0		PWDNSUCCES

An average Uc-voltage error during

a power failure.

TEE	439	1B7	0	0		NETFAILCOUNTER

Counter of power failures.

TEE	440	1B8				PROTOCOL_SEL

Selection of communications

protocol for serial channel 2.

0 = SAMI protocol

1 = Fast protocol

TEE	441	1B9				SENDADDR

Address of the transmitted data.

0 = no transmission

0 = address of the transmitted

data.

TEE	442	1BA				SENDMUL

Scaling factor of the transmitted

data.

TEE	443	1BB				SENDDIV

Divisor of the transmitted data.

0 = no scaling

1 = divisor

TEE	444	1BC				RESADDR

Receiving address

0 = no reception

1 = address for storing the received

data.

TEE	445	1BD				RESMUL

Scaling factor of the received data.

TEE	446	1BE				RESDIV

Divisor of the received

TEE	447	1BF				MAXDELTA

Maximum allowed change between

two consecutively received data.

TEE	448	1C0				ID_NR

SAMI identification number.

In Fast-protocol transmission, the

Master SAMI sends the ID_NR to

the Slaves.

0 = identification number not sent

0 = identification number sent

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	449	1C1				ID_ACT

Identification number received by

the Slave SAMI in Fast-protocol

transmission

T	450	1C2

TEE	451	1C3

TEE	452	1C4				D_A3REFADDR

Reference voltage address of the

D/A converter (SAFT 154 DAC)

channel 3.

TEE	453	1C5			224	D_A3ADDR

Address of the variable monitored

by means of the channel 3 of the

D/A converter.

TEE	454	1C6			3	D_A3SCALE

Scaling of the variable before

conversion to an 8-bit code.

Channel 3.

TEE	455	1C7			1	D_A3MODE

Mode of operation of the channel 3

of the D/A converter.

TEE	456	1C8				D_A4REFADDR

Reference voltage address of the

D/A converter (SAFT 154 DAC)

channel 4.

TEE	457	1C9			231	D_A4ADDR

Address of the variable monitored

by means of the channel 4 of the

D/A converter.

TEE	458	1CA			6	D_A4SCALE

Scaling of the variable before

conversion to an 8-bit code.

Channel 4.

TEE	459	1CB			1	D_A4MODE

Mode of operation of the channel 4

of the D/A converter.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	460	1CC	1	0		VARSLS

Selection of VARIABLE SLOPE

0 = not selected

1 = selected

T	461	1CD	3600	0		RATETD

Time from start after which variable

slope function will be activated.

1 = 1 s.

T	462	1CE	1000	1	1	TMS

External control speed reference

updating interval.

100 = 100 ms.

T	463	1CF

T	464	1D0

T	465	1D1

T	466	1D2

T	467	1D3

TEE	468	1D4	2000	0	100	IRETHRESHOLD

Threshold of the IRE minimum

search in the running start.

TEE	469	1D5	200	0	15	ZEROVOLTAGE

Increase of voltage at the zero

frequency in the running start

mode.  10 = 1 %.

TEE	470	1D6	5000	100	2000	FLYINGFLUXSPEED

Rate of rise of the voltage reference

to the rated U/f function after finding

of the frequency magnitude.

2000 = 2 s.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	471	1D7	0	0		FLSTARTACTIVE

Running start status.

0 = not activated

2 = increase of frequency (60TEE)

4 = increase of voltage (472TEE)

6 = decrease of frequency,

searching for synchronous frequency

8 = increase of voltage to the value

on the U/f characteristic

10 = when searching in the other

direction of rotation, the frequency

is brought down to the value

defined by FLYINGFREQMIN(473)

12 = increase of voltage 2

15% (472TEE)

14 = decrease of frequency 2

16 = flying start by means of a

tachometer

TEE	472	1D8	40	10	15	FLSTARTVOLTAGE

Voltage reference value in the

running start mode.

15 = 15 %.

TEE	473	1D9	600	5	300	FLYINGFREQLIMIT

Absolute value of the running start

low limit frequency. 300 = 3 Hz.

TEE	474	1DA	600	50	200	FLYINGGAIN

Running start search rate.

T	475	1DB	100	0	20	FLYINGIRELIMIT

Synchronous frequency

identification level. When IRE goes

below this limit during running start,

the synchronous frequency is found.

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	476	1DC

T	477	1DD

T	478	1DE				MODSEL

Selection of the modulation type.

1 = When the voltage reference

is above 80% level and the

frequency reference below 61 Hz,

about 3% higher output voltage

is produced compared to the

previous modulator. Due to the

change, a higher output voltage

is obtained while the supply

voltage is low.

0 = The same modulator as in

versions SAFRSC 4.04A and B.

T	479	1DF	0	0		IREC

An IRE value corrected for IREMIN

control by means of the stator

resistance.

T	480	1E0

T	481	1E1	0	0		IDFILT

Filtered active current before

cosphi scaling.

T	482	1E2	0	0		IQFILT

Filtered reactive current.

T	483	1E3	0	0		IREMAX1

Torque limit of the motor side used

by the control circuit.

T	484	1E4

TEE	485	1E5	20	0	4	IREFTR_FAST

IRE filtering time constant in the

running start and in the power loss

control mode. 5 = 15 ms.

TEE	486	1E6	100	2	10	IREFTR_SLOW

IRE filtering time constant in

normal run.

10 = 30 ms.

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	487	1E7	10000	100	2000	INTEGUP

Integrator S-curve gain in ramp up

function. Increase of the value

reduces the duration of the

rounding function.

TEE	488	1E8	10000	100	800	INTEGDOWN

Integrator S-curve gain in ramp

down function. Increase of the

value reduces the duration of the

rounding function.

TEE	489	1E9	300	0	200	HIGHVOLTAGEHYST

Hysteresis of the modulator's

minimum pulse at a voltage

reference above the 83 % level.

100 = one minimum pulse.

T	490	1EA	0	0		HIGHVOLTAGE

Status of the modulator's minimum

pulse hysteresis.

200 = voltage reference is above

83 % level

0= voltage reference is below 83

% level

T	491	1EB	0	0		TD1

Time value of the modulator.

T	492	1EC	0	0		TD2

Time value of the modulator.

T	493	1ED	0	0		TD3

Time value of the modulator.

T	494	1EE	0	0		MODULSYNC

Modulator synchronization.

255=	synchronous

0=	asynchronous

T	495	1EF	0	0		MODULTYPE

Modulation type.

255=	high-level modulation

0=	low-level modulation

TYP	D	H	High Limit	Low Limit	Init	Explanation

T	496	1F0	0	0		VPACT

Slice number of the modulator.

11= asynchronous

9 low-level modulation

7= synchronous

high-level modulation

5

3

1

T	497	1F1	0	0		SLIPTIME

Internal measuring point of the

modulator.

T	498	1F2	0	0		ANGLE

Angle of the modulator voltage

vector.

0 = 0°

1536 = 360°

T	499	1F3	0	0		FULLVOLTAGE

Modulator status flag.

200 = maximum output voltage

0= output voltage lower than

maximum voltage

TM	500	1F4				TRENDBUF1

500TM...599TM trend range of the

measuring point defined by

191TEE.

TM	599	257

TM	600	258				TRENDBUF2

600TM...699TM trend range of the

measuring point defined by

192TEE.

TM	699	2BB

TYP	D	H	High Limit	Low Limit	Init	Explanation

TM	700	2BC				TRENDBUF3

700TM...799TM trend range of the

measuring point defined by 193TEE.

TM	799	31F

TM	800	320				TRENDBUF4

800TM...899TM trend range of the

measuring point defined by 194TEE.

TM	899	383

TM	900	384				TRENDBUF5

900TM...999TM trend range of the

measuring point defined by 195TEE.

TM	999	3E7

TM	1000	3E8				TRENDBUF6

1000TM...1099TM trend range of

the measuring point defined by

241TEE.

TM	1099	446

TM	1100	447				TRENDBUF7

1100TM...1199TM trend range of

the measuring point defined by

242TEE.

TM	1199	4AF

TM	1200	4B0				TRENDBUF8

1200TM...1299TM trend range of

the measuring point defined by

243TEE.

TM	1299	513

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	2250	8CA	143	32	32	UNIT_NR

Unit number of SAMI in Fieldbus.

= 32 * bus_nr + node_nr.

E.g. Bus number = 1,

node number = 5

UNIT_NR = 32 * 1 + 5 = 37

TEE	2251	8CB	2	1	2	SAMI_SER_CH

Number of SAMIs serial channel

where SamiNode is connected.

TEE	2252	8CC	32767	0	200	REFRES_IVAL

Normally SamiNode sends to SAMI

a signal when the data of the signal

is changing.

If the data does not change the

signals will be send with an interval

REFRES_IVAL. Unit is in 20 ms.

TEE	2254	8CE	2500	0	214	PBIND1_ADDR

The address of signal PBIND1.

TEE	2255	8CF	32767	-32768	20	PBIND1_IVAL

The transmission interval of

PBIND1. Unit in 24 ms.

TEE	2256	8D0	2500	0	210	PBIND2_ADDR

See 2254TEE.

TEE	2257	8D1	32767	-32768	20	PBIND2_IVAL

See 2255TEE.

TEE	2258	8D2	2500	0	211	PBIND3_ADDR

See 2254TEE

TEE	2259	8D3	32767	-32768	20	PBIND3_IVAL

See 2255TEE

TEE	2260	8D4	2500	0	212	PBIND4_ADDR

See 2254TEE

TEE	2261	8D5	32767	-32768	20	PBIND4_IVAL

See 2255TEE

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	2262	8D6	2500	0	0	PBIND5_ADDR

See 2254TEE

TEE	2263	8D7	32767	-32768	0	PBIND5_IVAL

See 2255TEE

TEE	2264	8D8	2500	0	0	I4IND1_MSW_ADDR

See 2254TEE

TEE	2265	8D9	32767	-32768	0	I4IND1_MSW_IVAL

See 2255TEE

TEE	2266	8DA	2500	0	0	I4IND1_LSW_ADDR

See 2254TEE

TEE	2267	8DB	32767	-32768	0	I4IND1_LSW_IVAL

See 2255TEE

TEE	2268	8DC	2500	0	208	RIND1_ADDR

See 2254TEE

TEE	2269	8DD	32767	-32768	15	RIND1_IVAL

See 2255TEE

TEE	2270	8DE	2500	0	0	RIND2_ADDR

See 2254TEE

TEE	2271	8DF	32767	-32768	0	RIND2_IVAL

See 2255TEE

TEE	2272	8E0	2500	0	201	RIND3_ADDR

See 2254TEE

TEE	2273	8E1	32767	-32768	15	RIND3_IVAL

See 2255TEE

TEE	2274	8E2	2500	0	0	RIND4_ADDR

See 2254TEE

TEE	2275	8E3	32767	-32768	0	RIND4_IVAL

See 2255TEE

TEE	2276	8E4	2500	0	0	RIND5_ADDR

See 2254TEE

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	2277	8E5	32767	-32768	0	RIND5_IVAL

See 2255TEE

TEE	2278	8E6	2500	0	0	RIND6_ADDR

See 2254TEE

TEE	2279	8E7	32767	-32768	0	RIND6_IVAL

See 2255TEE

TEE	2280	8E8	2500	0	0	RIND7_ADDR

See 2254TEE

TEE	2281	8E9	32767	-32768	0	RIND7_IVAL

See 2255TEE

TEE	2282	8EA	2500	0	0	RIND8_ADDR

See 2254TEE

TEE	2283	8EB	32767	-32768	0	RIND8_IVAL

See 2255TEE

TEE	2284	8EC	2500	0	0	RIND9_ADDR

See 2254TEE

TEE	2285	8ED	32767	-32768	0	RIND9_IVAL

See 2255TEE

Parameters 2295TEE...2312TEE

content can be address to which

SAMI will send the respective signal.

TEE	2286.....2294

TYP	D	H	High Limit	Low Limit	Init	Explanation

TEE	2295	8F7	255	-2500	47	PBORD1_ADDR

TEE	2296	8F8	255	-2500	0	PBORD2_ADDR

TEE	2297	8F9	255	-2500	0	I4ORD1_MSW_ADDR

TEE	2298	8FA	255	-2500	0	I4ORD1-LSW_ADDR

TEE	2299	8FB	255	-2500	46	RORD1_ADDR

TEE	2300	8FC	255	-2500	0	RORD2_ADDR

TEE	2301	8FD	255	-2500	0	RORD3_ADDR

TEE	2302	8FE	255	-2500	0	RORD4_ADDR

TEE	2303	8FF	255	-2500	0	RORD5_ADDR

TEE	2304	900	255	-2500	0	RORD6_ADDR

TEE	2305	901	255	-2500	0	RORD7_ADDR

TEE	2306	902	255	-2500	0	RORD8_ADDR

TEE	2307	903	255	-2500	0	RORD9_ADDR

TEE	2308	904	255	-2500	0	RORD10_ADDR

TEE	2309	905	255	-2500	0	RORD11_ADDR

TEE	2310	906	255	-2500	0	RORD12_ADDR

TEE	2311	907	255	-2500	0	RORD13_ADDR

TEE	2312	908	255	-2500	0	RORD14_ADDR

TEE	2313...2350

TEE	2351	92F	3	0	0	SAMINODECOMM

Operation in communication error:

0 = no effect

1 = displayed on panel

2 = displayed and stopped the

inverter with integrator.

3 = displayed and stopped the

inverter immediately.

28.	GENERAL BLOCK DIAGRAM (57777931)

29.	IDENTIFICATION OF THE MEMORY CIRCUITS

The EPROM and EEPROM memory circuits located on the SAFT 187 CON inverter control card are selected in accordance with the application.  The circuits are identified by means of their identification codes.  The memory circuits of other cards (e.g. Interface Card, control card of the control panel) used by the inverter are also identified by means of the code.

IDENTIFICATION CODE

SAFR _ _ _______ _

! !    !    !___ Version identification letter

! !    !

! !    !________ Version number

! !

! !_____________ Extent of software

!			    C =	single/sectional drive,

!				standard version

!			    D =	testing version

!

!

!_______________ Control mode

S =	scalar control

V =	vector control

L =	LGU mode

T =	SAFT 188 IOC interface board

C =	SAFP 21 PAN control panel

In addition to the identification code, every memory circuit is provided with an 8-digit numeric code.  Circuits with the same code are interchangeable so that circuits of the previous version can be replaced with a new circuit.  A version number is altered when the new version is functionally different from the old one.  A version identification letter is altered when in the new version an error has been corrected without any functional changes.

30.	SOFTWARE REVISIONS

30.1	Changes in the scalar control software

SAFRSC4.04 A

D17 and D18

New version:

SAFRSC4.04 B

D17 and D18

Changes:

The false start state diagnostics data with power connection card

SAFT 190 APC and auxiliary power card SAFT 192 POW.

-	SAMISTATUS 214T bit 5 (xxxx xxxx xx1x xxxx)

0 = the false start is inactive

1 = the false start is active

-	FAULTWORD2 212TM bit 7 (xxxx xxxx 1xxx xxxx)

0 = the start up inhibited is inactive

1 = the start up inhibited is active

-	FAULTWORD0 210TM is set to zero (0)

-	FAULTWORD1 211TM is set to zero (0)

-	SA 58 is displayed on the control panel CP1 (SAFP 11 PAN)

-	START INHIBIT is displayed on the control panel CP2 (SAFP 21 PAN)

-	IR-compensation with constant voltage (IRCOMPSEL 85TEE = 1 and

IRCOMPVOLTAGE 420TEE < > 0)

Voltage boosting is made using speed defined by the parameter

IRFLUXSPEED 408TEE without flux generation time FLUXTIME 414TEE.

SAFRSC4.04 B

D17 and D18

New version:

SAFRSC4.04 C

D17 and D18

Changes:

New parameter MODSEL 478TEE

478TEE = 1 ; New modulation (initial value)

About 3% higher output voltage is produced when voltage

reference is above 80% and frequency reference is below 61 Hz.

Now is possible to get higher motorvoltage also, when main

supply voltage is low.

= 0 ; Modulation is same as in version SAFRSC 4.04A and

SAFRSC 4.04B.

New initial value for the parameter IRESTABGAIN_VP3 360TEE

old value 1600 new value 1100.

New scaling factor for the current measurement

old scaling factor 2.42 new scaling factor 2.33

SAFRSC 4.04C

New version:

SAFRSC4.04 D

D17 and D18

Changes:

Malfunction occured when the software version SAFRSC4.04A,B or C are

used with control panel SAFP 11PAN(CP1)

Malfunction:

When parameters P500...P1299(trend area) are setted by the control panel

SAFP 11PAN the following malfunctions will be occured:

-	Control panel SAFP 11 PAN stopped the operation.

-	The serial communication stopped on the channel CH1 and CH2.

-	SAMI stopped the modulation.

The fault situation can only reset by power off operation.

Malfunction has been corrected in the version SAFRSC4.04D.

SAFRSC4.04D

D17 and D18

New version:

SAFRSC4.04E

D17 and D18

Changes:

Initial value of the parameter E_S_LIMIT 275TEE has been changed.

P275: Old value 100 New value 150

Initial value of the parameters IRCOMPCURRENT 70TEE and

IPEAKLIMIT 419TEE has been changed.

P70: Old value 500  New value 300

P419: Old value 160  New value 140

New parameter COSFIIFACTOR 76TEE

Malfunction in the False Start Inhibition diagnostic software corrected.

When the False Start Inhibition was activated for short time 1....7 s then

incorrect phase faults were generated.

Parameters are stored to the EEPROM memory only when EEPROMLOCK

8T = 1.

Motor thermal model added for supervision of the motor load.

New parameter I_MULTIPLY 256TEE

In the following SAMI STAR type scaling factor value is set according to

inverter type:

| TYPE | I_MULTIPLY 256TEE |
| --- | --- |
| SAMI 1100 F 380 | 1145 |
| SAMI 1500 F 380 | 1053 |
| SAMI 1100 F 400 | 1145 |
| SAMI 1600 F 400 | 1039 |
| SAMI 1100 F 415 | 1145 |
| SAMI 1650 F 415 | 1046 |
| SAMI 1230 F 440 | 1139 |
| SAMI 1750 F 440 | 1045 |

| TYPE | I_MULTIPLY 256TEE |
| --- | --- |
| SAMI 1300 F 460 | 1123 |
| SAMI 1850 F 460 | 1034 |
| SAMI 1400 F 500 | 1143 |
| SAMI 2000 F 500 | 1039 |
| SAMI 1550 F 575 | 1123 |
| SAMI 2200 F 575 | 1086 |
| SAMI 1800 F 660 | 1111 |
| SAMI 2500 F 660 | 1097 |
| SAMI 1800 F 690 | 1111 |
| SAMI 2500 F 690 | 1147 |
| SAMI 1000 F 500 | 1039 |
| SAMI 1370 F 690 | 1047 |

Overcurrent tripping based on software.

In the following SAMI STAR type over current trip is made by the software

after first short time overcurrent release:

| TYPE | TYPE | TYPE |
| --- | --- | --- |
| SAMI 500 F 380/400/415 |
| SAMI 630 F 380/400/415 | SAMI 1400 F 500 | SAMI 1550 F 575 |
| SAMI 1100 F 380/400/415 | SAMI 2000 F 500 | SAMI 2200 F 575 |
| SAMI 800 F 380 | SAMI 555 F 440 | SAMI 800 F 660 |
| SAMI 1500 F 380 | SAMI 700 F 440 | SAMI 1000 F 660 |
| SAMI 830 F 400 | SAMI 900 F 440 | SAMI 1370 F 660 |
| SAMI 1600 F 400 | SAMI 1230 F 440 | SAMI 1800 F 660 |
| SAMI 860 F 415 | SAMI 1750 F 440 | SAMI 2500 F 660 |
| SAMI 1650 F 415 | SAMI 580 F 460 | SAMI 800 F 690 |
| SAMI 630 F 500 | SAMI 730 F 460 | SAMI 1000 F 690 |
| SAMI 800 F 500 | SAMI 950 F 460 | SAMI 1370 F 690 |
| SAMI 1000 F 500 | SAMI 1300 F 460 | SAMI 1800 F 690 |
| SAMI 1850 F 460 | SAMI 870 F 575 | SAMI 2500 F 690 |
| SAMI 700 F 575 | SAMI 1200 F 575 |

LABEL

A memory circuit is labelled as follows:

-	identification code

-	code on the circuit diagram

-	jumper S5 and S6 for selection of size of EPROM.

-	storage code

-	date

ÚÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄ¿

³SAFRSC4.04 E     ³

³D17       S5=A-C  ³

³56020322  94MMDD  ³

ÀÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÙ

ÚÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄ¿

³SAFRSC4.04 E     ³

³D18       S6=A-C  ³

³56020331  94MMDD  ³

ÀÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÄÙ

Annex 1

Figure 5812 4427/02

NOTES