ACRONYM CMS-100 PS series / Current sensor

# GENERAL INFORMATION

Sensors are necessary components of the measuring system, since they collect and send information form the electrical cables. Sensors should be able to measure all types of current, whether AC, DC or mixed, in TRMS, enabling exact and effective measurements.

Every sensor should be equipped with a signal microprocessor, as measurement data could be transmitted digitally trough the CMS-bus interface to the control unit, reducing, as a consequence, the the number of cables into the distribution units and maximizing the security of the transmitted measurement values.

Current sensor should be integrated in all instalation devices with cylinder lift terminals.

Sensors should be installed one-by-one even at a later date, guaranting the most flexible mounting suitable for every enviroment solution.

The range of sensor should be flexible to every kind of installation. To integrate the sensors within PDUs there must be four different mounting variants available.

The The size of sensors must be contained in order to not waste space, not exceeding 25 mm width.

The range from which sensors must be selected should be varied. They can be divided in different groups depending on:

- Shape:

  - Open-core sensor

  - Closed-core sensor

- Tipe of application:

  - System pro M, SMISSLINE: For all LS, FI 6 FI-LS with twin terminals

  - S800: For all S800 devices with cage terminals

  - DIN rail: Universally usable

  - Cable tie: Universally usable

- Overall dimension:

  - 18-mm overall width

  - 25-mm overall width

- Mesasurement range:

  - Measuremnet range: 20 A, 40 A, 80 A, 160 A

The Table 1.1 resumes the total range of possible sensors, classified in according to shape, type of application and overall dimension:

| Sensors | System pro M, SMISSLINE | S800 | DIN rail | Cable tie |
| --- | --- | --- | --- | --- |
|  | For all LS, FI 6 FI-LS with twin terminals | For all S800 devices with cage terminals | Universally usable | Universally usable |
| Open-core sensors |  |  |  |  |
| 18-mm overall width | CMS-120PS CMS-121PS CMS-122PS | - | CMS-120DR CMS-121DR CMS-122DR | CMS-120CA CMS-121CA CMS-122CA |
| Solid-core sensors |  |  |  |  |
| 18-mm overall width | CMS-100PS CMS-101PS CMS-102PS | CMS-100S8 CMS-101S8 CMS-102S8 | CMS-100DR CMS-101DR CMS-102DR | CMS-100CA CMS-101CA CMS-102CA |
| 25-mm overall width | - | CMS-200S8 CMS-201S8 CMS-202S8 | CMS-200DR CMS-201DR CMS-202DR | CMS-200CA CMS-201CA CMS-202CA |

Table 1.1

Open-core sensors

In the open-core sensors cables are directly insert without using a screwdriver, guaranting a faster cabling.

The open-core sensors should be able to measure all types of current, whether AC, DC or mixed, up to 80 A in TRMS, enabling exact and effective measurements.

The open-core senors are available in 18 mm width.

The open-core sensors could be installed in all kind of application, except for all S800 devices with cage terminals.

In the Table 1.2 there are listed the whole range of possible open-core sensors, divided into type of application and mesasurement range:

| Open-core sensors | System pro M, SMISSLINE | S800 | DIN rail | Cable tie |
| --- | --- | --- | --- | --- |
| Measuremnet range | For all LS, FI 6 FI-LS with twin terminals | For all S800 devices with cage terminals | Universally usable | Universally usable |
| 18 mm overall width | 80 A | CMS-120PS | - | CMS-120DR | CMS-120CA |
|  | 40 A | CMS-121PS | - | CMS-121DR | CMS-121CA |
|  | 20 A | CMS-122PS | - | CMS-122DR | CMS-122CA |

Table 1.2

Solid-core sensors

In the solid-core sensors cables are closed inside the core, guaranting a secure insertion.

The solid-core sensors should be able to measure all types of current, whether AC, DC or mixed, up to 160 A in TRMS, enabling exact and effective measurements.

The solid-core senors are available in 18 mm and 25 mm width.

The solid-core sensors could be installed in all kind of application.

In the Table 1.3 there are listed the whole range of possible open-core sensors, divided into type of application and mesasurement range:

| Solid-core sensors | System pro M, SMISSLINE | S800 | DIN rail | Cable tie |
| --- | --- | --- | --- | --- |
| Measuremnet range | For all LS, FI 6 FI-LS with twin terminals | For all S800 devices with cage terminals | Universally usable | Universally usable |
| 18 mm overall width | 80 A | CMS-100PS | CMS-100S8 | CMS-100DR | CMS-100CA |
|  | 40 A | CMS-101PS | CMS-101S8 | CMS-101DR | CMS-101CA |
|  | 20 A | CMS-102PS | CMS-102S8 | CMS-102DR | CMS-102CA |
| 25 mm overall width | 160 A | - | CMS-200S8 | CMS-200DR | CMS-200CA |
|  | 80 A | - | CMS-201S8 | CMS-201DR | CMS-201CA |
|  | 40 A | - | CMS-202S8 | CMS-202DR | CMS-202CA |

Table 1.3

# STANDARDS, MARKS, CERTIFICATION

The current sensor shall conform to the following international standards:

- Electrostatic discharge IEC/EN 61000-4-2

- Electromagnetic compatibility IEC/EN 61000-4-3, -4-4, -4-5, -4-6, -6-3, -6.4

# ELECTRICAL and MECHANICAL PROPERTIES

The current sensor should have the following mechanical and electrical properties that determine its use and employment:

- Measuring range:

  - Current input range: 20 A, 40 A, 80 A, 160 A

  - Method: TRMS, AC 50/60 Hz, DC

- Crest factor distorted wave forms: ≤ 1, ≤ 3 or ≤ 6

- Accuracy classes:

  - AC accuracy (TA = +25 °C):	≤ ±0.5 %

  - AC temperature coefficient: ≤ ±0.036 %/K

  - DC accuracy (TA = +25 °C):	≤ ±0.7 %, ≤ ±1 % or ≤ ±1.7 %

  - DC temperature coefficient: ≤ ±0.047 %/K, 0.059 %/K or 0.084 %/K

- Resolution: 0.01 A

- Internal sampling rate: 5000 Hz

- Settle time (±1 %): typ. 0.25 sec

- Cable feed through: 10 mm or 15 mm

- Insulation voltage: 690 V AC / 1500 V DC

- Weight: 12 g

- Overall dimensions:

CMS-100PS series [mm] 17.4 x 41.0 x 26.5

CMS-100S8 series [mm] 26.5 x 45.5 x 31.8

CMS-100DR series [mm] 17.4 x 51.5 x 43.2

CMS-100CA series [mm] 17.4 x 41.0 x 29.0

CMS-200S8 series [mm] 26.5 x 43.0 x 38.5

CMS-200DR series [mm] 25.4 x 43.0 x 43.2

CMS-200CA series [mm] 25.4 x 43.0 x 35.7

# ENVIRONMENTAL FEATURES

The current sensor may ensure the installation and storage under the following environmental conditions:

- Operating temperature –25 °C .. +65 °C

- Storage temperature –40 °C .. +85 °C

- Relative humidity max 80% at 31°C decreasing linearly to 50 % relative humidity at 40 °C