## 1st Sheet
PREPARED |  |  | STATUS | SECURITY LEVEL
ELSP Digital Operation |  |  | Published | Public
APPROVED |  |  | DOCUMENT KIND
Technical specification
TITLE
ABB AbilityTM - Electrification connectable devices
OWNING ORGANIZATION |  |  | DOCUMENT ID | REV. | LANG.
ABB Electrification Smart Power |  |  | 9AKK107991A2811 | X | EN
© Copyright 2022-2024 ABB. All rights reserved.
Revision | Sheet | Description |  | Date Dept./Name
N | 2 | Added special notes Compatibility matix updated |  | Oct. 20th 2022
O | 2 | Added e-kit PLC device Updated UPS section Added specific FW compatibility for each gateway model Added specific compatibility column for EL Industrial Gateway Local View |  | Dec. 1st 2022
P | 2 | Removed support for Digital Inputs and Temperarure in the E-Kit PLC compatibility |  | Dec. 7th 2022
Q | 2 | Added PSTX Added M4M 2X Updated E-Kit |  | Jan. 31st 2023
R | 2 | Added CPX-C Updated EQMatic notes Updates SCU100 notes Added Device Application scope |  | March. 1st 2023
S | 2 | Added CM-UFD M22M/M31M/M33M/M34M |  | March. 27th 2023
T | 2 | List of UPS has been consolidated Minor fixes |  | July. 18th 2023
U | 2 | CM-UFD M22 and M34 removed Updated M31M/M33M/M34M compatibility with Ekip Com Hub and Ekip E-Hub |  | August, 22nd 2023
V | 2 | Updated EQ Matic compatibility. FW 2.4.62 for EQ Matic Modbus is now required (click for the release notes) |  | September, 25th 2023
W | 2 | Update the list of devices supported by Asset Manager Please contact global-el.operations.digital@abb.com before starting any SWICOM related project |  | October, 25th 2023
X | 2 | Update M1M and ITS2.1 compatibility list |  | February, 5th 2024

## ABB connectable devices
ABB | 9AKK107991A2811 Rev X (R24Q1.1) | ABB AbilityTM - Electrification connectable devices
| Device | Electronic Unit | Additional modules and communication | Firmware | Device Application | Notes | Automatic Discovery | Ekip Com Hub | E-Hub 2.0 | ABB Ability ELIG Cloud | ABB Ability ELIG Local View | MyRemoteCare Gateway | Currents | Voltages | Frequency | Power | Energy | Power factor | Max I and P values | Measure history | Power quality | Temperatures | Total Number of operations | Number of trips | Number of trip tests | Contact wear | Number of Manual Operations | Protection alarms | Diagnostic alarms | Busbar temperature monitoring | Circuit Breaker joints temperature monitoring | Cable joints temperature monitoring | Circuit Breaker open/close coil monitoring | Circuit Breaker angle and position monitoring | Switchgear Partial Discharge Monitoring | Device Information | State information (open/close, alarms) | Pulse meters | Analog meters or inputs
Molded case | Tmax XT | EKIP LSI, LSIG | Ekip COM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [9 empty] | x | x | x | x | x | x | x | [6 empty] | x | x
|  | EKIP M-LRIU | Ekip COM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [9 empty] | x | x | x | x | x | x | x | [6 empty] | x | x
|  | EKIP LSI, LSIG | Ekip COM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [9 empty] | x | x | x | x | x | x | x | [6 empty] | x | x
|  | Ekip E | Ekip COM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  | x |  | x | x | x | x | x | x | x | [6 empty] | x | x
| T4 | PR222DS/PD |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [10 empty] | x | x | x | x | x | x | [6 empty] | x
|  | PR222DS/PD | AUX-E | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [9 empty] | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR223DS |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [5 empty] | x |  |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR223DS | VM10 | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
| T5 | PR222DS/PD |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [10 empty] | x | x | x | x | x | x | [6 empty] | x
|  | PR222DS/PD | AUX-E | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [9 empty] | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR223DS |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [5 empty] | x |  |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR223DS | VM10 | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | Ekip E (+COM) |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  | x |  |  | x | x | x | x | x | x | [6 empty] | x
|  | Ekip E (+COM) | AUX-E | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  | x |  | x | x | x | x | x | x | x | [6 empty] | x | x
| T6 | PR222DS/PD |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [10 empty] | x | x | x | x | x | x | [6 empty] | x
|  | PR222DS/PD | AUX-E | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [9 empty] | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR223DS |  | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [5 empty] | x |  |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR223DS | VM10 | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
| T7 | PR332 | PR330/DM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [5 empty] | x | x |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR332 | PR330/DM + PR330/V | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
| XT2 | Touch Measuring / Hi Touch | Modbus RTU / TCP | 03.00.40 3.22 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
| XT4 | Touch Measuring / Hi Touch | Modbus RTU / TCP | 03.00.40 3.22 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
| XT5 | Touch Measuring / Hi Touch | Modbus RTU / TCP | 03.00.40 3.22 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
| XT7 | Touch Measuring / Hi Touch | Modbus RTU / TCP | 03.00.40 3.22 | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
Airc Circuit Breaker | New Emax | PR122 | PR120/DM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [5 empty] | x | x |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR122 | PR120/DM + PR120/V | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x |  |  | x | x | x | x | x | x | x | [6 empty] | x | x
|  | PR123 | PR120/DM | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x
| Emax 2 | Ekip Touch | Ekip Supply + Ekip COM Modbus | 2.24.03 2.44 TCP / 1.19 RTU | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | [5 empty] | x | x |  |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
|  | Ekip Touch | Ekip Supply + Ekip COM Modbus + Ekip Measuring | 2.24.03 2.44 TCP / 1.19 RTU | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x |  |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
|  | Ekip Hi Touch | Ekip Supply + Ekip COM Modbus | 2.24.03 2.44 TCP / 1.19 RTU | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
|  | Ekip G-Touch | Ekip Supply + Ekip COM Modbus | 2.24.03 2.44 TCP / 1.19 RTU | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | [6 empty] | x | x |  | x
External Trip Unit | Ekip UP | Ekip UP Monitor | Ekip COM Modbus | 2.24.03 2.44 TCP / 1.19 RTU | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x | [7 empty] | x | [6 empty] | x | x |  | x
|  | Ekip UP Protect / Protect+ / Control+ | Ekip COM Modbus | 2.24.03 2.44 TCP / 1.19 RTU | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x |  |  | x | x |  |  | x | x | [6 empty] | x | x |  | x
External Trip Unit | Ekip UP+ | Ekip UP+ | Ekip COM Modbus | 3.22 3.23 TCP / 2.32 RTU | Energy Manager | - Predictive maintenance supported via Asset Manager with the LV CB health add-on | x | 3.35 |  | 1.22 |  |  | x | x | x | x | x | x | x | x | x | [7 empty] | x | [6 empty] | x | x |  | x
Switches and fusegear | TruONE ATS | Level 3 controls (LCD) | OXEA1 power supply + Ekip COM Modbus | 1.01.02 2.44 TCP / 1.19 RTU | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  |  | x | x | [7 empty] | x | [5 empty] | x | [6 empty] | x | x
|  | Level 4 controls (Touch) | OXEA1 power supply + Ekip COM Modbus | 1.01.02 2.44 TCP / 1.19 RTU | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  | x |  | x |  |  | x |  | x | x | [6 empty] | x | x
| ITS2 |  | Modbus RTU | 2.7 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.46 |  | x | x | x | x | x | x | x |  |  |  | x | [12 empty] | x | x
| ITS2.1 |  | Modbus RTU / TCP | 2.7 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  |  |  | x | [12 empty] | x | x
Digital inputs interface | Ekip Signalling MODBUS TCP | through digital inputs | Modbus TCP | 1.09 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 | [11 empty] | x | x | x |  | x | x | x | [6 empty] | x | x
Meters | EQ Meters | A41, A43, A44 | Modbus RTU | A1.19.0 | Energy Manager | - EQ Meter Steel series do not provide Reactive Power, Reactive Energy and non-istantaneous Power Factor | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x |  | x | x | x | x | [16 empty] | x
|  | B23, B24 |  | B1.28.0 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x |  | x | x | x | x | [16 empty] | x
|  | B21 |  | B10.12.0 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x |  | x | x | x | x | [16 empty] | x
| M1M | M1M 10 | Modbus RTU |  | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | x | x | [17 empty] | x
|  | M1M 11 | Modbus RTU |  | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | x | x | [17 empty] | x
|  | M1M 12 | Modbus RTU |  | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | x | x | [17 empty] | x
|  | M1M 15 | Modbus RTU |  | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | x | x | [17 empty] | x
|  | M1M 20 | Modbus RTU / TCP | 1.1.03 or newer | Energy Manager | - I/O module is not supported yet |  |  |  | 1.22 | 1.46 |  | x | x | x | x | x | x | [17 empty] | x
|  | M1M 30 | Modbus RTU / TCP | 1.1.03 or newer | Energy Manager | - I/O module is not supported yet |  |  |  | 1.22 | 1.46 |  | x | x | x | x | x | x |  |  | x | [14 empty] | x
|  | M1M 20B | Modbus RTU / TCP |  | Energy Manager | - I/O module is not supported yet |  |  |  | 1.22 |  |  | x | x | x | x | x | x |  |  | x | [14 empty] | x
|  | M1M 30B | Modbus RTU / TCP |  | Energy Manager | - I/O module is not supported yet |  |  |  | 1.22 |  |  | x | x | x | x | x | x |  |  | x | [14 empty] | x
|  | M1M C20 | Modbus RTU / TCP |  | Energy Manager | - I/O module is not supported yet - Only available for CN market |  |  |  | 1.22 |  |  | x | x | x | x | x | x |  |  | x | [14 empty] | x
|  | M1M C30 | Modbus RTU / TCP |  | Energy Manager | - I/O module is not supported yet - Only available for CN market |  |  |  | 1.22 |  |  | x | x | x | x | x | x |  |  | x | [14 empty] | x
| M2M |  | Modbus TCP | 2.2.6 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x | [14 empty] | x
|  |  | Modbus RTU | 2.2.5 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x | [14 empty] | x
| M4M | M4M | Modbus RTU / TCP | 1.3.10 | Energy Manager | - I/O module is not supported yet | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x | x | x | [14 empty] | x
|  | M4M 2X | Modbus RTU / TCP | 2.6.14 | Energy Manager | - I/O module is not supported yet | x |  |  | 1.22 |  |  | x | x | x | x | x | x | x | x | x | [14 empty] | x
| CMS700 |  | Upstream: Modbus TCP Downstream: N/A | 1.32 | Energy Manager |  | x | 3.35 | 1.17 | 1.24 | 1.35 |  | x | x | x | x | x |  | x | [16 empty] | x
| InSite Pro M/SCU100 |  | Upstream: Modbus TCP Downstream: Modbus RTU | 1.1.0 | Energy Manager | - New features introduced with FW 1.3.0+ are not supported - eOVR modules are not supported - EQ Meter Steel series are not supported as connected devices | x |  | 1.17 | 1.24 | 1.35 |  | x | x | x | x | x |  | x | [16 empty] | x | x | x
| EQMatic | QA/S 3.16.1 | Upstream: Modbus TCP Downstream: M-Bus | 3.0.0 | Energy Manager | - "KNX" variant not supported - FW updates from older versions might require a new commissioning | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x1 | x1 |  | x1 | x1
|  | QA/S 4.16.1 | Upstream: Modbus TCP Downstream: Modbus RTU | 2.4.62 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 |  | x1 | x1 |  | x1 | x1
PLC for third party device integration | E-Kit | PM5630 | Upstream: Modbus TCP Downstream: Modbus TCP and RTU | 1.0.5.0 | Energy Manager | - The list of pre-defined teplates for device integration is available via https://library.abb.com/d/1SDH002226A1001 - Third party devices integarion requires a System Integrator |  |  |  | 1.24 |  |  | x1 | x1 | x1 | x1 | x1 | x1 |  |  | x1 | x2 |  | x1 |  | x1 |  | x1 | x1 | [7 empty] | x2 | x2 | x1
Feeder Protection Relay | REF615 |  | Modbus TCP | 5.0 FP1 or newer | Energy Manager | - Modbus RTU is not supported - Reboot required after enabling Modbus TCP |  |  |  | 1.22 | 1.46 |  | x | x | x | x | x | x |  |  | x |  |  |  |  | x |  |  | x | [6 empty] | x
| REF620 |  | Modbus TCP | 2.0 FP1 or newer | Energy Manager | - Modbus RTU is not supported - Reboot required after enabling Modbus TCP |  |  |  | 1.22 | 1.46 |  | x | x | x | x | x | x |  |  | x |  |  |  |  | x |  |  | x | [6 empty] | x
| REF 5xx | REF 542 PLUS | Modbus TCP | Specific Configuration is Required | Energy Manager | - Required Modbus map available via https://library.abb.com/d/9AKK108467A5485 |  | 3.35 | 1.17 | 1.22 | 1.35 |  | x | x | x | x | x | x | x |  |  |  | x | [12 empty] | x
Grid feeding monitoring relay | CM-UFD | M22M | Modbus RTU | 1.0.3 | Energy Manager | - Firmware 1.1.x not supported | x | 3.35 | 1.17 | 1.22 | 1.35 |  |  | x | x | [8 empty] | x |  |  |  | x | x | [6 empty] | x | x
|  | M31M/M33M | Modbus RTU | 1.1.2 | Energy Manager |  | x | 3.35 | 1.17 | 1.22 |  |  |  | x | x | [8 empty] | x |  |  |  | x | x | [6 empty] | x | x
|  | M34M | Modbus RTU | 1.1.2 | Energy Manager |  |  | 3.35 | 1.17 | 1.22 |  |  |  | x | x | [8 empty] | x |  |  |  | x | x | [6 empty] | x | x
Arc protection relay | TVOC-2 |  | Modbus RTU | All versions | Energy Manager |  | x | 3.35 | 1.17 | 1.22 | 1.35 | [16 empty] | x | [7 empty] | X | X
Smart Monitoring Relay | CM-TCN.012 |  | Modbus RTU | 2.0.1 | Energy Manager |  | x | 3.35 |  | 1.22 | [11 empty] | x |  | x | [11 empty] | x
Motor controller | UMC 100.3 |  | Modbus TCP via PNU32 card MTQ22 card | 3.0.9 | Energy Manager | - Ekip Com Hub supports PNU32 only |  | 3.35 |  | 1.22 |  |  | x | x | x | x |  | x |  |  | x | [6 empty] | x | x | [6 empty] | x |  |  | x
Safety Switch | Panduit Smart Safety Switch |  | Modbus TCP via Network Module | 1.0.1 for network module 0.0.18 for AVT | Energy Manager | - Only available for NEMA market |  |  |  | 1.22 |  |  |  | x | [7 empty] | x | [13 empty] | x
Temperature monitoring | Johar wireless temperature sensors |  | Modbus RTU | 1.19 | Energy Manager | - Only available for CN market |  |  |  | 1.22 | [11 empty] | x | [13 empty] | x
PCS | PCS100/120 |  | Modbus TCP | 1.19 | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [19 empty] | x
Softstarter | PSTX |  | Modbus RTU | 1.41.1 | Energy Manager | - Only Modbus RTU is currently supported |  |  |  | 1.22 |  |  | x | x | x | [6 empty] | x | [6 empty] | x | [6 empty] | x
| CPX-C |  | Modbus RTU | 1.00 | Energy Manager | - Only available for CN market |  |  |  | 1.22 |  |  | x | x | x | [6 empty] | x | [6 empty] | x | [6 empty] | x
UPS | PowerLine DPA IEC |  | CS141 card | 2.04 for CS141 All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| PowerLine 33 IEC |  | CS141 card | 2.04 for CS141 All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| PowerValue 11 RT |  | CS141 card | 2.04 for CS141 All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| ConceptPower DPA IEC 400V |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA 240 UL 415V |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA 250 S4 IEC 300 kW UPS |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA 500 IEC 100 kW UPS |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA 500 UL 100 kW UPS |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA Upscale RI IEC 10-20 kW UPS |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA UPSCALE ST IEC 10-200 kW UPS |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| DPA UPScale ST TS8 IEC 10-120 kW UPS |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| MegaFlex IEC |  | ANC card | min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| PowerScale 33 IEC 400V |  | CS141 card or ANC card | 2.04 for CS141, All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| PowerWave 33 IEC 400V |  | CS141 card or ANC card | 2.04 for CS141 min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| SG Series IEC 400V |  | ANC-L or SNMP 5 card | min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| SG Series UL 480V |  | ANC-L or SNMP 5 card | min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| MegaFlex UL |  | ANC-L or SNMP 5 card | min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| TLE Series UL 480V |  | ANC-L or SNMP 5 card | min 1.0.6 for ANC All versions for UPS | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| PowerValue 11 RT G2 |  | ANC mini card | All versions | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
| PowerValue11 / 31 T |  | CS141 card | All versions | Energy Manager |  |  |  |  | 1.22 |  |  | x | x | x | x | [5 empty] | x | [13 empty] | x
MV Switchgear | SWICOM |  | Upstream: Modbus TCP Downstream: IEC61850 | 2.5.3 to 2.6.x | Asset Manager | - Please contact global-el.operations.digital@abb.com before starting any SWICOM related project |  |  |  | 1.24 | [12 empty] | x | x | x | x |  | x | x | x | x | x |  |  | x | x
Note on D96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Available in Q4'23

## REF615-620 Scaling calculator
ABB | REF615/620 measurement scaling factory calculator for ABB Ability Energy and Asset Manager
Fill the Yellow boxes based on your switchgear setup (Primary values) and Modbus scale factor settings as in PCM600 configuration.
The four calculated multiplier factor values shall be set in the ABB Ability Energy and Asset Manager portal, in the specfic REF asset page -> Settings page.
| Settings (PCM600) - Current measurements |  |  |  | Settings (PCM600) - Voltage measurements
| Primary Scale Factor in Use | No |  |  | Primary Scale Factor in Use | No |  | Yes | No
| Primary current (hide if "Yes") | 100 | A |  | Primary voltage (hide if "Yes") | 20000 | V
| Scale Factor | 1000 |  |  | Scale Factor | 1000
| Offset | 0 | must be 0 |  | Offset | 0 | must be 0
| Ability data model scale factor | 1000 |  |  | Ability data model scale factor | 1
→ | Current Multiplier factor | 100 |  | → | Voltage Multiplier factor | 20
| Settings (PCM600) - Power calculation |  |  |  | Settings (PCM600) - Energy calculation
| Primary Scale Factor in Use | No | not relevant |  | Primary Scale Factor in Use | No | not relevant
| Scale Factor | 1 |  |  | Scale Factor | 1
| Offset | 0 | not considered |  | Offset | 0 | not considered
→ | Power Multiplier factor | 1 |  | → | Energy Multiplier factor | 1
Test (Example)
| Test current measurement scaling |  |  | Primary current | 14.7 | A
|  |  |  | REF analog input (internal) | 0.147 | A
|  |  |  | REF Modbus register value | 147
|  |  |  | Ability value (internal) | 0.147
|  |  |  | Current as dispalyed on cloud UI | 14.7 | A
| Test voltage measurement scaling |  |  | Primary voltage | 2160 | V
|  |  |  | REF analog input (internal) | 0.108 | kV
|  |  |  | REF Modbus register value | 108
|  |  |  | Ability value (internal) | 108
|  |  |  | Voltage as dispalyed on cloud UI | 2160 | V
| Test power measurement scaling |  |  | Primary voltage | 31752 | kW
|  |  |  | REF Modbus register value | 31752
|  |  |  | Ability value (internal) | 31752
|  |  |  | Voltage as dispalyed on cloud UI | 31752 | kV
Feeder Protection and Control REF 615 - Modbus Point List Manual
615 Series - Modbus Communication Protocol Manual
PCM600 - Protection and control IED manager (web page)
Note on B7: PCM600 -> go to the REF -> right-click -> Communication Management -> select Modbus Search the Current registers (138, 139, 140) Copy the "Primary Factor in Use" value DEFAULT = No
Note on F7: PCM600 -> go to the REF -> right-click -> Communication Management -> select Modbus Search the Voltage registers (152,153,154 and 155,156,157) Copy the "Primary Factor in Use" value DEFAULT = No
Note on B8: PCM600 -> go to the REF -> IED Configuration -> Configuration -> Analog Inputs -> Parameter Setting Copy the Primary Current value
Note on F8: PCM600 -> go to the REF -> IED Configuration -> Configuration -> Analog Inputs -> Parameter Setting Copy the Primary Voltage value
Note on B9: PCM600 -> go to the REF -> right-click -> Communication Management -> select Modbus Search the Current registers (138, 139, 140) Copy the "Scale Factor" value DEFAULT = 1000
Note on F9: PCM600 -> go to the REF -> right-click -> Communication Management -> select Modbus Search the Voltage registers (152,153,154 and 155,156,157) Copy the "Scale factor" value DEFAULT = 1000
Note on B10: The offset value must be 0.
Note on F10: The offset value must be 0.
Note on B16: The Primary Scale factor in use is not relevant.
Note on F16: The Primary Scale factor in use is not relevant.

## SWICOM configuration calculator
SWICOM's devices combinations
Notes: | (*) 1 Relays = 1 CB (no multi-instances)
SWICOM support now the following relay versions:
o REX615 4.0 (it’s required a logical block modification)
o REX615 4.0 FP1 (it’s required a logical block modification)
o REX615 5.0
o REX615 5.0 FP1
o REX620 2.0 FP1
o REX640
SINGLE FUNCTIONALITY |  | MULTIPLE FUNCTIONALITY
Only Temp Reader (SenseOr/MDC4-M/Exertherm…) |  | CB Monitoring + PD Monitoring
|  | 1 SWICOM | Relion relays(*) ≤ 14 & PDCOM ≤ 2
1 SWICOM | Up to 24 Readers | 1 SWICOM | SenseOr's Readers (with PD function) ≤ 12 & Relion relays (*) ≤ 12
Only PD Monitoring (PDCOM) |  | Temp Monitoring + CB Monitoring
1 SWICOM | Up to 3 PDCOM | 1 SWICOM | SenseOr's Readers (Temp) ≤ 12 & Relion relays(*) ≤ 12
Only CB Monitoring (Relays) |  | 1 SWICOM | MDC4-M (Temp) ≤ 12 & Relion relays(*) ≤ 12
1 SWICOM | Up to 14 Relion relays (*) | Temp Monitoring + PD Monitoring
|  | 1 SWICOM | SenseOr's Readers (Temp) ≤ 24 & PDCOM ≤ 3
Temp Monitoring + PD Monitoring + CB Monitoring (from MDC4-M)
|  | 1 SWICOM | MDC4-M ≤ 14 (Temp + CB Monitoring) & PDCOM ≤ 2
Temp + PD Monitoring + CB Monitoring
|  | 1 SWICOM | Relion relays (*) ≤ 12 & SenseOr's Readers (Temp) ≤ 12 & PDCOM ≤ 2
|  | 1 SWICOM | Relion relays (*) ≤ 12 & MDC4-M ≤12 (Temp) & PDCOM ≤ 2