## Integer Table
Quantity/Functionality | Explanation | Unit | Resolution | Data Type | Access | Register (Hex) | Register (Dec) | No of registers | Product Type | Functional Block | Ekip/Epic Integration
Active energy + | import(consumption) | kWh | 0.01 | Unsigned | Read | 5000 | 20480 | 4 | M1M 15/20/30 | Energy values | Yes
Active energy - | export(generation) | kWh | 0.01 | Unsigned | Read | 5004 | 20484 | 4 | M1M 20/30 | Energy values | Yes
Reactive energy + | import(consumption) | kvarh | 0.01 | Unsigned | Read | 500C | 20492 | 4 | M1M 15/20/30 | Energy values | Yes
Reactive energy - | export(generation) | kvarh | 0.01 | Unsigned | Read | 5010 | 20496 | 4 | M1M 20/30 | Energy values | Yes
Apparent energy | import(consumption) | kVA | 0.01 | Unsigned | Read | 5018 | 20504 | 4 | M1M 15/20/30 | Energy values | Yes
Total Active energy - import (Tariffs) | Tariff from 1 to 4 | kWh | 0.01 | Unsigned | Read | 5170 | 20848 | 16 | M1M 30 I/O Pro | Energy values
Total Active energy - export (Tariffs) | Tariff from 1 to 4 | kWh | 0.01 | Unsigned | Read | 5190 | 20880 | 16 | M1M 30 I/O Pro | Energy values
Total Reactive energy - import (Tariffs) | Tariff from 1 to 4 | kvarh | 0.01 | Unsigned | Read | 51B0 | 20912 | 16 | M1M 30 I/O Pro | Energy values
Total Reactive energy - export (Tariffs) | Tariff from 1 to 4 | kvarh | 0.01 | Unsigned | Read | 51D0 | 20944 | 16 | M1M 30 I/O Pro | Energy values
Three phase system | Avg of Line voltage | V | 0.1 | Unsigned | Read | 5B00 | 23296 | 2 | M1M 15/20/30 | Real-Time values | Yes
Phase Voltage L1 |  | V | 0.1 | Unsigned | Read | 5B02 | 23298 | 2 | M1M 15/20/30 | Real-Time values | Yes
Phase Voltage L2 |  | V | 0.1 | Unsigned | Read | 5B04 | 23300 | 2 | M1M 15/20/30 | Real-Time values | Yes
Phase Voltage L3 |  | V | 0.1 | Unsigned | Read | 5B06 | 23302 | 2 | M1M 15/20/30 | Real-Time values | Yes
Line voltage L1-L2 |  | V | 0.1 | Unsigned | Read | 5B08 | 23304 | 2 | M1M 15/20/30 | Real-Time values | Yes
Line voltage L3-L2 |  | V | 0.1 | Unsigned | Read | 5B0A | 23306 | 2 | M1M 15/20/30 | Real-Time values | Yes
Line voltage L1-L3 |  | V | 0.1 | Unsigned | Read | 5B0C | 23308 | 2 | M1M 15/20/30 | Real-Time values | Yes
Three phase Current | Avg of Current | A | 0.01 | Unsigned | Read | 5B0E | 23310 | 2 | M1M 15/20/30 | Real-Time values | Yes
Current L1 |  | A | 0.01 | Unsigned | Read | 5B10 | 23312 | 2 | M1M 15/20/30 | Real-Time values | Yes
Current L2 |  | A | 0.01 | Unsigned | Read | 5B12 | 23314 | 2 | M1M 15/20/30 | Real-Time values | Yes
Current L3 |  | A | 0.01 | Unsigned | Read | 5B14 | 23316 | 2 | M1M 15/20/30 | Real-Time values | Yes
Current N |  | A | 0.01 | Unsigned | Read | 5B16 | 23318 | 2 | M1M 20/30 | Real-Time values | Yes
Active Power total |  | W | 0.01 | Signed | Read | 5B1A | 23322 | 2 | M1M 15/20/30 | Real-Time values | Yes
Active Power L1 |  | W | 0.01 | Signed | Read | 5B1C | 23324 | 2 | M1M 15/20/30 | Real-Time values | Yes
Active Power L2 |  | W | 0.01 | Signed | Read | 5B1E | 23326 | 2 | M1M 15/20/30 | Real-Time values | Yes
Active power L3 |  | W | 0.01 | Signed | Read | 5B20 | 23328 | 2 | M1M 15/20/30 | Real-Time values | Yes
Reactive Power total |  | VAR | 0.01 | Signed | Read | 5B22 | 23330 | 2 | M1M 15/20/30 | Real-Time values | Yes
Reactive Power L1 |  | VAR | 0.01 | Signed | Read | 5B24 | 23332 | 2 | M1M 15/20/30 | Real-Time values | Yes
Reactive Power L2 |  | VAR | 0.01 | Signed | Read | 5B26 | 23334 | 2 | M1M 15/20/30 | Real-Time values | Yes
Reactive Power L3 |  | VAR | 0.01 | Signed | Read | 5B28 | 23336 | 2 | M1M 15/20/30 | Real-Time values | Yes
Apparent Power total |  | VA | 0.01 | Signed | Read | 5B2A | 23338 | 2 | M1M 15/20/30 | Real-Time values | Yes
Apparent Power L1 |  | VA | 0.01 | Signed | Read | 5B2C | 23340 | 2 | M1M 15/20/30 | Real-Time values | Yes
Apparent Power L2 |  | VA | 0.01 | Signed | Read | 5B2E | 23342 | 2 | M1M 15/20/30 | Real-Time values | Yes
Apaprent power L3 |  | VA | 0.01 | Signed | Read | 5B30 | 23344 | 2 | M1M 15/20/30 | Real-Time values | Yes
Frequency |  | Hz | 0.01 | Unsigned | Read | 5B32 | 23346 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power Total Angle |  | ° | 0.1 | Signed | Read | 5B33 | 23347 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power Angle L1 |  | ° | 0.1 | Signed | Read | 5B34 | 23348 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power Angle L2 |  | ° | 0.1 | Signed | Read | 5B35 | 23349 | 1 | M1M 15/20/30 | Real-Time values
Power Angle L3 |  | ° | 0.1 | Signed | Read | 5B36 | 23350 | 1 | M1M 15/20/30 | Real-Time values
Voltage Angle L1 |  | ° | 0.1 | Signed | Read | 5B37 | 23351 | 1 | M1M 15/20/30 | Real-Time values
Voltage Angle L2 |  | ° | 0.1 | Signed | Read | 5B38 | 23352 | 1 | M1M 15/20/30 | Real-Time values
Voltage Angle L3 |  | ° | 0.1 | Signed | Read | 5B39 | 23353 | 1 | M1M 15/20/30 | Real-Time values
Current Angle L1 |  | ° | 0.1 | Signed | Read | 5B3D | 23357 | 1 | M1M 15/20/30 | Real-Time values
Current Angle L2 |  | ° | 0.1 | Signed | Read | 5B3E | 23358 | 1 | M1M 15/20/30 | Real-Time values
Current Angle L3 |  | ° | 0.1 | Signed | Read | 5B3F | 23359 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power factor total |  |  | 0.001 | Signed | Read | 5B40 | 23360 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power factor L1 |  |  | 0.001 | Signed | Read | 5B41 | 23361 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power factor L2 |  |  | 0.001 | Signed | Read | 5B42 | 23362 | 1 | M1M 15/20/30 | Real-Time values | Yes
Power factor L3 |  |  | 0.001 | Signed | Read | 5B43 | 23363 | 1 | M1M 15/20/30 | Real-Time values | Yes
Displacement factor total | Cos phi |  | 0.001 | Signed | Read | 5B48 | 23368 | 1 | M1M 15/20/30 | Real-Time values
Displacement factor L1 | Cos phi |  | 0.001 | Signed | Read | 5B49 | 23369 | 1 | M1M 15/20/30 | Real-Time values
Displacement factor L2 | Cos phi |  | 0.001 | Signed | Read | 5B4A | 23370 | 1 | M1M 15/20/30 | Real-Time values
Displacement factor L3 | Cos phi |  | 0.001 | Signed | Read | 5B4B | 23371 | 1 | M1M 15/20/30 | Real-Time values
Average current L1 | Data value | A | 0.01 | Unsigned | Read | 5BD4 | 23508 | 2 | M1M 30 | Avg/Min/Max values
Average current L2 | Data value | A | 0.01 | Unsigned | Read | 5BD6 | 23510 | 2 | M1M 30 | Avg/Min/Max values
Average current L3 | Data value | A | 0.01 | Unsigned | Read | 5BD8 | 23512 | 2 | M1M 30 | Avg/Min/Max values
Average current neutral | Data value | A | 0.01 | Unsigned | Read | 5BDA | 23514 | 2 | M1M 30 | Avg/Min/Max values
Average voltage L1 | Data value | V | 0.1 | Unsigned | Read | 5BDC | 23516 | 2 | M1M 30 | Avg/Min/Max values
Average voltage L2 | Data value | V | 0.1 | Unsigned | Read | 5BDE | 23518 | 2 | M1M 30 | Avg/Min/Max values
Average voltage L3 | Data value | V | 0.1 | Unsigned | Read | 5BE0 | 23520 | 2 | M1M 30 | Avg/Min/Max values
Average voltage L1-L2 | Data value | V | 0.1 | Unsigned | Read | 5BE2 | 23522 | 2 | M1M 30 | Avg/Min/Max values
Average voltage L2-L3 | Data value | V | 0.1 | Unsigned | Read | 5BE4 | 23524 | 2 | M1M 30 | Avg/Min/Max values
Average voltage L1-L3 | Data value | V | 0.1 | Unsigned | Read | 5BE6 | 23526 | 2 | M1M 30 | Avg/Min/Max values
Average active power total | Data value | W | 0.01 | Signed | Read | 5BE8 | 23528 | 2 | M1M 30 | Avg/Min/Max values
Average active power L1 | Data value | W | 0.01 | Signed | Read | 5BEA | 23530 | 2 | M1M 30 | Avg/Min/Max values
Average active power L2 | Data value | W | 0.01 | Signed | Read | 5BEC | 23532 | 2 | M1M 30 | Avg/Min/Max values
Average active power L3 | Data value | W | 0.01 | Signed | Read | 5BEE | 23534 | 2 | M1M 30 | Avg/Min/Max values
Average reactive power total | Data value | VAR | 0.01 | Signed | Read | 5BF0 | 23536 | 2 | M1M 30 | Avg/Min/Max values
Average reactive power L1 | Data value | VAR | 0.01 | Signed | Read | 5BF2 | 23538 | 2 | M1M 30 | Avg/Min/Max values
Average reactive power L2 | Data value | VAR | 0.01 | Signed | Read | 5BF4 | 23540 | 2 | M1M 30 | Avg/Min/Max values
Average reactive power L3 | Data value | VAR | 0.01 | Signed | Read | 5BF6 | 23542 | 2 | M1M 30 | Avg/Min/Max values
Average apparent power total | Data value | VA | 0.01 | Signed | Read | 5BF8 | 23544 | 2 | M1M 30 | Avg/Min/Max values
Average apparent power L1 | Data value | VA | 0.01 | Signed | Read | 5BFA | 23546 | 2 | M1M 30 | Avg/Min/Max values
Average apparent power L2 | Data value | VA | 0.01 | Signed | Read | 5BFC | 23548 | 2 | M1M 30 | Avg/Min/Max values
Average apparent power L3 | Data value | VA | 0.01 | Signed | Read | 5BFE | 23550 | 2 | M1M 30 | Avg/Min/Max values
Maximum current L1 | Data value | A | 0.01 | Unsigned | Read | 5C10 | 23568 | 2 | M1M 30 | Avg/Min/Max values
Maximum current L2 | Data value | A | 0.01 | Unsigned | Read | 5C12 | 23570 | 2 | M1M 30 | Avg/Min/Max values
Maximum current L3 | Data value | A | 0.01 | Unsigned | Read | 5C14 | 23572 | 2 | M1M 30 | Avg/Min/Max values
Maximum current neutral | Data value | A | 0.01 | Unsigned | Read | 5C16 | 23574 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L1 | Data value | V | 0.1 | Unsigned | Read | 5C18 | 23576 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L2 | Data value | V | 0.1 | Unsigned | Read | 5C1A | 23578 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L3 | Data value | V | 0.1 | Unsigned | Read | 5C1C | 23580 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L1-L2 | Data value | V | 0.1 | Unsigned | Read | 5C1E | 23582 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L2-L3 | Data value | V | 0.1 | Unsigned | Read | 5C20 | 23584 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L1-L3 | Data value | V | 0.1 | Unsigned | Read | 5C22 | 23586 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power total | Data value | W | 0.01 | Signed | Read | 5C24 | 23588 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power L1 | Data value | W | 0.01 | Signed | Read | 5C26 | 23590 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power L2 | Data value | W | 0.01 | Signed | Read | 5C28 | 23592 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power L3 | Data value | W | 0.01 | Signed | Read | 5C2A | 23594 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power total | Data value | VAR | 0.01 | Signed | Read | 5C2C | 23596 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power L1 | Data value | VAR | 0.01 | Signed | Read | 5C2E | 23598 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power L2 | Data value | VAR | 0.01 | Signed | Read | 5C30 | 23600 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power L3 | Data value | VAR | 0.01 | Signed | Read | 5C32 | 23602 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power total | Data value | VA | 0.01 | Signed | Read | 5C34 | 23604 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power L1 | Data value | VA | 0.01 | Signed | Read | 5C36 | 23606 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power L2 | Data value | VA | 0.01 | Signed | Read | 5C38 | 23608 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power L3 | Data value | VA | 0.01 | Signed | Read | 5C3A | 23610 | 2 | M1M 30 | Avg/Min/Max values
Maximum current L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C4C | 23628 | 2 | M1M 30 | Avg/Min/Max values
Maximum current L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C4E | 23630 | 2 | M1M 30 | Avg/Min/Max values
Maximum current L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C50 | 23632 | 2 | M1M 30 | Avg/Min/Max values
Maximum current neutral timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C52 | 23634 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C54 | 23636 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C56 | 23638 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C58 | 23640 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L1-L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C5A | 23642 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L2-L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C5C | 23644 | 2 | M1M 30 | Avg/Min/Max values
Maximum voltage L1-L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C5E | 23646 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power total timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C60 | 23648 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C62 | 23650 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C64 | 23652 | 2 | M1M 30 | Avg/Min/Max values
Maximum active power L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C66 | 23654 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power total timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C68 | 23656 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C6A | 23658 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C6C | 23660 | 2 | M1M 30 | Avg/Min/Max values
Maximum reactive power L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C6E | 23662 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power total timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C70 | 23664 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C72 | 23666 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C74 | 23668 | 2 | M1M 30 | Avg/Min/Max values
Maximum apparent power L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5C76 | 23670 | 2 | M1M 30 | Avg/Min/Max values
Minimum current L1 | Data value | A | 0.01 | Unsigned | Read | 5C88 | 23688 | 2 | M1M 30 | Avg/Min/Max values
Minimum current L2 | Data value | A | 0.01 | Unsigned | Read | 5C8A | 23690 | 2 | M1M 30 | Avg/Min/Max values
Minimum current L3 | Data value | A | 0.01 | Unsigned | Read | 5C8C | 23692 | 2 | M1M 30 | Avg/Min/Max values
Minimum current neutral | Data value | A | 0.01 | Unsigned | Read | 5C8E | 23694 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L1 | Data value | V | 0.1 | Unsigned | Read | 5C90 | 23696 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L2 | Data value | V | 0.1 | Unsigned | Read | 5C92 | 23698 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L3 | Data value | V | 0.1 | Unsigned | Read | 5C94 | 23700 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L1-L2 | Data value | V | 0.1 | Unsigned | Read | 5C96 | 23702 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L2-L3 | Data value | V | 0.1 | Unsigned | Read | 5C98 | 23704 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L1-L3 | Data value | V | 0.1 | Unsigned | Read | 5C9A | 23706 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power total | Data value | W | 0.01 | Signed | Read | 5C9C | 23708 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power L1 | Data value | W | 0.01 | Signed | Read | 5C9E | 23710 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power L2 | Data value | W | 0.01 | Signed | Read | 5CA0 | 23712 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power L3 | Data value | W | 0.01 | Signed | Read | 5CA2 | 23714 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power total | Data value | VAR | 0.01 | Signed | Read | 5CA4 | 23716 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power L1 | Data value | VAR | 0.01 | Signed | Read | 5CA6 | 23718 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power L2 | Data value | VAR | 0.01 | Signed | Read | 5CA8 | 23720 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power L3 | Data value | VAR | 0.01 | Signed | Read | 5CAA | 23722 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power total | Data value | VA | 0.01 | Signed | Read | 5CAC | 23724 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power L1 | Data value | VA | 0.01 | Signed | Read | 5CAE | 23726 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power L2 | Data value | VA | 0.01 | Signed | Read | 5CB0 | 23728 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power L3 | Data value | VA | 0.01 | Signed | Read | 5CB2 | 23730 | 2 | M1M 30 | Avg/Min/Max values
Minimum current L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CC4 | 23748 | 2 | M1M 30 | Avg/Min/Max values
Minimum current L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CC6 | 23750 | 2 | M1M 30 | Avg/Min/Max values
Minimum current L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CC8 | 23752 | 2 | M1M 30 | Avg/Min/Max values
Minimum current neutral timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CCA | 23754 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CCC | 23756 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CCE | 23758 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CD0 | 23760 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L1-L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CD2 | 23762 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L2-L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CD4 | 23764 | 2 | M1M 30 | Avg/Min/Max values
Minimum voltage L1-L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CD6 | 23766 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power total timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CD8 | 23768 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CDA | 23770 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CDC | 23772 | 2 | M1M 30 | Avg/Min/Max values
Minimum active power L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CDE | 23774 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power total timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CE0 | 23776 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CE2 | 23778 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CE4 | 23780 | 2 | M1M 30 | Avg/Min/Max values
Minimum reactive power L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CE6 | 23782 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power total timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CE8 | 23784 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power L1 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CEA | 23786 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power L2 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CEC | 23788 | 2 | M1M 30 | Avg/Min/Max values
Minimum apparent power L3 timestamp | second from 2000-01-01 |  | 1 | Unsigned | Read | 5CEE | 23790 | 2 | M1M 30 | Avg/Min/Max values
Voltage harmonics | L1 (THD) | % | 0.1 | Unsigned | Read | 5D00 | 23808 | 1 | M1M 20/30 | Power Quality values | Yes
| L1 (2nd,3rd…40th), up to 15th for M1M 20 | % | 0.1 | Unsigned | Read | 5D01 | 23809 | 39 | M1M 20/30 | Power Quality values
| L2 (THD) | % | 0.1 | Unsigned | Read | 5D80 | 23936 | 1 | M1M 20/30 | Power Quality values | Yes
| L2 (2nd,3rd…40th), up to 15th for M1M 20 | % | 0.1 | Unsigned | Read | 5D81 | 23937 | 39 | M1M 20/30 | Power Quality values
| L3 (THD) | % | 0.1 | Unsigned | Read | 5E00 | 24064 | 1 | M1M 20/30 | Power Quality values | Yes
| L3 (2nd,3rd…40th), up to 15th for M1M 20 | % | 0.1 | Unsigned | Read | 5E01 | 24065 | 39 | M1M 20/30 | Power Quality values
Current harmonics | L1 (THD) | % | 0.1 | Unsigned | Read | 6000 | 24576 | 1 | M1M 20/30 | Power Quality values | Yes
| L1 (2nd,3rd…40th), up to 15th for M1M 20 | % | 0.1 | Unsigned | Read | 6001 | 24577 | 39 | M1M 20/30 | Power Quality values
| L2 (THD) | % | 0.1 | Unsigned | Read | 6080 | 24704 | 1 | M1M 20/30 | Power Quality values | Yes
| L2 (2nd,3rd…40th), up to 15th for M1M 20 | % | 0.1 | Unsigned | Read | 6081 | 24705 | 39 | M1M 20/30 | Power Quality values
| L3 (THD) | % | 0.1 | Unsigned | Read | 6100 | 24832 | 1 | M1M 20/30 | Power Quality values | Yes
| L3 (2nd,3rd…40th), up to 15th for M1M 20 | % | 0.1 | Unsigned | Read | 6101 | 24833 | 39 | M1M 20/30 | Power Quality values
Unbalances | Phase voltage | % | 0.1 | Unsigned | Read | 6200 | 25088 | 2 | M1M 30, M1M 20 I/O Pro | Power Quality values | Yes
| Line voltage | % | 0.1 | Unsigned | Read | 6202 | 25090 | 2 | M1M 30, M1M 20 I/O Pro | Power Quality values | Yes
| Current | % | 0.1 | Unsigned | Read | 6204 | 25092 | 2 | M1M 30, M1M 20 I/O Pro | Power Quality values | Yes
Digital Output 1-2 | 0=OFF, 1=ON(only for COMM mode which set on HMI) | -- | -- | Unsigned | Read/Write | 6300 | 25344 | 2 | M1M 20 IO, M1M 20 IO Pro, M1M 30 all products | Digital Input/Output | Yes
Digital Inputs 1-2 | Input Port 1~2; 0-OFF, 1-ON |  | 1 | Unsigned | Read | 6308 | 25352 | 2 | M1M 20 IO, M1M 30 IO, M1M 20 IO Pro, M1M 30 I/O Pro | Digital Input/Output
Digital Inputs 3-4 | Input Port 3~4; 0-OFF, 1-ON |  | 1 | Unsigned | Read | 630A | 25354 | 2 | M1M 30 I/O Pro | Digital Input/Output | Yes
Digital Inputs 1-2 Counters | Input Port 1~2; pulse counter |  | 1 | Unsigned | Read | 6318 | 25368 | 8 | M1M 20 IO, M1M 30 IO, M1M 20 IO Pro, M1M 30 I/O Pro | Digital Input/Output
Digital Inputs 3-4 Counters | Input Port 3~4; pulse counter |  | 1 | Unsigned | Read | 6310 | 25360 | 8 | M1M 30 I/O Pro | Digital Input/Output | Yes
Serial number(s) |  |  |  | ASCII | Read | 8900 | 35072 | 5 | M1M 15/20/30 | Device information | Yes
Meter firmware version | Vx.x.xx and Vx.x.xx |  |  | ASCII | Read | 8908 | 35080 | 8 | M1M 15/20/30 | Device information
Product type number ID | See sheet "Details" |  |  | ASCII | Read | 8910 | 35088 | 1 | M1M 15/20/30 | Device information
Product tag name | default equal to SN code |  |  | ASCII | Read/Write | 8919 | 35097 | 5 | M1M 15/20/30 | Device information
Type designation | e.g. M1M 15, M1M 20, … |  |  | ASCII | Read | 8960 | 35168 | 6 | M1M 15/20/30 | Device information | Yes
Product Name | E.g. M1M 30 MODBUS |  |  | ASCII | Read | 8966 | 35174 | 8 | M1M 15/20/30 | Device information | Yes
Date Time | Format: YYMMDD:HHMMSS |  | 1 | Unsigned | Read/Write | 8A00 | 35328 | 3 | M1M 30 | Device configuration | Yes
Current tariff | Current active tariff (1~4) |  | -- | Unsigned | Read/Write | 8A07 | 35335 | 1 | M1M 30 I/O Pro | Tariff | Yes
Transformer ratios | CT primary |  | 1 | Unsigned | Read/Write | 8C00 | 35840 | 2 | M1M 15/20/30 | Device configuration | Yes
| CT secondary |  | 1 | Unsigned | Read/Write | 8C02 | 35842 | 2 | M1M 15/20/30 | Device configuration | Yes
| VT primary |  | 1 | Unsigned | Read/Write | 8C04 | 35844 | 2 | M1M 15/20/30 | Device configuration
| VT secondary |  | 1 | Unsigned | Read/Write | 8C06 | 35846 | 2 | M1M 15/20/30 | Device configuration | Yes
Tariff settings | Tariffs source, 0=RTC, 1=Communication, 2=DI | -- | -- | Unsigned | Read/Write | 8C90 | 35984 | 1 | M1M 30 I/O Pro | Tariff | Yes
| Input configuration, fixed 0x04E4, see the sheet "Details" | -- | -- | Unsigned | Read | 8C91 | 35985 | 1 | M1M 30 I/O Pro | Tariff | Yes
| Weekday type - Monday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C92 | 35986 | 1 | M1M 30 I/O Pro | Tariff | Yes
| Weekday type - Tuesday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C93 | 35987 | 1 | M1M 30 I/O Pro | Tariff | Yes
| Weekday type - Wednesday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C94 | 35988 | 1 | M1M 30 I/O Pro | Tariff | Yes
| Weekday type - Thursday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C95 | 35989 | 1 | M1M 30 I/O Pro | Tariff | Yes
| Weekday type - Friday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C96 | 35990 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekday type - Saturday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C97 | 35991 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekday type - Sunday, 0=weekday, 1=weekend | -- | -- | Unsigned | Read/Write | 8C98 | 35992 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekday Start time - T1, 0xHHMM, 0xFFFF: Disable | -- | -- | Unsigned | Read/Write | 8C99 | 35993 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekday Start time - T2, 0xHHMM | -- | -- | Unsigned | Read/Write | 8C9A | 35994 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekday Start time - T3, 0xHHMM | -- | -- | Unsigned | Read/Write | 8C9B | 35995 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekday Start time - T4, 0xHHMM | -- | -- | Unsigned | Read/Write | 8C9C | 35996 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekend Start time - T1, 0xHHMM, 0xFFFF: Disable | -- | -- | Unsigned | Read/Write | 8CA1 | 36001 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekend Start time - T2, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA2 | 36002 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekend Start time - T3, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA3 | 36003 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Weekend Start time - T4, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA4 | 36004 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Specialday Start time - T1, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CA9 | 36009 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Specialday Start time - T2, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CAA | 36010 | 1 | M1M 30 I/O Pro | Tariff | M4M 30 (all versions)
| Specialday Start time - T3, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CAB | 36011 | 1 | M1M 30 I/O Pro | Tariff
| Specialday Start time - T4, 0xHHMM | -- | -- | Unsigned | Read/Write | 8CAC | 36012 | 1 | M1M 30 I/O Pro | Tariff
| Specialday - Total number, 1~50 | -- | -- | Unsigned | Read/Write | 8CD3 | 36051 | 1 | M1M 30 I/O Pro | Tariff
| Specialday - Current special day number, 1~50 | -- | -- | Unsigned | Read | 8CD4 | 36052 | 1 | M1M 30 I/O Pro | Tariff
| Specialday - Entry Date, 0xYYMMDDxx(xx fixed FF) | -- | -- | Unsigned | Read/Write | 8CD5 | 36053 | 2 | M1M 30 I/O Pro | Tariff
| Specialday - Day ID, 1~50 | -- | -- | Unsigned | Read/Write | 8CD7 | 36055 | 1 | M1M 30 I/O Pro | Tariff
Wiring type | See sheet "Details" |  | 1 | Unsigned | Read/Write | 8CE5 | 36069 | 1 | M1M 15/20/30 | Device configuration
DST | Start Date time, 0xYYMMDDHH | -- | -- | Unsigned | Read/Write | 8CE6 | 36070 | 2 | M1M 30 I/O Pro | Tariff
| Start Date time, 0xYYMMDDHH | -- | -- | Unsigned | Read/Write | 8CE8 | 36072 | 2 | M1M 30 I/O Pro | Tariff
| Enable, 0=Disable, 1=Enable | -- | -- | Unsigned | Read/Write | 8CEA | 36074 | 1 | M1M 30 I/O Pro | Tariff
Modbus RTU | Address, 1 - 247 |  | 1 | Unsigned | Read/Write | 8CEB | 36075 | 1 | M1M 15/20/30 | Comm configuration
| Baudrate, 9600, 19200, 38400, 57600, 115200 |  | 1 | Unsigned | Read/Write | 8CEC | 36076 | 2 | M1M 15/20/30 | Comm configuration
| Parity, 0—8N1，1—8E1，2—8O1 |  | 1 | Unsigned | Read/Write | 8CEE | 36078 | 1 | M1M 15/20/30 | Comm configuration
Ethernet | DHCP, 0-disable; 1- enable |  | 1 | Unsigned | Read/Write | 8CEF | 36079 | 1 | M1M 20/30 | Comm configuration
| IP, A.B.C.D -> 0xAABBCCDD |  | 1 | Unsigned | Read/Write | 8CF0 | 36080 | 2 | M1M 20/30 | Comm configuration
| Mask, A.B.C.D -> 0xAABBCCDD |  | 1 | Unsigned | Read/Write | 8CF2 | 36082 | 2 | M1M 20/30 | Comm configuration
| Gateway, A.B.C.D -> 0xAABBCCDD |  | 1 | Unsigned | Read/Write | 8CF4 | 36084 | 2 | M1M 20/30 | Comm configuration
Active power total Scaler 1 |  | W | 1 | Signed | Read | CB1A | 51994 | 2 | M1M 15/20/30 | Real-Time values
Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CB1C | 51996 | 2 | M1M 15/20/30 | Real-Time values
Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CB1E | 51998 | 2 | M1M 15/20/30 | Real-Time values
Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CB20 | 52000 | 2 | M1M 15/20/30 | Real-Time values
Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CB22 | 52002 | 2 | M1M 15/20/30 | Real-Time values
Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CB24 | 52004 | 2 | M1M 15/20/30 | Real-Time values
Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CB26 | 52006 | 2 | M1M 15/20/30 | Real-Time values
Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CB28 | 52008 | 2 | M1M 15/20/30 | Real-Time values
Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CB2A | 52010 | 2 | M1M 15/20/30 | Real-Time values
Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CB2C | 52012 | 2 | M1M 15/20/30 | Real-Time values
Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CB2E | 52014 | 2 | M1M 15/20/30 | Real-Time values
Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CB30 | 52016 | 2 | M1M 15/20/30 | Real-Time values
Average Active power total Scaler 1 |  | W | 1 | Signed | Read | CBE8 | 52200 | 2 | M1M 30 | Avg/Min/Max values
Average Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CBEA | 52202 | 2 | M1M 30 | Avg/Min/Max values
Average Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CBEC | 52204 | 2 | M1M 30 | Avg/Min/Max values
Average Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CBEE | 52206 | 2 | M1M 30 | Avg/Min/Max values
Average Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CBF0 | 52208 | 2 | M1M 30 | Avg/Min/Max values
Average Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CBF2 | 52210 | 2 | M1M 30 | Avg/Min/Max values
Average Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CBF4 | 52212 | 2 | M1M 30 | Avg/Min/Max values
Average Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CBF6 | 52214 | 2 | M1M 30 | Avg/Min/Max values
Average Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CBF8 | 52216 | 2 | M1M 30 | Avg/Min/Max values
Average Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CBFA | 52218 | 2 | M1M 30 | Avg/Min/Max values
Average Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CBFC | 52220 | 2 | M1M 30 | Avg/Min/Max values
Average Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CBFE | 52222 | 2 | M1M 30 | Avg/Min/Max values
Max Active power total Scaler 1 |  | W | 1 | Signed | Read | CC24 | 52260 | 2 | M1M 30 | Avg/Min/Max values
Max Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CC26 | 52262 | 2 | M1M 30 | Avg/Min/Max values
Max Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CC28 | 52264 | 2 | M1M 30 | Avg/Min/Max values
Max Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CC2A | 52266 | 2 | M1M 30 | Avg/Min/Max values
Max Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CC2C | 52268 | 2 | M1M 30 | Avg/Min/Max values
Max Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CC2E | 52270 | 2 | M1M 30 | Avg/Min/Max values
Max Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CC30 | 52272 | 2 | M1M 30 | Avg/Min/Max values
Max Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CC32 | 52274 | 2 | M1M 30 | Avg/Min/Max values
Max Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CC34 | 52276 | 2 | M1M 30 | Avg/Min/Max values
Max Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CC36 | 52278 | 2 | M1M 30 | Avg/Min/Max values
Max Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CC38 | 52280 | 2 | M1M 30 | Avg/Min/Max values
Max Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CC3A | 52282 | 2 | M1M 30 | Avg/Min/Max values
Min Active power total Scaler 1 |  | W | 1 | Signed | Read | CC9C | 52380 | 2 | M1M 30 | Avg/Min/Max values
Min Active power L1 Scaler 1 |  | W | 1 | Signed | Read | CC9E | 52382 | 2 | M1M 30 | Avg/Min/Max values
Min Active power L2 Scaler 1 |  | W | 1 | Signed | Read | CCA0 | 52384 | 2 | M1M 30 | Avg/Min/Max values
Min Active power L3 Scaler 1 |  | W | 1 | Signed | Read | CCA2 | 52386 | 2 | M1M 30 | Avg/Min/Max values
Min Reactive power total Scaler 1 |  | VAR | 1 | Signed | Read | CCA4 | 52388 | 2 | M1M 30 | Avg/Min/Max values
Min Reactive power L1 Scaler 1 |  | VAR | 1 | Signed | Read | CCA6 | 52390 | 2 | M1M 30 | Avg/Min/Max values
Min Reactive power L2 Scaler 1 |  | VAR | 1 | Signed | Read | CCA8 | 52392 | 2 | M1M 30 | Avg/Min/Max values
Min Reactive power L3 Scaler 1 |  | VAR | 1 | Signed | Read | CCAA | 52394 | 2 | M1M 30 | Avg/Min/Max values
Min Apparent power total Scaler 1 |  | VA | 1 | Signed | Read | CCAC | 52396 | 2 | M1M 30 | Avg/Min/Max values
Min Apparent power L1 Scaler 1 |  | VA | 1 | Signed | Read | CCAE | 52398 | 2 | M1M 30 | Avg/Min/Max values
Min Apparent power L2 Scaler 1 |  | VA | 1 | Signed | Read | CCB0 | 52400 | 2 | M1M 30 | Avg/Min/Max values
Min Apparent power L3 Scaler 1 |  | VA | 1 | Signed | Read | CCB2 | 52402 | 2 | M1M 30 | Avg/Min/Max values
***M1M 15/20/30 means all products scope of M1M 15, M1M 20 or M1M 30

## Float Table
Quantity/Functionality | Explanation | Unit | Resolution | Data Type | Access | Register (Hex) | Register (Dec) | No of registers | Product Type | Functionality Block
Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 3000 | 12288 | 2 | M1M 15/20/30 | Real-Time value
Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 3002 | 12290 | 2 | M1M 15/20/30 | Real-Time value
Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 3004 | 12292 | 2 | M1M 15/20/30 | Real-Time value
Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 3006 | 12294 | 2 | M1M 15/20/30 | Real-Time value
Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 3008 | 12296 | 2 | M1M 15/20/30 | Real-Time value
Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 300A | 12298 | 2 | M1M 15/20/30 | Real-Time value
Three phase system voltage |  | V | 1 | Float 32 bits | Read | 300C | 12300 | 2 | M1M 15/20/30 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 300E | 12302 | 2 | M1M 15/20/30 | Real-Time value
Current phase 1 |  | A | 1 | Float 32 bits | Read | 3010 | 12304 | 2 | M1M 15/20/30 | Real-Time value
Current phase 2 |  | A | 1 | Float 32 bits | Read | 3012 | 12306 | 2 | M1M 15/20/30 | Real-Time value
Current phase 3 |  | A | 1 | Float 32 bits | Read | 3014 | 12308 | 2 | M1M 15/20/30 | Real-Time value
Neutral current |  | A | 1 | Float 32 bits | Read | 3016 | 12310 | 2 | M1M 20/30 | Real-Time value
Three phase system current |  | A | 1 | Float 32 bits | Read | 3018 | 12312 | 2 | M1M 15/20/30 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 301A | 12314 | 2 | M1M 15/20/30 | Real-Time value
Active power phase 1 |  | W | 1 | Float 32 bits | Read | 301C | 12316 | 2 | M1M 15/20/30 | Real-Time value
Active power phase 2 |  | W | 1 | Float 32 bits | Read | 301E | 12318 | 2 | M1M 15/20/30 | Real-Time value
Active power phase 3 |  | W | 1 | Float 32 bits | Read | 3020 | 12320 | 2 | M1M 15/20/30 | Real-Time value
Active power total |  | W | 1 | Float 32 bits | Read | 3022 | 12322 | 2 | M1M 15/20/30 | Real-Time value
Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 3024 | 12324 | 2 | M1M 15/20/30 | Real-Time value
Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 3026 | 12326 | 2 | M1M 15/20/30 | Real-Time value
Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 3028 | 12328 | 2 | M1M 15/20/30 | Real-Time value
Reactive power total |  | Var | 1 | Float 32 bits | Read | 302A | 12330 | 2 | M1M 15/20/30 | Real-Time value
Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 302C | 12332 | 2 | M1M 15/20/30 | Real-Time value
Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 302E | 12334 | 2 | M1M 15/20/30 | Real-Time value
Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 3030 | 12336 | 2 | M1M 15/20/30 | Real-Time value
Apparente power total |  | VA | 1 | Float 32 bits | Read | 3032 | 12338 | 2 | M1M 15/20/30 | Real-Time value
Reserved |  |  | 1 | Float 32 bits | Read | 3034 | 12340 | 2 | M1M 15/20/30 | Real-Time value
Power factor phase 1 |  |  | 1 | Float 32 bits | Read | 3036 | 12342 | 2 | M1M 15/20/30 | Power Quality value
Power factor phase 2 |  |  | 1 | Float 32 bits | Read | 3038 | 12344 | 2 | M1M 15/20/30 | Power Quality value
Power factor phase 3 |  |  | 1 | Float 32 bits | Read | 303A | 12346 | 2 | M1M 15/20/30 | Power Quality value
Power factor phase total |  |  | 1 | Float 32 bits | Read | 303C | 12348 | 2 | M1M 15/20/30 | Power Quality value
Displacement factor phase 1 | Cos phi |  | 1 | Float 32 bits | Read | 303E | 12350 | 2 | M1M 15/20/30 | Power Quality value
Displacement factor phase 2 | Cos phi |  | 1 | Float 32 bits | Read | 3040 | 12352 | 2 | M1M 15/20/30 | Power Quality value
Displacement factor phase 3 | Cos phi |  | 1 | Float 32 bits | Read | 3042 | 12354 | 2 | M1M 15/20/30 | Power Quality value
Displacement factor phase total | Cos phi |  | 1 | Float 32 bits | Read | 3044 | 12356 | 2 | M1M 15/20/30 | Power Quality value
Power Angle L1 |  | ° | 1 | Float 32 bits | Read | 3046 | 12358 | 2 | M1M 15/20/30 | Real-Time value
Power Angle L2 |  | ° | 1 | Float 32 bits | Read | 3048 | 12360 | 2 | M1M 15/20/30 | Real-Time value
Power Angle L3 |  | ° | 1 | Float 32 bits | Read | 304A | 12362 | 2 | M1M 15/20/30 | Real-Time value
Power Angle Total |  | ° | 1 | Float 32 bits | Read | 304C | 12364 | 2 | M1M 15/20/30 | Real-Time value
Frequency |  | Hz | 1 | Float 32 bits | Read | 304E | 12366 | 2 | M1M 15/20/30 | Real-Time value
Current demand phase 1 |  | A | 1 | Float 32 bits | Read | 3050 | 12368 | 2 | M1M 30 | Demand value
Current demand phase 2 |  | A | 1 | Float 32 bits | Read | 3052 | 12370 | 2 | M1M 30 | Demand value
Current demand phase 3 |  | A | 1 | Float 32 bits | Read | 3054 | 12372 | 2 | M1M 30 | Demand value
Active power demand |  | W | 1 | Float 32 bits | Read | 3056 | 12374 | 2 | M1M 30 | Demand value
Reactive power demand |  | Var | 1 | Float 32 bits | Read | 3058 | 12376 | 2 | M1M 30 | Demand value
Apparent power demand |  | VA | 1 | Float 32 bits | Read | 305A | 12378 | 2 | M1M 30 | Demand value
Voltage angle phase 1 |  | ° | 1 | Float 32 bits | Read | 305C | 12380 | 2 | M1M 15/20/30 | Real-Time value
Voltage angle phase 2 |  | ° | 1 | Float 32 bits | Read | 305E | 12382 | 2 | M1M 15/20/30 | Real-Time value
Voltage angle phase 3 |  | ° | 1 | Float 32 bits | Read | 3060 | 12384 | 2 | M1M 15/20/30 | Real-Time value
Currente angle phase 1 |  | ° | 1 | Float 32 bits | Read | 3062 | 12386 | 2 | M1M 15/20/30 | Real-Time value
Currente angle phase 2 |  | ° | 1 | Float 32 bits | Read | 3064 | 12388 | 2 | M1M 15/20/30 | Real-Time value
Currente angle phase 3 |  | ° | 1 | Float 32 bits | Read | 3066 | 12390 | 2 | M1M 15/20/30 | Real-Time value
THD Phase voltage 1 |  | % | 1 | Float 32 bits | Read | 3068 | 12392 | 2 | M1M 20/30 | Power Quality value
THD Phase voltage 2 |  | % | 1 | Float 32 bits | Read | 306A | 12394 | 2 | M1M 20/30 | Power Quality value
THD Phase voltage 3 |  | % | 1 | Float 32 bits | Read | 306C | 12396 | 2 | M1M 20/30 | Power Quality value
THD Current 1 |  | % | 1 | Float 32 bits | Read | 306E | 12398 | 2 | M1M 20/30 | Power Quality value
THD Current 2 |  | % | 1 | Float 32 bits | Read | 3070 | 12400 | 2 | M1M 20/30 | Power Quality value
THD Current 3 |  | % | 1 | Float 32 bits | Read | 3072 | 12402 | 2 | M1M 20/30 | Power Quality value
Umbalance phase voltage |  | % | 1 | Float 32 bits | Read | 3074 | 12404 | 2 | M1M 30, M1M 20 I/O Pro | Power Quality value
Umbalance line voltage |  | % | 1 | Float 32 bits | Read | 3076 | 12406 | 2 | M1M 30, M1M 20 I/O Pro | Power Quality value
Umbalance currente |  | % | 1 | Float 32 bits | Read | 3078 | 12408 | 2 | M1M 30, M1M 20 I/O Pro | Power Quality value
Direct active energy |  | kWh | 0.1 | Unsigned | Read | 307A | 12410 | 2 | M1M 15/20/30 | Energy values
Reverse active energy |  | kWh | 0.1 | Unsigned | Read | 307C | 12412 | 2 | M1M 15/20/30 | Energy values
Direct reactive energy |  | kvarh | 0.1 | Unsigned | Read | 307E | 12414 | 2 | M1M 15/20/30 | Energy values
Reverse reactive energy |  | kvarh | 0.1 | Unsigned | Read | 3080 | 12416 | 2 | M1M 15/20/30 | Energy values
Apparente energy |  | kVAh | 0.1 | Unsigned | Read | 3082 | 12418 | 2 | M1M 15/20/30 | Energy values
Average Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 3084 | 12420 | 2 | M1M 30 | Avg/Min/Max value
Average Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 3086 | 12422 | 2 | M1M 30 | Avg/Min/Max value
Average Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 3088 | 12424 | 2 | M1M 30 | Avg/Min/Max value
Average Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 308A | 12426 | 2 | M1M 30 | Avg/Min/Max value
Average Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 308C | 12428 | 2 | M1M 30 | Avg/Min/Max value
Average Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 308E | 12430 | 2 | M1M 30 | Avg/Min/Max value
Average Current phase 1 |  | A | 1 | Float 32 bits | Read | 3090 | 12432 | 2 | M1M 30 | Avg/Min/Max value
Average Current phase 2 |  | A | 1 | Float 32 bits | Read | 3092 | 12434 | 2 | M1M 30 | Avg/Min/Max value
Average Current phase 3 |  | A | 1 | Float 32 bits | Read | 3094 | 12436 | 2 | M1M 30 | Avg/Min/Max value
Average Neutral current |  | A | 1 | Float 32 bits | Read | 3096 | 12438 | 2 | M1M 30 | Avg/Min/Max value
Average Active power phase 1 |  | W | 1 | Float 32 bits | Read | 3098 | 12440 | 2 | M1M 30 | Avg/Min/Max value
Average Active power phase 2 |  | W | 1 | Float 32 bits | Read | 309A | 12442 | 2 | M1M 30 | Avg/Min/Max value
Average Active power phase 3 |  | W | 1 | Float 32 bits | Read | 309C | 12444 | 2 | M1M 30 | Avg/Min/Max value
Average Active power total |  | W | 1 | Float 32 bits | Read | 309E | 12446 | 2 | M1M 30 | Avg/Min/Max value
Average Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 30A0 | 12448 | 2 | M1M 30 | Avg/Min/Max value
Average Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 30A2 | 12450 | 2 | M1M 30 | Avg/Min/Max value
Average Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 30A4 | 12452 | 2 | M1M 30 | Avg/Min/Max value
Average Reactive power total |  | Var | 1 | Float 32 bits | Read | 30A6 | 12454 | 2 | M1M 30 | Avg/Min/Max value
Average Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 30A8 | 12456 | 2 | M1M 30 | Avg/Min/Max value
Average Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 30AA | 12458 | 2 | M1M 30 | Avg/Min/Max value
Average Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 30AC | 12460 | 2 | M1M 30 | Avg/Min/Max value
Average Apparente power total |  | VA | 1 | Float 32 bits | Read | 30AE | 12462 | 2 | M1M 30 | Avg/Min/Max value
Maximum Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 30B0 | 12464 | 2 | M1M 30 | Avg/Min/Max value
Maximum Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 30B2 | 12466 | 2 | M1M 30 | Avg/Min/Max value
Maximum Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 30B4 | 12468 | 2 | M1M 30 | Avg/Min/Max value
Maximum Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 30B6 | 12470 | 2 | M1M 30 | Avg/Min/Max value
Maximum Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 30B8 | 12472 | 2 | M1M 30 | Avg/Min/Max value
Maximum Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 30BA | 12474 | 2 | M1M 30 | Avg/Min/Max value
Maximum Current phase 1 |  | A | 1 | Float 32 bits | Read | 30BC | 12476 | 2 | M1M 30 | Avg/Min/Max value
Maximum Current phase 2 |  | A | 1 | Float 32 bits | Read | 30BE | 12478 | 2 | M1M 30 | Avg/Min/Max value
Maximum Current phase 3 |  | A | 1 | Float 32 bits | Read | 30C0 | 12480 | 2 | M1M 30 | Avg/Min/Max value
Maximum Neutral current |  | A | 1 | Float 32 bits | Read | 30C2 | 12482 | 2 | M1M 30 | Avg/Min/Max value
Maximum Active power phase 1 |  | W | 1 | Float 32 bits | Read | 30C4 | 12484 | 2 | M1M 30 | Avg/Min/Max value
Maximum Active power phase 2 |  | W | 1 | Float 32 bits | Read | 30C6 | 12486 | 2 | M1M 30 | Avg/Min/Max value
Maximum Active power phase 3 |  | W | 1 | Float 32 bits | Read | 30C8 | 12488 | 2 | M1M 30 | Avg/Min/Max value
Maximum Active power total |  | W | 1 | Float 32 bits | Read | 30CA | 12490 | 2 | M1M 30 | Avg/Min/Max value
Maximum Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 30CC | 12492 | 2 | M1M 30 | Avg/Min/Max value
Maximum Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 30CE | 12494 | 2 | M1M 30 | Avg/Min/Max value
Maximum Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 30D0 | 12496 | 2 | M1M 30 | Avg/Min/Max value
Maximum Reactive power total |  | Var | 1 | Float 32 bits | Read | 30D2 | 12498 | 2 | M1M 30 | Avg/Min/Max value
Maximum Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 30D4 | 12500 | 2 | M1M 30 | Avg/Min/Max value
Maximum Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 30D6 | 12502 | 2 | M1M 30 | Avg/Min/Max value
Maximum Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 30D8 | 12504 | 2 | M1M 30 | Avg/Min/Max value
Maximum Apparente power total |  | VA | 1 | Float 32 bits | Read | 30DA | 12506 | 2 | M1M 30 | Avg/Min/Max value
Minimum Voltage L1 and Neutral |  | V | 1 | Float 32 bits | Read | 30DC | 12508 | 2 | M1M 30 | Avg/Min/Max value
Minimum Voltage L2 and Neutral |  | V | 1 | Float 32 bits | Read | 30DE | 12510 | 2 | M1M 30 | Avg/Min/Max value
Minimum Voltage L3 and Neutral |  | V | 1 | Float 32 bits | Read | 30E0 | 12512 | 2 | M1M 30 | Avg/Min/Max value
Minimum Voltage L1 and L2 |  | V | 1 | Float 32 bits | Read | 30E2 | 12514 | 2 | M1M 30 | Avg/Min/Max value
Minimum Voltage L2 and L3 |  | V | 1 | Float 32 bits | Read | 30E4 | 12516 | 2 | M1M 30 | Avg/Min/Max value
Minimum Voltage L3 and L1 |  | V | 1 | Float 32 bits | Read | 30E6 | 12518 | 2 | M1M 30 | Avg/Min/Max value
Minimum Current phase 1 |  | A | 1 | Float 32 bits | Read | 30E8 | 12520 | 2 | M1M 30 | Avg/Min/Max value
Minimum Current phase 2 |  | A | 1 | Float 32 bits | Read | 30EA | 12522 | 2 | M1M 30 | Avg/Min/Max value
Minimum Current phase 3 |  | A | 1 | Float 32 bits | Read | 30EC | 12524 | 2 | M1M 30 | Avg/Min/Max value
Minimum Neutral current |  | A | 1 | Float 32 bits | Read | 30EE | 12526 | 2 | M1M 30 | Avg/Min/Max value
Minimum Active power phase 1 |  | W | 1 | Float 32 bits | Read | 30F0 | 12528 | 2 | M1M 30 | Avg/Min/Max value
Minimum Active power phase 2 |  | W | 1 | Float 32 bits | Read | 30F2 | 12530 | 2 | M1M 30 | Avg/Min/Max value
Minimum Active power phase 3 |  | W | 1 | Float 32 bits | Read | 30F4 | 12532 | 2 | M1M 30 | Avg/Min/Max value
Minimum Active power total |  | W | 1 | Float 32 bits | Read | 30F6 | 12534 | 2 | M1M 30 | Avg/Min/Max value
Minimum Reactive power phase 1 |  | Var | 1 | Float 32 bits | Read | 30F8 | 12536 | 2 | M1M 30 | Avg/Min/Max value
Minimum Reactive power phase 2 |  | Var | 1 | Float 32 bits | Read | 30FA | 12538 | 2 | M1M 30 | Avg/Min/Max value
Minimum Reactive power phase 3 |  | Var | 1 | Float 32 bits | Read | 30FC | 12540 | 2 | M1M 30 | Avg/Min/Max value
Minimum Reactive power total |  | Var | 1 | Float 32 bits | Read | 30FE | 12542 | 2 | M1M 30 | Avg/Min/Max value
Minimum Apparente power fase 1 |  | VA | 1 | Float 32 bits | Read | 3100 | 12544 | 2 | M1M 30 | Avg/Min/Max value
Minimum Apparente power fase 2 |  | VA | 1 | Float 32 bits | Read | 3102 | 12546 | 2 | M1M 30 | Avg/Min/Max value
Minimum Apparente power fase 3 |  | VA | 1 | Float 32 bits | Read | 3104 | 12548 | 2 | M1M 30 | Avg/Min/Max value
Minimum Apparente power total |  | VA | 1 | Float 32 bits | Read | 3106 | 12550 | 2 | M1M 30 | Avg/Min/Max value
***M1M 15/20/30 means all products scope of M1M 15, M1M 20 or M1M 30

## Details
Product type number ID | M1M 15 | M1M 15 MODBUS RTU | M1M 20 | M1M 20 MODBUS RTU | M1M 20 Ethernet | M1M 20 IO MODBUS RTU | M1M 20 I/O PrO | M1M 30 MODBUS RTU | M1M 30 Ethernet | M1M 30 IO MODBUS RTU | M1M 30 I/O Pro
| 60 | 61 | 62 | 63 | 64 | 65 | 69 | 66 | 67 | 68 | 70
SlaveID LS Byte | 69 | 69 | 70 | 70 | 70 | 70 | 70 | 71 | 71 | 71 | 71
Wires | 3 phase-4 wires network+3CTs (3N3T) | 3 phase-3 wires network+3CTs (3 3T) | 3 phase-3 wires network+2CTs (3 2T) | 3 phase-3 wires network+1CT (3 1T) | 1 phase-2 wires network+1CT (1N1T)
| 1 | 3 | 4 | 5 | 7
11H Function code | Format | part 1 | Part 2 | part 3 | part 4 | part 5 | part 6 | part 7 | part 8
| Byte count | 1 | 1 | 1 | 2 | 2 | 16 | 2 | 1
| Describe | Byte count | SlaveID MS Byte | Run Indicator Status | Firmware Major Ver | Event Addr | SN Code(ASCII Big Endian) If less than 16 add Null | Field code and length | SlaveID LS Byte
| Example | 0x19 | 0xFA(Fixed) | 0xFF(Fixed) | 0x0101 | 0xFFFF(Fixed) | T012345678 | 0x0201(Fixed) | 0x45
V1.1
[5 empty] | 8 bits | 8 bits
[5 empty] | 15~08 bit | 07~00 bit
[5 empty] | Major Version | Minor Version

## Changes
Map version |  | Date
V1.0 | First version | 20201211
V1.1 | 1.Use different colors to distinguish different functions. 2.Unify the style of each register. 3.Removed several invalid registers such as "Current quadrant". 4.Fixed several errors such as number of register. | 20210508
V1.2 | 1.Deleted harmonics of neutral current | 20220123
V1.2A | 1.Added the function that control DO status. | 20230412
V1.3 | 1. Merged M1M 96 and M1M 96 extension map. 2. Improved Float Table | 20231114
V1.3A | 1. Added the 15th harmonics for M1M 20 series products in communication. 2. Changed the Slave ID of M1M 20 IO Pro as same as M1M 20 products, and and M1M 30 IO Pro as same as M1M 30 products. | 20240228