—

Medium voltage products

ABB Electrification Products Division Technical Specification - UniSec

Project: Price List 2020

Customer: USP-PL-2020

Issuer: PT ABB SAKTI INDUSTRI

Your ref.:

Our ref.:	USP-PL-2020 - 01 - 11/18/2020

Table of Contents

1	General Specification: Price List 2020 (Unisec 630A 16kA HD4/VD4)	4

1.1	General Data / Type of apparatus	4

1.2	Electrical Data	4

1.3	Additional Data	5

1.4	Auxiliary supply and wiring data	5

1.5	Switchgear Accessories	6

1.6	Switchgear Composition:  Price List 2020 (Unisec 630A 16kA HD4)	6

2	Typical Unit Description	9

2.1	Panel:   SDC	9

2.2	Panel:   SDC CT	10

2.3	Panel:   SDC LA	11

2.4	Panel:   SDC Motorized	12

2.5	Panel:   SFC (No Fuse)	13

2.6	Panel:   SFC Motorized (No Fuse)	14

2.7	Panel:   SFV	15

2.8	Panel:   SFV with Power Meter	16

2.9	Panel:   DRC	17

2.10	Panel:   DRC LA	18

2.11	Panel:   SBC CT (REF601)	19

2.12	Panel:   SBC CT VT (REF601 + Power Meter)	21

2.13	Panel:   SBC CT VT (REF615F + Power Meter)	23

2.14	Panel:   SBC CT Mot (REF601)	25

2.15	Panel:   SBC CT LA Mot (REF601)	27

2.16	Panel:   SBC CT VT Mot (REF601 + Power Meter)	29

2.17	Panel:   SBC-W CT (REF601)	31

2.18	Panel:   SBC-W CT VT (REF601+Power Meter)	33

2.19	Panel:   SBC CT Mot (REF611)	35

2.20	Panel:   SBC CT (REF611)	37

2.21	Panel:   SBC CT LA Mot (REF611)	39

2.22	Panel:   SBC CT LA (REF611)	41

2.23	Panel:   SBC CT VT Mot (REF611 + Power Meter)	43

2.24	Panel:   SBC CT VT (REF611 + Power Meter)	45

2.25	Panel:   SBC CT VT Mot (REF611 + Power Meter)(ZCT)	47

2.26	Panel:   SBC CT VT (REF611 + Power Meter )(ZCT)	49

2.27	Panel:   SBC CT Mot (REF615F)	51

2.28	Panel:   SBC CT (REF615F)	53

2.29	Panel:   SBC CT LA Mot (REF615F)	55

2.30	Panel:   SBC CT LA (REF615F)	57

2.31	Panel:   SBC CT VT Mot (REF615F)	59

2.32	Panel:   SBC CT VT (REF615F)	61

2.33	Panel:   SBC CT VT Mot (REF615F+Power Meter)	63

2.34	Panel:   SBC-W CT Mot (REF601)	65

2.35	Panel:   SBC-W CT Mot (REF611)	67

2.36	Panel:   SBC-W CT (REF611)	69

2.37	Panel:   SBC-W CT VT Mot (REF611+Power Meter)	71

2.38	Panel:   SBC-W CT VT (REF611+Power Meter)	73

2.39	Panel:   SBC-W CT Mot (REF615F)	75

2.40	Panel:   SBC-W CT (REF615F)	77

2.41	Panel:   SBC-W CT VT Mot (REF615F+Power Meter)	79

2.42	Panel:   SBC-W CT VT (REF615F+Power Meter)	81

2.43	Panel:   SBM CT (REF601)	83

2.44	Panel:   SBM CT (REF611)	85

2.45	Panel:   SBM CT (REF615F)	87

3	General remarks and clarifications	89

4	Routine Tests and Factory Acceptance Test  (FAT)	90

5	Service Proposal	92

5.1	Service	92

5.2	Installation Services	92

5.3	Corrective Services	92

5.4	Preventive Services	93

5.5	Value Added Services	93

5.6	Training Center	93

6	MyRemoteCare	94

# General Specification: Price List 2020 (Unisec 630A 16kA HD4/VD4)

| ## General Data / Type of apparatus |  |  |  |  |
| --- | --- | --- | --- | --- |
| Air insulated MV switchgear for secondary distribution type UniSec |  |  |  |  |
| - Type: | Complete switchgear |  |  |  |
| - Application: | Standard IEC 62271-200 |  |  |  |
| - Additional technical requests: |  |  |  |  |
| - Degree of protection: | IP3X |  |  |  |
| - Internal Arc Classification (IAC): | Front Accessibility (AF) |  |  |  |
| ATTENTION: IAC A-F version - No access to rear and sides of the Swg while is in service. Installation distances to be respected. |  |  |  |  |
| - Type of apparatus: | Switch disconnector type SF6, Circuit breaker type SF6 (HD4/R-Sec) or Vacuum (VD4/R-Sec) |  |  |  |
| - Packing: | Domestic |  |  |  |
| - Ambient temperature (Mim/Max): | -5°C /40°C |  |  |  |
| - Storage temperature: | -5°C |  |  |  |
| - Altitude: | ≤1000 m |  |  |  |
| ## Electrical Data |  |  |  |  |
| - Rated voltage: |  |  | 24kV |  |
| - Service voltage: |  |  | 20kV |  |
| - Power frequency withstand voltage: |  |  | 50kV |  |
| - BIL: |  |  | 125kV |  |
| - Rated frequency: |  |  | 50Hz |  |
| - Rated busbar current: |  |  | 630A |  |
| - Rated short circuit current: |  |  | 16kA |  |
| - Rated short circuit current duration: |  |  | 3s |  |
| - Peak current: |  |  | 40kA |  |
| - Arc test current 1s (According to IEC 62271-200): |  |  | 16 kA |  |

| ## Additional Data |  |  |
| --- | --- | --- |
| - Internal lighting | No |  |
| - Anti Condensation heater of self-regulating type | Yes, in cable compartment |  |
| - Voltage presence indicating system | Fixed lamps, type VPIS |  |
| - Type of key locks interlocking (if selected in functional units) | Giussani |  |
| - Address labels on functional units | Yes |  |
| - Mimic diagrams | Yes |  |
| - Routine test reports | Yes |  |
| - Our ABB standard drawing template | Yes |  |
| - Switchgear colour | RAL 7035 |  |
| - For SF6 CB HD4/R-sec the pressure indicator is not included in price list - For CT with low primary current (below 75A) please consult with ABB Factory |  |  |
| ## Auxiliary supply and wiring data |  |  |
| - Local control voltage: | 230VAC |  |
| - Spring charging motor voltage for CB: | 230VAC |  |
| - Control circuits cross section | 1.5 mm2 |  |
| - Voltage circuits cross section | 2.5 mm2 |  |
| - Current circuits cross section | 2.5 mm2 |  |
| - Earthing circuits cross section | 2.5 mm2 |  |
| - Interconnection circuits cross section | 1.5 mm2 |  |
| - Auxiliary Supply circuits cross section | 2.5 mm2 |  |
| - Wiring cable type | Standard, PVC |  |
| - Wiring cable rated voltage | ABB standard, 0.45/0.75 kV |  |
| - Wiring cable colors | STANDARD |  |
| - Colour of Auxiliary AC | Black |  |
| - Colour of Auxiliary DC | Black |  |
| - Colour of CT circuits | Black |  |
| - Colour of VT circuits | Black |  |
| - Colour of Earthing circuits | Yellow/Green |  |

## Switchgear Accessories

1	Lifting hooks

## Switchgear Composition:  Price List 2020 (Unisec 630A 16kA HD4)

Overall dimensions(*)

| Description | Qty | Weight (Kg) | Width (mm) | Depth (mm) | Heigth(mm) |
| --- | --- | --- | --- | --- | --- |
| SDC (630 A) H01 | 1 | 263 | 500 | 1070 | 1700 |
| SDC CT (630 A) H02 | 1 | 246 | 500 | 1070 | 1700 |
| SDC LA (630 A) H03 | 1 | 213 | 500 | 1070 | 1700 |
| SDC Motorized (630 A) H04 | 1 | 213 | 500 | 1070 | 1700 |
| SFC (No Fuse) (100 A) H05 | 1 | 218 | 500 | 1070 | 1700 |
| SFC Motorized (No Fuse) (100 A) H06 | 1 | 218 | 500 | 1070 | 1700 |
| SFV (6 A) H07 | 1 | 271 | 500 | 1070 | 1700 |
| SFV with Power Meter (6 A) H08 | 1 | 271 | 500 | 1070 | 1700 |
| DRC (630 A) H09 | 1 | 140 | 500 | 1070 | 1700 |
| DRC LA (630 A) H10 | 1 | 140 | 500 | 1070 | 1700 |
| SBC CT (REF601) (630 A) H11 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT VT (REF601 + Power Meter) (630 A) H12 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT VT (REF615F + Power Meter) (630 A) H13 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT Mot (REF601) (630 A) H14 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT LA Mot (REF601) (630 A) H15 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT VT Mot (REF601 + Power Meter) (630 A) H16 | 1 | 551 | 750 | 1180 | 2000 |
| SBC-W CT (REF601) (630 A) H17 | 1 | 516 | 750 | 1180 | 2000 |
| SBC-W CT VT (REF601+ Power Meter) (630 A) H18 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT Mot (REF611) (630 A) H19 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT (REF611) (630 A) H20 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT LA Mot (REF611) (630 A) H21 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT LA (REF611) (630 A) H22 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT VT Mot (REF611 + Power Meter) (630 A) H23 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT VT (REF611 + Power Meter) (630 A) H24 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT VT Mot (REF611 + Power Meter)(ZCT) (630 A) H25 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT VT (REF611 + Power Meter)(ZCT) (630 A) H26 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT Mot (REF615F) (630 A) H27 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT (REF615F) (630 A) H28 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT LA Mot (REF615F) (630 A) H29 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT LA (REF615F) (630 A) H30 | 1 | 516 | 750 | 1180 | 2000 |
| SBC CT VT Mot (REF615F) (630 A) H31 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT VT (REF615F) (630 A) H32 | 1 | 551 | 750 | 1180 | 2000 |
| SBC CT VT Mot (REF615F+ Power Meter) (630 A) H33 | 1 | 551 | 750 | 1180 | 2000 |
| SBC-W CT Mot (REF601) (630 A) H34 | 1 | 516 | 750 | 1180 | 2000 |
| SBC-W CT Mot (REF611) (630 A) H35 | 1 | 516 | 750 | 1180 | 2000 |
| SBC-W CT (REF611) (630 A) H36 | 1 | 516 | 750 | 1180 | 2000 |
| SBC-W CT VT Mot (REF611+ Power Meter) (630 A) H37 | 1 | 551 | 750 | 1180 | 2000 |
| SBC-W CT VT (REF611+ Power Meter) (630 A) H38 | 1 | 551 | 750 | 1180 | 2000 |
| SBC-W CT Mot (REF615F) (630 A) H39 | 1 | 516 | 750 | 1180 | 2000 |
| SBC-W CT (REF615F) (630 A) H40 | 1 | 516 | 750 | 1180 | 2000 |
| SBC-W CT VT Mot (REF615F+ Power Meter) (630 A) H41 | 1 | 551 | 750 | 1180 | 2000 |
| SBC-W CT VT (REF615F+ Power Meter) (630 A) H42 | 1 | 551 | 750 | 1180 | 2000 |
| SBM CT (REF601) (630 A) H43 | 1 | 609 | 750 | 1180 | 2000 |
| SBM CT (REF611) (630 A) H44 | 1 | 609 | 750 | 1180 | 2000 |
| SBM CT (REF615F) (630 A) H45 | 1 | 659 | 750 | 1180 | 2000 |
| Sidewalls |  |  | 54 |  |  |
|  |  | 21658 | 32054 | 1180 | 2000 |

(*)ABB wishes to highlight that values of dimensions and weights provided herein are preliminary and may change after final design preparation, based on final scope of supply and installation details of the switchgear. As a consequence, provided values of dimensions and weights are NOT to be considered as final but only for standard reference purposes.
ACCORDINGLY, YOU EXPRESSLY ACKNOWLEDGE AND AGREE THAT VALUES OF DIMENSIONS AND WEIGHTS PROVIDED HEREIN ARE NEITHER FINAL NOR BINDING AND THAT THE RESULT OF THEIR USE IS NEITHER FEASIBLE NOR ACCURATE NOR ERROR FREE

# Typical Unit Description

## Panel:   SDC

(630 A, 1: H01)

1 Panel type SDC, LSC2 - Switch disconnector unit - 500 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1	Installation and operating manual in English

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   SDC CT

(630 A, 1: H02)

1 Panel type SDC, LSC2 - Switch disconnector unit - 500 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

## Panel:   SDC LA

(630 A, 1: H03)

1 Panel type SDC, LSC2 - Switch disconnector unit - 500 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   SDC Motorized

(630 A, 1: H04)

1 Panel type SDC, LSC2 - Switch disconnector unit - 500 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   SFC (No Fuse)

(100 A, 1: H05)

1 Panel type SFC, LSC2A - Switch-fuse combination unit with cable - 500 mm

1	Cable entry for 1-phase cables up to 95 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 2-spring operating device

1	Tripping coil for opening 230 VAC

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1	Downstream earthing switch with limited making capacity (2kA)

1	Fuse base 500 for fuses 442mm, prepared for fuse CEF 24kV max. 80A

1	Fuse tripping

1	Indication of fuse status

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   SFC Motorized (No Fuse)

(100 A, 1: H06)

1 Panel type SFC, LSC2A - Switch-fuse combination unit with cable - 500 mm

1	Cable entry for 1-phase cables up to 95 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 2-spring operating device

1	Motor control with one push button for charging and one for closing for 2-spring device 230 VAC

1	Tripping Coil for Opening and Closing Included

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1	Downstream earthing switch with limited making capacity (2kA)

1	Fuse base 500 for fuses 442mm, prepared for fuse CEF 24kV max. 80A

1	Fuse tripping

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   SFV

(6 A, 1: H07)

1 Panel type SFV, LSC2A - Switch-fuse combination unit for measuring - 500 mm

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

3 HV fuse 24 kV – 6.3 A (e=442mm) - ABB CEF

1	Fuse base 500 for fuses 442mm

1	Fuse upper support

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	VOLTAGE SELECTOR SWITCH

1	ANALOG AC VOLTMETER Class 1.5

## Panel:   SFV with Power Meter

(6 A, 1: H08)

1 Panel type SFV, LSC2A - Switch-fuse combination unit for measuring - 500 mm

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

3 HV fuse 24 kV – 6.3 A (e=442mm) - ABB CEF

1	Fuse base 500 for fuses 442mm

1	Fuse upper support

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   DRC

(630 A, 1: H09)

1 Panel type DRC, LSC1 - Direct riser unit with cable - 500 mm

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   DRC LA

(630 A, 1: H10)

1 Panel type DRC, LSC1 - Direct riser unit with cable - 500 mm

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 Low voltage compartment for 500 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

## Panel:   SBC CT (REF601)

(630 A, 1: H11)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

## Panel:   SBC CT VT (REF601 + Power Meter)

(630 A, 1: H12)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC CT VT (REF615F + Power Meter)

(630 A, 1: H13)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	POWER METER CLASS 0.5 SINGLE TARIFF

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT Mot (REF601)

(630 A, 1: H14)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

## Panel:   SBC CT LA Mot (REF601)

(630 A, 1: H15)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

## Panel:   SBC CT VT Mot (REF601 + Power Meter)

(630 A, 1: H16)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC-W CT (REF601)

(630 A, 1: H17)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

## Panel:   SBC-W CT VT (REF601+Power Meter)

(630 A, 1: H18)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER, 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	POWER METER CLASS 0.5 SINGLE TARIFF

1	RELAY REF601 IEC

## Panel:   SBC CT Mot (REF611)

(630 A, 1: H19)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBC CT (REF611)

(630 A, 1: H20)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBC CT LA Mot (REF611)

(630 A, 1: H21)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBC CT LA (REF611)

(630 A, 1: H22)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBC CT VT Mot (REF611 + Power Meter)

(630 A, 1: H23)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC CT VT (REF611 + Power Meter)

(630 A, 1: H24)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC CT VT Mot (REF611 + Power Meter)(ZCT)

(630 A, 1: H25)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC CT VT (REF611 + Power Meter )(ZCT)

(630 A, 1: H26)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC CT Mot (REF615F)

(630 A, 1: H27)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT (REF615F)

(630 A, 1: H28)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT LA Mot (REF615F)

(630 A, 1: H29)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT LA (REF615F)

(630 A, 1: H30)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

3	Surge arresters 20kV (MWD type)

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT VT Mot (REF615F)

(630 A, 1: H31)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT VT (REF615F)

(630 A, 1: H32)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC CT VT Mot (REF615F+Power Meter)

(630 A, 1: H33)

1 Panel type SBC, LSC2A - Switch-disconnector unit with removable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER,W/O FUSE 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	POWER METER CLASS 0.5 SINGLE TARIFF

1	RELAY REF615 IEC CONF. F

## Panel:   SBC-W CT Mot (REF601)

(630 A, 1: H34)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

## Panel:   SBC-W CT Mot (REF611)

(630 A, 1: H35)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBC-W CT (REF611)

(630 A, 1: H36)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBC-W CT VT Mot (REF611+Power Meter)

(630 A, 1: H37)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER, 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC-W CT VT (REF611+Power Meter)

(630 A, 1: H38)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER, 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

1	POWER METER CLASS 0.5 SINGLE TARIFF

## Panel:   SBC-W CT Mot (REF615F)

(630 A, 1: H39)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC-W CT (REF615F)

(630 A, 1: H40)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

## Panel:   SBC-W CT VT Mot (REF615F+Power Meter)

(630 A, 1: H41)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Motor control operation for 1-spring device 230 VAC

1	Auxiliary contacts for switch-disconnector closed

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER, 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	POWER METER CLASS 0.5 SINGLE TARIFF

1	RELAY REF615 IEC CONF. F

## Panel:   SBC-W CT VT (REF615F+Power Meter)

(630 A, 1: H42)

1 Panel type SBC-W, LSC2A - Switch-disconnector unit with withdrawable circuit-breaker - 750 mm

1	Cable entry for 1-phase cables up to 300 mm2

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 Earthing switch, full making capacity

1	Interlocked with Gsec

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1	Auxiliary contacts for switch-disconnector closed

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

3 VOLTAGE TRANSFORMER, 20kV/R3:110V/R3,0.5 25VA

3	Core 1 : Us=0,11/V3 kV; 25 VA; 0.5

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	POWER METER CLASS 0.5 SINGLE TARIFF

1	RELAY REF615 IEC CONF. F

## Panel:   SBM CT (REF601)

(630 A, 1: H43)

1 Panel type SBM, LSC2A - Switch disconnector and removable circuit breaker unit for measuring - 750 mm

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1 GSec - Three position switch-disconnector and with earthing switch

1	Auxiliary contacts for switch-disconnector closed in right unit

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1	key locks lock for CB open

1	ABB standard key locks for line open / closed free

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF601 IEC

## Panel:   SBM CT (REF611)

(630 A, 1: H44)

1 Panel type SBM, LSC2A - Switch disconnector and removable circuit breaker unit for measuring - 750 mm

1	Voltage presence indicator with fixed lamps type VPIS

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1 GSec - Three position switch-disconnector and with earthing switch

1	Auxiliary contacts for switch-disconnector closed in right unit

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1	key locks lock for CB open

1	ABB standard key locks for line open / closed free

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF611 IEC

## Panel:   SBM CT (REF615F)

(630 A, 1: H45)

1 Panel type SBM, LSC2A - Switch disconnector and removable circuit breaker unit for measuring - 750 mm

1	Voltage presence indicator with fixed lamps type VPIS

1	Operating Handle for Switch-disconnector and Earthing switch

1	Anti condensation heater for cable compartment 230VAC

1 GSec - Three position switch-disconnector and with earthing switch and 1-spring operating device

1 GSec - Three position switch-disconnector and with earthing switch

1	Auxiliary contacts for switch-disconnector closed in right unit

1	Auxiliary contacts for earthing switch

- Set of 4 pcs change-over

- Set of 4 pcs change-over

1	key locks lock for CB open

1	ABB standard key locks for line open / closed free

1 Wide low voltage compartment for 750 mm functional unit

1	Necessary auxiliary circuit and MCBs are automatically included as per factory stds according panel configuration/selections.

1 Circuit breaker, 24kV, 630A, 16kA

1	Closing push button

1	Opening push button

1	Mechanical signalling device for closing springs

1	Mechanical signalling device for circuit breaker

1	Operation counter

1	Set of 5 auxiliary contacts

1	Lock push buttons

1	Shunt opening release 230 VAC

1	Shunt closing release 230 VAC

1	Spring charging motor 230 VAC

1	Cover for open/close push buttons

3 CURRENT TRANSFORMER, …../5-5A,0.5 5P10+C (set 1, Ip=….. A, Polarity: P1 on busbar side)

3	Core1 : Is=5A; 10VA; 0.5; fs

3	Core2 : Is=5A; 7.5VA; 5P10

3	Voltage divider

Frequency: 50Hz

Additional Data

1	PUSH BUTTON RED

1	PUSH BUTTON GREN

1	PILOT LIGHT RED (230V AC)

1	PILOT LIGHT GREEN (230V AC)

1	SELECTOR SWITCH LOCAL-REMOTE

1	CURRENT TEST BLOCK

1	RELAY REF615 IEC CONF. F

# General remarks and clarifications

1) Both the offered equipment and switchboards are in accordance with the international IEC Standards.

2) The switchboard will be tested in the ABB workshops, according to the normal tests for acceptance of switchboards foreseen by IEC Standards.

3) Our quotation does not include:

- Power cables terminals and connections

- Erection and commissioning

- On site tests

- Spare parts

Available as option if required and listed in “Switchgear Accessory” chapter if included.

Auxiliary Voltage will be the same of the Switchgear.

If Included, must be considered for replacement of an existing equipment and not for future additions not according with delivered product.

Installation shall be done according to ABB Training Level “L1-L2-L3” by qualified person.

- Engineering and design beyond our scope of supply:

  - relay setting calculations

  - relay protection coordination/selectivity study

  - ITs calculations

  - network study

  - calculation of the short circuit current

  - pressure calculation of the building

  - etc..

- All LV, MV control and power cables out of our panels and related cable sealing

- Means of hoisting for site unloading and transportation

- Factory tests other than routine IEC tests

- Any floor mounting accessory/material (metallic profiles, bolts, nuts, etc.) needed for site erection

- laptop or computer for setting of control and protection unit

- Training

- Civil works

- Any other equipment other than specified in our technical schedule.

- All what is not expressly described (excluding those accessories or devices which are essential for a good performance of the switchboard).

4) The following documentation in English language will be part of our supply:

- For approval (twofold):

  - Front and single line of the switchboards

  - Front of each typical unit

  - Foundation drawings

  - Schematic diagram of each typical unit

- Final as-built (threefold) in addition to the above mentioned documentation:

  - Equipment list

  - Catalogues of the switchboard, and circuit breakers

  - Instruction manuals of the switchboards and circuit breakers

  - Catalogues of the protection relays

We engage ourselves to submit to your technicians the as-built documentation at the moment of the acceptance test of each lot of the supply in order to get your formal acceptance of the same.

Relevant documentation will be sent to you by courier within 10 working days from the shipment of the lot itself.

In case such documentation will be considered by you defective and/or not sufficient you should communicate us, by registered letter, within 15 days from the receipt of the documentation itself the degree of in-completion and/or the requested modifications. In case we will not get any comment from you within or later than the 15th day from the receipt of the documentation it is agreed that you could not oppose any argument about the in-completion of the documentation in order to the observance of agreed term of payment.

5) The treatment and painting cycle will according to our standards and the colour of external painted surfaces will be RAL7035 (if not differently written into additional data section).

6) Our internal quality system is certified as per UNI EN ISO 9001 (ISO 9001).

7) Our quotation has been processed considering the following documentation:

With the following remarks and/or specifications:

# Routine Tests

A1.2 Routine Test

Activities considered for the Routine Tests are:

  - Visual inspection and check of dimensions

  - Mechanical operation tests

  - Electrical - logic operation and wiring test

  - Check of measurement and protection circuits

  - Power frequency voltage insulation test of the aux. circuits

  - Power frequency voltage insulation tests of main circuits

  - Measurement of the insulation resistance on main circuits

  - Measurement of the ohmic resistance of the main circuits

Following detailed list of the activities.

A1.2.1 Visual inspection and check of dimensions

1. Check that the units are built according to the purchase order and project requirements.

2. Check of the correspondence of all components installed according to the switchgear drawings.

3. Check that the wording and positioning of the data plates comply with the drawings.

4. Check that the painting complies with the requirements.

A1.2.2 Mechanical operation tests

1. The purpose of these tests is to carry out the mechanical operation tests on the typical panels in the following way:

2. Switching devices shall be operated, removed and inserted in order to  check the interlocks

3. Check of the correct accessibility to the circuit breaker compartment.

4. Check of the correct closing of the doors.

5. Check that circuit breaker is prevented from racking in and out when it is closed; the racking in and out is allowed only with the circuit breaker in open position.

6. Check that the circuit breaker (*) is prevented from closing during racking in and out.

7. Check that the circuit breaker is prevented from racking in when the door is open (Optional).

8. Check that the door is prevented from opening when the circuit breaker is in racked in position (Optional).

9. Check that the circuit breaker is prevented from racking in when the earthing switch is closed.

10. Check that the earthing switch cannot be closed when the circuit breaker is racked in.

11. Check that the cable compartment door cannot be opened if the earthing switch is open (Optional).

12. Check that the earthing switch cannot be opened if the cable compartment door is open (Optional).

13. Check of the interchangeability of the moving part of circuit-breakers that have the same rated current.

14. Check of the functionality of the key interlocks, if provided, and the difference in code (Optional).

15. Check of the signalling of the mechanical indicators.

16. In case of V.T.’s truck in the circuit breaker compartment (Metering or Bus Riser units), check of the correct insertion of the main contacts.

(*)  The test shall be carried out in the same way in case of other removable apparatus (e.g. contactor).

A1.2.3 Electrical - logic operation and wiring test

The purpose of these tests is to carry out the electrical operation tests on the typical panels in the following way:

1. Check of the electrical functionality with reference to electric drawings.

2. Check of logic functions of signalling, blocking and operation in compliance with the logic diagram.

A1.2.4 Check of measurement and protection circuits

The purpose of these tests is to carry out the measurement and protection circuits on the typical panels in the following way:

1. By means of primary current injection:

a) The correct ratio of the current transformers.

b) The measurements of instruments and transducers.

c) The tripping of the protection relays.

d) have to be verified.

2. By applying a secondary voltage:

a) The voltmeter circuits.

b) The measurements of instruments and transducers.

c) The tripping of the protection relays.

have to be verified.

By applying a low primary voltage (110 V three-phase), the correct electrical connection of the VT’s has to be verified.

Contact us

PT. ABB Sakti Industri Electrification Products Division

| PT. ABB Sakti Industri World Trade Center I, 15th Floor Jl. Jend. Sudirman Kav 29-31 Jakarta, 12920 - Indonesia Phone : +62 21 2551 5555 Fax : +62 21 2551 5566 www. abb.com |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

www.abb.com