## Fuse coord. OTDC S2.0 100-250A
Fuse coordination for OTDC S2.0 Series (OTDC100...250_G_11-ESS) OTDC100...250G11-ESS for 1000Vdc, IEC only OTDC100...250UG11-ESS for 1000Vdc, IEC and UL98B OTDC100...250GV11-ESS for 1500Vdc, IEC only OTDC100...250UGV11-ESS for 1500Vdc, IEC and UL98B More detailed info, please contact us Global Sales Support, switch.technicalservice@fi.abb.com
FUSE DATA
Fuse Manuf. | Order code | Size | Type | Rated Voltage | Rated Current | Rated Breaking Capacity | Self certified Conditional Short Circuit Withstand current
Littelfuse | PSX1XLDB0100X | NH1XL | aBat | 1500 | 100 | 250 | 50
Littelfuse | PSX1XLDB0125X | NH1XL | aBat | 1500 | 125 | 250 | 50
Littelfuse | PSX1XLDB0160X | NH1XL | aBat | 1500 | 160 | 250 | 50
Littelfuse | PSX1XLDB0200X | NH1XL | aBat | 1500 | 200 | 250 | 50
Littelfuse | PSX1XLDB0250X | NH1XL | aBat | 1500 | 250 | 250 | 50
SIBA | 50 271 06 100 | SM 140 | aR | 1500 | 100 | 100 | 50
SIBA | 50 271 06 125 | SM 140 | aR | 1500 | 125 | 100 | 50
SIBA | 90 441 25 100 | NH1XL | aR | 1500 | 100 | 100 | 50
SIBA | 90 441 25 125 | NH1XL | aR | 1500 | 125 | 100 | 50
SIBA | 90 441 25 160 | NH1XL | aR | 1500 | 160 | 100 | 50
SIBA | 90 441 25 200 | NH1XL | aR | 1500 | 200 | 100 | 50
SIBA | 90 223 38 100 | SQB-DC0 | aR | 1500 | 100 | 100 | 50
SIBA | 90 223 38 125 | SQB-DC0 | aR | 1500 | 125 | 100 | 50
SIBA | 90 223 38 160 | SQB-DC0 | aR | 1500 | 160 | 100 | 50
SIBA | 90 223 38 180 | SQB-DC0 | aR | 1500 | 180 | 100 | 50
SIBA | 90 223 38 200 | SQB-DC0 | aR | 1500 | 200 | 100 | 50
SIBA | 90 203 38 125 | SQB-DC2 | aR | 1500 | 125 | 100 | 50
SIBA | 90 203 38 160 | SQB-DC2 | aR | 1500 | 160 | 100 | 50
SIBA | 90 203 38 200 | SQB-DC2 | aR | 1500 | 200 | 100 | 50
SIBA | 90 203 38 250 | SQB-DC2 | aR | 1500 | 250 | 100 | 50
SIBA | 90 213 38 250 | SQB-DC2-2 | aR | 1500 | 250 | 170 | 50
SIBA | 90 443 25 200 | NH3L | aR | 1500 | 200 | 100 | 50
SIBA | 90 443 25 250 | NH3L | aR | 1500 | 250 | 100 | 50
Mersen | D72SG120V160QF (K079428) | 72 | aR | 1500 | 160 | 100 | 50
Mersen | D72SG120V200QF (L079429) | 72 | aR | 1500 | 200 | 100 | 50
Mersen | D72SG120V250QF (M079430) | 72 | aR | 1500 | 250 | 100 | 50
Sinofuse | RSZ307-3-RAZ-100A1500V | NH3 | aR | 1500 | 100 | 250 | 50
Sinofuse | RSZ307-3-RAZ-125A1500V | NH3 | aR | 1500 | 125 | 250 | 50
Sinofuse | RSZ307-3-RAZ-160A1500V | NH3 | aR | 1500 | 160 | 250 | 50
Sinofuse | RSZ307-3-RAZ-200A1500V | NH3 | aR | 1500 | 200 | 250 | 50
Sinofuse | RSZ307-3-RAZ-250A1500V | NH3 | aR | 1500 | 250 | 250 | 50
Mersen | ABAT15AA100GI/BI | - | aR/aBat | 1500 | 100 | 250 | 50
Mersen | ABAT15AA125GI/BI | - | aR/aBat | 1500 | 125 | 250 | 50
Mersen | ABAT15AA160GI/BI | - | aR/aBat | 1500 | 160 | 250 | 50
Mersen | ABAT15AA200GI/BI | - | aR/aBat | 1500 | 200 | 250 | 50
Mersen | ABAT15AA250GI/BI | - | aR/aBat | 1500 | 250 | 250 | 50
Mersen | ABAT15AD200GI/BI | - | aR/aBat | 1500 | 200 | 250 | 50
Mersen | ABAT15AD250GI/BI | - | aR/aBat | 1500 | 250 | 250 | 50
ETI | 004110 653/660/667 | NH1XL | gBat | 1500 | 100 | 100 | 50
ETI | 004110 654/661/668 | NH1XL | gBat | 1500 | 125 | 100 | 50
ETI | 004110 655/662/669 | NH1XL | gBat | 1500 | 160 | 100 | 50
ETI | 004110 656/663/670 | NH1XL | gBat | 1500 | 200 | 100 | 50
ETI | 004110 671/673/675 | NH2XL | gBat | 1500 | 200 | 100 | 50
ETI | 004110 672/674/676 | NH2XL | gBat | 1500 | 250 | 100 | 50
Mersen | 15NH1XLGBAT100 | NH1XL | gBat | 1500 | 100 | 50 | 50
Mersen | 15NH1XLGBAT125 | NH1XL | gBat | 1500 | 125 | 50 | 50
Mersen | 15NH2XLGBAT125 | NH2XL | gBat | 1500 | 125 | 50 | 50
Mersen | 15NH2XLGBAT160 | NH2XL | gBat | 1500 | 160 | 50 | 50
Mersen | 15NH2XLGBAT200 | NH2XL | gBat | 1500 | 200 | 50 | 50
Mersen | 15NH2XLGBAT250 | NH2XL | gBat | 1500 | 250 | 50 | 50
Mersen | 15NH3LGBAT160 | NH3L | gBat | 1500 | 160 | 150 | 50
Mersen | 15NH3LGBAT200 | NH3L | gBat | 1500 | 200 | 150 | 50
Mersen | 15NH3LGBAT250 | NH3L | gBat | 1500 | 250 | 150 | 50
Eaton-Bussmann | BSF-250G-3XL15 | NH3XL | gBat | 1500 | 250 | 100 | 50
Eaton-Bussmann | BSF-100G-NH110 | NH1 | gBat | 1000 | 100 | 100 | 50
Eaton-Bussmann | BSF-125G-NH110 | NH1 | gBat | 1000 | 125 | 100 | 50
Eaton-Bussmann | BSF-160G-NH110 | NH1 | gBat | 1000 | 160 | 100 | 50
Eaton-Bussmann | BSF-200G-NH110 | NH1 | gBat | 1000 | 200 | 100 | 50
Eaton-Bussmann | BSF-160G-NH210 | NH2 | gBat | 1000 | 160 | 100 | 50
Eaton-Bussmann | BSF-200G-NH210 | NH2 | gBat | 1000 | 200 | 100 | 50
Eaton-Bussmann | BSF-250G-NH210 | NH2 | gBat | 1000 | 250 | 100 | 50
Mersen | 10NH1GBAT100 | NH1 | gBat | 1000 | 100 | 50 | 50
Mersen | 10NH1GBAT125 | NH1 | gBat | 1000 | 125 | 50 | 50
Mersen | 10NH1GBAT160 | NH1 | gBat | 1000 | 160 | 50 | 50
Mersen | 10NH2GBAT200 | NH2 | gBat | 1000 | 200 | 50 | 50
Mersen | 10NH2GBAT250 | NH2 | gBat | 1000 | 250 | 50 | 50
ETI | 004110 695/746/752 | NH01XL | gPV | 1500 | 100 | 30 | 30
ETI | 004110 696/747/753 | NH01XL | gPV | 1500 | 125 | 30 | 30
ETI | 004110 697/748/754 | NH01XL | gPV | 1500 | 160 | 30 | 30
ETI | 004110 562/593/608 | NH1XL | gPV | 1500 | 100 | 30 | 30
ETI | 004110 563/594/609 | NH1XL | gPV | 1500 | 125 | 30 | 30
ETI | 004110 564/595/610 | NH1XL | gPV | 1500 | 160 | 30 | 30
ETI | 004110 565/596/611 | NH1XL | gPV | 1500 | 200 | 30 | 30
ETI | 004110 566/597/612 | NH2XL | gPV | 1500 | 200 | 30 | 30
ETI | 004110 567/598/613 | NH2XL | gPV | 1500 | 250 | 30 | 30
SIBA | 20 041 28 100 | NH1XL | gPV | 1500 | 100 | 100 | 50
SIBA | 20 041 28 125 | NH1XL | gPV | 1500 | 125 | 100 | 50
SIBA | 20 041 28 160 | NH1XL | gPV | 1500 | 160 | 100 | 50
SIBA | 20 041 28 200 | NH1XL | gPV | 1500 | 200 | 100 | 50
SIBA | 20 042 29 160 | NH2XL | gPV | 1500 | 160 | 50 | 50
SIBA | 20 042 29 200 | NH2XL | gPV | 1500 | 200 | 50 | 50
SIBA | 20 042 29 250 | NH2XL | gPV | 1500 | 250 | 50 | 50
SIBA | 20 243 28 200 | NH3L | gPV | 1500 | 200 | 100 | 50
SIBA | 20 243 28 250 | NH3L | gPV | 1500 | 250 | 100 | 50
Mersen | HP15NH1XLGPV100 | NHXL1 | gPV | 1500 | 100 | 50 | 50
Mersen | HP15NH1XLGPV125 | NHXL1 | gPV | 1500 | 125 | 50 | 50
Mersen | HP15NH2XLGPV125 | NHXL2 | gPV | 1500 | 125 | 50 | 50
Mersen | HP15NH2XLGPV160 | NHXL2 | gPV | 1500 | 160 | 50 | 50
Mersen | HP15NH2XLGPV200 | NHXL2 | gPV | 1500 | 200 | 50 | 50
Mersen | HP15NH2XLGPV250 | NHXL2 | gPV | 1500 | 250 | 50 | 50
Mersen | HP15NH3LGPV160 | NH3L | gPV | 1500 | 160 | 50 | 50
Mersen | HP15NH3LGPV200 | NH3L | gPV | 1500 | 200 | 50 | 50
Mersen | HP15NH3LGPV250 | NH3L | gPV | 1500 | 250 | 50 | 50
Littelfuse | SPNH100.X | NH1XL | gPV | 1500 | 100 | 30 | 30
Littelfuse | SPNH125.X | NH1XL | gPV | 1500 | 125 | 30 | 30
Littelfuse | SPNH160.X | NH1XL | gPV | 1500 | 160 | 30 | 30
Littelfuse | SPNH200.X | NH1XL | gPV | 1500 | 200 | 30 | 30
Littelfuse | SPNH200.X2XL | NH2XL | gPV | 1500 | 200 | 30 | 30
Littelfuse | SPNH250.X2XL | NH2XL | gPV | 1500 | 250 | 30 | 30
Eaton-Bussmann | PV-100A-01XL-15 | NH01XL | gPV | 1500 | 100 | 30 | 30
Eaton-Bussmann | PV-125A-01XL-15 | NH01XL | gPV | 1500 | 125 | 30 | 30
Eaton-Bussmann | PV-160A-01XL-12 | NH01XL | gPV | 1500 | 160 | 30 | 30
Eaton-Bussmann | PV-100A-1XL-15 | NH1XL | gPV | 1500 | 100 | 30 | 30
Eaton-Bussmann | PV-125A-1XL-15 | NH1XL | gPV | 1500 | 125 | 30 | 30
Eaton-Bussmann | PV-160A-1XL-15 | NH1XL | gPV | 1500 | 160 | 30 | 30
Eaton-Bussmann | PV-200A-1XL-15 | NH1XL | gPV | 1500 | 200 | 30 | 30
Eaton-Bussmann | PV-125A-2XL-15 | NH2XL | gPV | 1500 | 125 | 30 | 30
Eaton-Bussmann | PV-160A-2XL-15 | NH2XL | gPV | 1500 | 160 | 30 | 30
Eaton-Bussmann | PV-200A-2XL-15 | NH2XL | gPV | 1500 | 200 | 30 | 30
Eaton-Bussmann | PV-250A-2XL-15 | NH2XL | gPV | 1500 | 250 | 30 | 30
Eaton-Bussmann | PV-250A-3L-15 | NH3L | gPV | 1500 | 250 | 100 | 50
Mersen | HP12NH1XLGPV125 | NH1XL | gPV | 1250 | 125 | 50 | 50
Mersen | HP12NH1XLGPV160 | NH1XL | gPV | 1250 | 160 | 50 | 50
Mersen | HP12NH2XLGPV200 | NH2XL | gPV | 1250 | 200 | 50 | 50
Mersen | HP12NH2XLGPV250 | NH2XL | gPV | 1250 | 250 | 50 | 50
Mersen | HP12NH3LGPV250 | NH3L | gPV | 1250 | 250 | 50 | 50
ETI | 004110 428 | NH1XL | gPV | 1100 | 100 | 10 | 10
ETI | 004110 429 | NH1XL | gPV | 1100 | 125 | 10 | 10
ETI | 004110 410 | NH1XL | gPV | 1100 | 160 | 10 | 10
ETI | 004110 411 | NH1XL | gPV | 1100 | 200 | 10 | 10
ETI | 004110 430 | NH2XL | gPV | 1100 | 200 | 10 | 10
ETI | 004110 413 | NH2XL | gPV | 1100 | 250 | 10 | 10
ETI | 004110 451 | NH3L | gPV | 1100 | 200 | 10 | 10
ETI | 004110 452 | NH3L | gPV | 1100 | 224 | 10 | 10
ETI | 004110 453 | NH3L | gPV | 1100 | 250 | 10 | 10
ETI | 004110 393 | NH1XL | gPV | 1100 | 100 | 10 | 10
ETI | 004110 394 | NH1XL | gPV | 1100 | 125 | 10 | 10
ETI | 004110 395 | NH1XL | gPV | 1100 | 160 | 10 | 10
ETI | 004110 396 | NH1XL | gPV | 1100 | 200 | 10 | 10
ETI | 004110 397 | NH2XL | gPV | 1100 | 200 | 10 | 10
ETI | 004110 398 | NH2XL | gPV | 1100 | 250 | 10 | 10
ETI | 004110 387 | NH0 | gPV | 1000 | 100 | 20 | 20
ETI | 004110 388 | NH0 | gPV | 1000 | 125 | 20 | 20
ETI | 004110 389 | NH0 | gPV | 1000 | 160 | 20 | 20
ETI | 004110 377 | NH1C | gPV | 1000 | 100 | 20 | 20
ETI | 004110 378 | NH1C | gPV | 1000 | 125 | 20 | 20
ETI | 004110 379 | NH1C | gPV | 1000 | 160 | 20 | 20
ETI | 004110 342 | NH1 | gPV | 1000 | 200 | 30 | 30
ETI | 004110 343 | NH2 | gPV | 1000 | 200 | 30 | 30
ETI | 004110 344 | NH2 | gPV | 1000 | 250 | 30 | 30
ETI | 004110 456 | NH3 | gPV | 1000 | 160 | 30 | 30
ETI | 004110 455 | NH3 | gPV | 1000 | 200 | 30 | 30
ETI | 004110 458 | NH3 | gPV | 1000 | 250 | 30 | 30
ETI | 004110 646 | NH1XL | gPV | 1000 | 250 | 30 | 30
Eaton-Bussmann | PV-100ANH1 | NH1 | gPV | 1000 | 100 | 50 | 50
Eaton-Bussmann | PV-110ANH1 | NH1 | gPV | 1000 | 110 | 50 | 50
Eaton-Bussmann | PV-125ANH1 | NH1 | gPV | 1000 | 125 | 50 | 50
Eaton-Bussmann | PV-160ANH1 | NH1 | gPV | 1000 | 160 | 50 | 50
Eaton-Bussmann | PV-175ANH1 | NH1 | gPV | 1000 | 175 | 50 | 50
Eaton-Bussmann | PV-200ANH1 | NH1 | gPV | 1000 | 200 | 50 | 50
Eaton-Bussmann | PV-160ANH2 | NH2 | gPV | 1000 | 160 | 50 | 50
Eaton-Bussmann | PV-200ANH2 | NH2 | gPV | 1000 | 200 | 50 | 50
Eaton-Bussmann | PV-250ANH2 | NH2 | gPV | 1000 | 250 | 50 | 50
Eaton-Bussmann | PV-100A-01XL | NH01XL | gPV | 1000 | 100 | 50 | 50
Eaton-Bussmann | PV-125A-01XL | NH01XL | gPV | 1000 | 125 | 50 | 50
Eaton-Bussmann | PV-160A-01XL | NH01XL | gPV | 1000 | 160 | 50 | 50
Eaton-Bussmann | PV-160A-2XL | NH2XL | gPV | 1000 | 160 | 33 | 30
Eaton-Bussmann | PV-200A-2XL | NH2XL | gPV | 1000 | 200 | 33 | 30
Eaton-Bussmann | PV-250A-2XL | NH2XL | gPV | 1000 | 250 | 33 | 30
Mersen | HP10NH1GPV100 | NH1 | gPV | 1000 | 100 | 50 | 50
Mersen | HP10NH1GPV125 | NH1 | gPV | 1000 | 125 | 50 | 50
Mersen | HP10NH1GPV160 | NH1 | gPV | 1000 | 160 | 50 | 50
Mersen | HP10NH2GPV200 | NH2 | gPV | 1000 | 200 | 50 | 50
Mersen | HP10NH2GPV250 | NH2 | gPV | 1000 | 250 | 50 | 50
SIBA | 20 243 36 100 | NH3L | gR | 1500 | 100 | 170 | 50
SIBA | 20 243 36 125 | NH3L | gR | 1500 | 125 | 170 | 50
SIBA | 20 243 36 160 | NH3L | gR | 1500 | 160 | 170 | 50
SIBA | 20 243 36 200 | NH3L | gR | 1500 | 200 | 170 | 50
SIBA | 20 243 36 250 | NH3L | gR | 1500 | 250 | 170 | 50

## Fuse coord. OTDC M 250-630A
Fuse coordination for OTDC M Series (OTDC250…630_F_11-ESS) OTDC250…630F11-ESS for 1000Vdc, IEC only OTDC250…600UF11-ESS for 1000Vdc, IEC and UL98B OTDC250…630FV11-ESS for 1500Vdc, IEC only OTDC250…600UFV11-ESS for 1500Vdc, IEC and UL98B More detailed info, please contact us Global Sales Support, switch.technicalservice@fi.abb.com
FUSE DATA
Fuse Manuf. | Order code | Size | Type | Rated Voltage | Rated Current | Rated Breaking Capacity | Self certified Conditional Short Circuit Withstand current
Littelfuse | PSX1XLDB0250X | NH1XL | aBat | 1500 | 250 | 250 | 50
Littelfuse | PSX1XLDB0280X | NH1XL | aBat | 1500 | 280 | 250 | 50
Littelfuse | PSX1XLDB0315X | NH1XL | aBat | 1500 | 315 | 250 | 50
Littelfuse | PSX1XLDB0350X | NH1XL | aBat | 1500 | 350 | 250 | 50
Littelfuse | PSX1XLDB0400X | NH1XL | aBat | 1500 | 400 | 250 | 50
Littelfuse | PSX1XLDB0450X | NH1XL | aBat | 1500 | 450 | 250 | 50
Littelfuse | PSX1XLDB0500X | NH1XL | aBat | 1500 | 500 | 250 | 50
Littelfuse | PSX1XLDB0550X | NH1XL | aBat | 1500 | 550 | 250 | 50
Littelfuse | PSX1XLDB0630X | NH1XL | aBat | 1500 | 630 | 250 | 50
Littelfuse | PSX3XLDB0450X | NH3XL | aBat | 1500 | 450 | 250 | 50
Littelfuse | PSX3XLDB0500X | NH3XL | aBat | 1500 | 500 | 250 | 50
Littelfuse | PSX3XLDB0550X | NH3XL | aBat | 1500 | 550 | 250 | 50
Littelfuse | PSX3XLDB0630X | NH3XL | aBat | 1500 | 630 | 250 | 50
SIBA | 90 203 38 250 | SQB-DC2 | aR | 1500 | 250 | 100 | 50
SIBA | 90 203 38 300 | SQB-DC2 | aR | 1500 | 300 | 100 | 50
SIBA | 90 203 38 315 | SQB-DC2 | aR | 1500 | 315 | 100 | 50
SIBA | 90 203 38 350 | SQB-DC2 | aR | 1500 | 350 | 100 | 50
SIBA | 90 203 38 400 | SQB-DC2 | aR | 1500 | 400 | 100 | 50
SIBA | 90 213 38 250 | SQB-DC2-2 | aR | 1500 | 250 | 170 | 50
SIBA | 90 213 38 320 | SQB-DC2-2 | aR | 1500 | 320 | 170 | 50
SIBA | 90 213 38 400 | SQB-DC2-2 | aR | 1500 | 400 | 170 | 50
SIBA | 90 213 38 500 | SQB-DC2-2 | aR | 1500 | 500 | 170 | 50
SIBA | 90 213 38 600 | SQB-DC2-2 | aR | 1500 | 600 | 170 | 50
SIBA | 90 213 38 630 | SQB-DC2-2 | aR | 1500 | 630 | 170 | 50
SIBA | 90 443 25 250 | NH3L | aR | 1500 | 250 | 100 | 50
SIBA | 90 443 25 315 | NH3L | aR | 1500 | 315 | 100 | 50
SIBA | 90 443 25 350 | NH3L | aR | 1500 | 350 | 100 | 50
SIBA | 90 443 25 400 | NH3L | aR | 1500 | 400 | 100 | 50
SIBA | 90 443 25 450 | NH3L | aR | 1500 | 450 | 100 | 50
SIBA | 90 443 25 500 | NH3L | aR | 1500 | 500 | 100 | 50
SIBA | 90 443 25 550 | NH3L | aR | 1500 | 550 | 100 | 50
SIBA | 90 443 25 630 | NH3L | aR | 1500 | 630 | 100 | 50
SIBA | 90 392 25 630 | SQB-DC154 | aR | 1500 | 630 | 100 | 50
Mersen | D72SG120V250QF (M079430) | 72 | aR | 1500 | 250 | 100 | 50
Mersen | D72SG120V315QF (N079431) | 72 | aR | 1500 | 315 | 100 | 50
Mersen | D72SG120V350QF (Q085574) | 72 | aR | 1500 | 350 | 100 | 50
Mersen | D72SG120V400QF (P079432) | 72 | aR | 1500 | 400 | 100 | 50
Mersen | D72SG120V420QF (Q079433) | 72 | aR | 1500 | 420 | 100 | 50
Sinofuse | RSZ307-3-RAZ-250A1500V | NH3 | aR | 1500 | 250 | 250 | 50
Sinofuse | RSZ307-3-RAZ-315A1500V | NH3 | aR | 1500 | 315 | 250 | 50
Sinofuse | RSZ307-3-RAZ-350A1500V | NH3 | aR | 1500 | 350 | 250 | 50
Sinofuse | RSZ307-3-RAZ-400A1500V | NH3 | aR | 1500 | 400 | 250 | 50
Sinofuse | RSZ307-3-RAZ-450A1500V | NH3 | aR | 1500 | 450 | 250 | 50
Mersen | ABAT15AA250GI/BI | - | aR/aBat | 1500 | 250 | 250 | 50
Mersen | ABAT15AD250GI/BI | - | aR/aBat | 1500 | 250 | 250 | 50
Mersen | ABAT15AD300GI/BI | - | aR/aBat | 1500 | 300 | 250 | 50
Mersen | ABAT15AD350GI/BI | - | aR/aBat | 1500 | 350 | 250 | 50
Mersen | ABAT15AD400GI/BI | - | aR/aBat | 1500 | 400 | 250 | 50
Mersen | ABAT15AD450GI/BI | - | aR/aBat | 1500 | 450 | 250 | 50
Mersen | ABAT15AD500GI/BI | - | aR/aBat | 1500 | 500 | 250 | 50
Mersen | ABAT15C500AIA | - | aR/aBat | 1500 | 500 | 250 | 50
Mersen | ABAT15C550AIA | - | aR/aBat | 1500 | 550 | 250 | 50
Mersen | ABAT15C630AIA | - | aR/aBat | 1500 | 630 | 250 | 50
ETI | 004110 672/674/676 | NH2XL | gBat | 1500 | 250 | 100 | 50
ETI | 004110 677/682/687 | NH3L | gBat | 1500 | 315 | 100 | 50
ETI | 004110 678/683/688 | NH3L | gBat | 1500 | 350 | 100 | 50
ETI | 004110 679/684/689 | NH3L | gBat | 1500 | 400 | 100 | 50
ETI | 004110 680/685/690 | NH3L | gBat | 1500 | 450 | 100 | 50
ETI | 004110 681/686/691 | NH3L | gBat | 1500 | 500 | 100 | 50
ETI | 004110 779/780/781 | NH3L | gBat | 1500 | 630 | 100 | 50
Mersen | 15NH2XLGBAT250 | NH2XL | gBat | 1500 | 250 | 50 | 50
Mersen | 15NH3LGBAT250 | NH3L | gBat | 1500 | 250 | 150 | 50
Mersen | 15NH3LGBAT315 | NH3L | gBat | 1500 | 315 | 150 | 50
Mersen | 15NH3LGBAT350 | NH3L | gBat | 1500 | 350 | 150 | 50
Mersen | 15NH3LGBAT400 | NH3L | gBat | 1500 | 400 | 150 | 50
Eaton-Bussmann | BSF-250G-3XL15 | NH3XL | gBat | 1500 | 250 | 100 | 50
Eaton-Bussmann | BSF-315G-3XL15 | NH3XL | gBat | 1500 | 315 | 100 | 50
Eaton-Bussmann | BSF-355G-3XL15 | NH3XL | gBat | 1500 | 355 | 100 | 50
Eaton-Bussmann | BSF-400G-3XL15 | NH3XL | gBat | 1500 | 400 | 100 | 50
Eaton-Bussmann | BSF-450G-3XL15 | NH3XL | gBat | 1500 | 450 | 100 | 50
Eaton-Bussmann | BSF-500G-3XL15 | NH3XL | gBat | 1500 | 500 | 100 | 50
Eaton-Bussmann | BSF-250G-NH210 | NH2 | gBat | 1000 | 250 | 100 | 50
Eaton-Bussmann | BSF-315G-NH310 | NH3 | gBat | 1000 | 315 | 100 | 50
Eaton-Bussmann | BSF-355G-NH310 | NH3 | gBat | 1000 | 355 | 100 | 50
Eaton-Bussmann | BSF-400G-NH310 | NH3 | gBat | 1000 | 400 | 100 | 50
Mersen | 10NH2GBAT250 | NH2 | gBat | 1000 | 250 | 50 | 50
ETI | 004110 567/598/613 | NH2XL | gPV | 1500 | 250 | 30 | 30
ETI | 004110 630/635/640 | NH3L | gPV | 1500 | 315 | 50 | 50
ETI | 004110 631/636/641 | NH3L | gPV | 1500 | 350 | 50 | 50
ETI | 004110 632/637/642 | NH3L | gPV | 1500 | 400 | 50 | 50
ETI | 004110 633/638/643 | NH3L | gPV | 1500 | 450 | 50 | 50
ETI | 004110 634/639/644 | NH3L | gPV | 1500 | 500 | 50 | 50
ETI | 2 in parallel 004110 634 | NH3L | gPV | 1500 | 500 | 50 | 50
ETI | 004110 647/648/649 | NH3L | gPV | 1500 | 630 | 50 | 50
ETI | 2 in parallel 004110 647 | NH3L | gPV | 1500 | 630 | 50 | 50
ETI | 004110 714/719/724 | NH3L | gPV | 1500 | 315 | 50 | 50
ETI | 004110 715/720/725 | NH3L | gPV | 1500 | 350 | 50 | 50
ETI | 004110 716/721/726 | NH3L | gPV | 1500 | 400 | 50 | 50
ETI | 004110 717/722/727 | NH3L | gPV | 1500 | 450 | 50 | 50
ETI | 004110 718/723/728 | NH3L | gPV | 1500 | 500 | 50 | 50
SIBA | 20 042 29 250 | NH2XL | gPV | 1500 | 250 | 50 | 50
SIBA | 20 042 29 315 | NH2XL | gPV | 1500 | 315 | 50 | 50
SIBA | 20 243 28 250 | NH3L | gPV | 1500 | 250 | 100 | 50
SIBA | 20 243 28 315 | NH3L | gPV | 1500 | 315 | 100 | 50
SIBA | 20 243 28 350 | NH3L | gPV | 1500 | 350 | 100 | 50
SIBA | 20 243 28 400 | NH3L | gPV | 1500 | 400 | 100 | 50
SIBA | 20 243 28 450 | NH3L | gPV | 1500 | 450 | 100 | 50
SIBA | 20 243 28 500 | NH3L | gPV | 1500 | 500 | 100 | 50
Mersen | HP15NH2XLGPV250 | NHXL2 | gPV | 1500 | 250 | 50 | 50
Mersen | HP15NH3LGPV250 | NH3L | gPV | 1500 | 250 | 50 | 50
Mersen | HP15NH3LGPV315 | NH3L | gPV | 1500 | 315 | 50 | 50
Mersen | HP15NH3LGPV350 | NH3L | gPV | 1500 | 350 | 50 | 50
Mersen | HP15NH3LGPV400 | NH3L | gPV | 1500 | 400 | 150 | 50
Littelfuse | SPNH250.X2XL | NH2XL | gPV | 1500 | 250 | 30 | 30
Littelfuse | SPNH315.X3L | NH3L | gPV | 1500 | 315 | 50 | 50
Littelfuse | SPNH350.X3L | NH3L | gPV | 1500 | 350 | 50 | 50
Littelfuse | SPNH400.X3L | NH3L | gPV | 1500 | 400 | 50 | 50
Eaton-Bussmann | PV-250A-2XL-15 | NH2XL | gPV | 1500 | 250 | 30 | 30
Eaton-Bussmann | PV-250A-3L-15 | NH3L | gPV | 1500 | 250 | 100 | 50
Eaton-Bussmann | PV-315A-3L-15 | NH3L | gPV | 1500 | 315 | 100 | 50
Eaton-Bussmann | PV-350A-3L-15 | NH3L | gPV | 1500 | 350 | 100 | 50
Eaton-Bussmann | PV-355A-3L-15 | NH3L | gPV | 1500 | 355 | 100 | 50
Eaton-Bussmann | PV-400A-3L-15 | NH3L | gPV | 1500 | 400 | 100 | 50
Eaton-Bussmann | PV-450A-3L-15 | NH3L | gPV | 1500 | 450 | 100 | 50
Eaton-Bussmann | PV-500A-3L-15 | NH3L | gPV | 1500 | 500 | 100 | 50
ETI | 004110 344 | NH2 | gPV | 1000 | 250 | 30 | 30
ETI | 004110 458 | NH3 | gPV | 1000 | 250 | 30 | 30
ETI | 004110 460 | NH3 | gPV | 1000 | 315 | 30 | 30
ETI | 004110 459 | NH3 | gPV | 1000 | 350 | 30 | 30
ETI | 004110 457 | NH3 | gPV | 1000 | 400 | 30 | 30
ETI | 004110 646 | NH1XL | gPV | 1000 | 250 | 30 | 30
ETI | 004110 413 | NH2XL | gPV | 1100 | 250 | 10 | 10
ETI | 004110 418 | NH2XL | gPV | 1100 | 315 | 10 | 10
ETI | 004110 483 | NH2XL | gPV | 1100 | 350 | 10 | 10
ETI | 004110 453 | NH3L | gPV | 1100 | 250 | 10 | 10
ETI | 004110 454 | NH3L | gPV | 1100 | 300 | 10 | 10
ETI | 004110 425 | NH3L | gPV | 1100 | 315 | 10 | 10
ETI | 004110 440 | NH3L | gPV | 1100 | 350 | 10 | 10
ETI | 004110 441 | NH3L | gPV | 1100 | 400 | 10 | 10
ETI | 004110 448 | NH3L | gPV | 1100 | 450 | 10 | 10
ETI | 004110 446 | NH3L | gPV | 1100 | 500 | 10 | 10
ETI | 004110 449 | NH3L | gPV | 1100 | 630 | 10 | 10
ETI | 004110 398 | NH2XL | gPV | 1100 | 250 | 10 | 10
ETI | 004110 399 | NH3L | gPV | 1100 | 315 | 10 | 10
ETI | 004110 400 | NH3L | gPV | 1100 | 350 | 10 | 10
ETI | 004110 401 | NH3L | gPV | 1100 | 400 | 10 | 10
ETI | 004110 485 | NH3L | gPV | 1100 | 450 | 10 | 10
ETI | 004110 629 | NH3L | gPV | 1100 | 500 | 10 | 10
Eaton-Bussmann | PV-250ANH2 | NH2 | gPV | 1000 | 250 | 50 | 50
Eaton-Bussmann | PV-300ANH3 | NH3 | gPV | 1000 | 300 | 50 | 50
Eaton-Bussmann | PV-315ANH3 | NH3 | gPV | 1000 | 315 | 50 | 50
Eaton-Bussmann | PV-350ANH3 | NH3 | gPV | 1000 | 350 | 50 | 50
Eaton-Bussmann | PV-355ANH3 | NH3 | gPV | 1000 | 355 | 50 | 50
Eaton-Bussmann | PV-400ANH3 | NH3 | gPV | 1000 | 400 | 50 | 50
Eaton-Bussmann | PV-250A-2XL | NH2XL | gPV | 1000 | 250 | 33 | 30
Eaton-Bussmann | PV-315A-2XL | NH2XL | gPV | 1000 | 315 | 33 | 30
Eaton-Bussmann | PV-355A-2XL | NH2XL | gPV | 1000 | 355 | 33 | 30
Eaton-Bussmann | PV-350A-3L | NH3L | gPV | 1000 | 350 | 50 | 50
Eaton-Bussmann | PV-400A-3L | NH3L | gPV | 1000 | 400 | 50 | 50
Eaton-Bussmann | PV-500A-3L | NH3L | gPV | 1000 | 500 | 50 | 50
Eaton-Bussmann | PV-600A-3L | NH3L | gPV | 1000 | 600 | 50 | 50
Mersen | HP10NH2GPV250 | NH2 | gPV | 1000 | 250 | 50 | 50
Mersen | HP12NH2XLGPV250 | NH2XL | gPV | 1250 | 250 | 50 | 50
Mersen | HP12NH3LGPV250 | NH3L | gPV | 1250 | 250 | 50 | 50
Mersen | HP12NH3LGPV315 | NH3L | gPV | 1250 | 315 | 50 | 50
Mersen | HP12NH3LGPV350 | NH3L | gPV | 1250 | 350 | 50 | 50
Mersen | HP12NH3LGPV400 | NH3L | gPV | 1250 | 400 | 50 | 50
SIBA | 20 243 36 250 | NH3L | gR | 1500 | 250 | 170 | 50
SIBA | 20 243 36 315 | NH3L | gR | 1500 | 315 | 170 | 50
SIBA | 20 243 36 350 | NH3L | gR | 1500 | 350 | 170 | 50
SIBA | 20 243 36 400 | NH3L | gR | 1500 | 400 | 170 | 50
SIBA | 20 243 36 450 | NH3L | gR | 1500 | 450 | 170 | 50
SIBA | 20 243 36 500 | NH3L | gR | 1500 | 500 | 170 | 50

## Fuse coord. OTDC M 800-1000A
Fuse coordination for OTDC M Series (OTDC800…1000_F_22-ESS) OTDC800…1000F22-ESS for 1000Vdc, IEC only OTDC800…1000UF22-ESS for 1000Vdc, IEC and UL98B OTDC800…1000FV22-ESS for 1500Vdc, IEC only OTDC800…1000UFV22-ESS for 1500Vdc, IEC and UL98B More detailed info, please contact us Global Sales Support, switch.technicalservice@fi.abb.com
FUSE DATA
Fuse Manuf. | Order code | Size | Type | Rated Voltage | Rated Current | Rated Breaking Capacity | Self certified Conditional Short Circuit Withstand current
Littelfuse | PSX3XLDB0800X | NH3XL | aBat | 1500 | 800 | 250 | 50
Littelfuse | PSX3XLDB0900X | NH3XL | aBat | 1500 | 900 | 250 | 50
Littelfuse | PSX3XLDB1000X | NH3XL | aBat | 1500 | 1000 | 250 | 50
SIBA | 90 213 38 800 | SQB-DC2-2 | aR | 1500 | 800 | 170 | 50
SIBA | 90 447 38 800 | SQB-DC153 | aR | 1500 | 800 | 170 | 50
SIBA | 90 447 38 900 | SQB-DC153 | aR | 1500 | 900 | 170 | 50
SIBA | 90 447 38 1000 | SQB-DC153 | aR | 1500 | 1000 | 170 | 50
SIBA | 90 392 25 800 | SQB-DC154 | aR | 1500 | 800 | 100 | 50
SIBA | 90 392 25 900 | SQB-DC154 | aR | 1500 | 900 | 100 | 50
SIBA | 90 392 25 1000 | SQB-DC154 | aR | 1500 | 1000 | 100 | 50
Mersen | ABAT15C800AIA | - | aR/aBat | 1500 | 800 | 250 | 50
Mersen | ABAT15C900AIA | - | aR/aBat | 1500 | 900 | 250 | 50
Mersen | ABAT15C1000AIB | - | aR/aBat | 1500 | 1000 | 250 | 50