## Revision History
Version | Date | Description
A (01.00, 01.01, 01.02) | 2018-10-15 | First version
B (01.03) | 2019-01-02 | Timing flag 'Manual to Auto Delay' added to register 48:14
Sensor Module Type added to register 547
Global status flag 'Control Alarm' is moved from 40:10 to 40:2
Global status flag 'Warning/Alarm/Info' added to register 40:10
Diagnostics counter 'Manual Operations' added to register 266
Registers 257…260 changed to relative pole temperature values
Single phase settings added to parameter 'Rated Voltage' in register 646
HMI home page and meter parameters added to registers 723, 770…772
Parameter 'Transfer to Dead Source' added to register 780:0
Digital input function 'Manual-Auto Mode' added in register 53:8 and input function table
Energy measures splitted for both sources in registers 300…310
Energy totals added in registers 316…320
Generator exerciser event duration parameters divided to minutes and seconds in registers 755...758, 781, 782, 791, 792
C (01.04) | 2019-05-14 | Function 'Elevetor Pre-signal' added to digital output function list in register 704
Info flag 'Elevator Pre-transfer Signal' added to register bit 54:9
Status flag 'Elevator Pre-transfer S1 to S2 Delay' added to register bit 48:3
Status flag 'Elevator Post-transfer S1 to S2 Delay' added to register bit 48:7
Status flag 'Elevator Pre-transfer S2 to S1 Delay' added to register bit 48:8
Status flag 'Elevator Post-transfer S2 to S1 Delay' added to register bit 48:15
Parameter 'Elevator Pre-transfer S1 to S2 Delay' added to register 790
Parameter 'Elevator Post-transfer S1 to S2 Delay' added to register 800
Parameter 'Elevator Pre-transfer S2 to S1 Delay' added to register 801
Parameter 'Elevator Post-transfer S2 to S1 Delay' added to register 802
Parameter 'Pre-transfer S1 to S2 Delay' range changed to 0…300 s in register 650
Parameter 'Post-transfer S1 to S2 Delay' range changed to 0…300 s in register 651
Parameter 'Pre-transfer S2 to S1 Delay' range changed to 0…300 s in register 705
Parameter 'Post-transfer S2 to S1 Delay' range changed to 0…300 s in register 706
Parameter 'Override S1 Failure Delay' range changed to 0…10 min in register 642
Resolution of diagnostics data 'Transfer Time' changed to milliseconds in register 23
D (01.05) | 2020-03-05 | Status flag 'Manual retransfer' added to register bit 40:1
Status flag 'New HMI Serial Number' added to register bit 42:15
Status flag 'S1 Neutral disconnected' added to register bit 57:3
Status flag 'S2 Neutral disconnected' added to register bit 57:4
Source 2 voltages added from register 224 to 232
HMI SW CRC for LCD and TOUCH added from register 540 to 543
Parameter 'Center OFF delay' added to register 780:1
Parameter 'Pre Signal delay' added to register 780:2
Parameter 'Branded device' added to register 780:3
Block 'HMI informations' added to address 860
E (01.05) | 2020-10-05 | Ekip COM modules not provided have been deleted Creation of dedicated sheets for Modbus - DeviceNet - Profibus - Profinet - Ethernet IP protocols
01.06 | 2021-05-20 | Status flag 'Manual Retransfer' removed from register bit 40:1
Status flag 'Manual Retransfer Mode' added to register bit 40:1
Added register 'Status Global 2' @41
Status flag 'Fw Update Ok' added to register bit 41:0
Status flag 'Fw Update Failed' added to register bit 41:1
Status flag 'FW Update Com Hub' added to register bit 41:2
Status flag 'FW Update Com OADR' added to register bit 41:3
Status flag 'On Primary' added to register bit 41:4
Status flag 'On Secondary' added to register bit 41:5
Status parameter 'Transition Type' added to register bit 41:6-7
Status parameter 'Priority' added to register bit 41:8-9
Status flag 'Elevator Pre-transfer S1 to S2 Delay' removed from register bit 48:3
Status flag 'Elevator Post-transfer S1 to S2 Delay' removed from register bit 48:7
Status flag 'Elevator Pre-transfer S2 to S1 Delay' removed from register bit 48:8
Status flag 'Elevator Post-transfer S2 to S1 Delay' removed from register bit 48:15
Status flag 'Pre-transfer S1 to S2 Delay' removed from register 48:9
Status flag 'Post-transfer S1 to S2 Delay' removed from register 48:10
Status flag 'Pre-transfer S2 to S1 Delay' removed from register 48:11
Status flag 'Post-transfer S2 to S1 Delay' removed from register 48:12
Status flag 'Elevator Pre-transfer Delay' added to register bit 48:7
Status flag 'Elevator Post-transfer Delay' added to register bit 48:8
Status flag 'Pre-transfer Delay' added to register bit 48:9
Status flag 'Post-transfer Delay' added to register bit 48:10
Status flag 'Pre-transfer 2 Delay' added to register bit 50:1
Status flag 'Post-transfer 2 Delay' added to register bit 50:2
Status flag 'Pre-transfer 3 Delay' added to register bit 50:3
Status flag 'Post-transfer 3 Delay' added to register bit 50:4
Status flag 'Pre-transfer 4 Delay' added to register bit 50:5
Status flag 'Post-transfer 4 Delay' added to register bit 50:6
Status flag 'Elevator Pre-transfer 2 Delay' added to register bit 50:7
Status flag 'Elevator Post-transfer 2 Delay' added to register bit 50:8
Status flag 'Elevator Pre-transfer 3 Delay' added to register bit 50:9
Status flag 'Elevator Post-transfer 3 Delay' added to register bit 50:10
Status flag 'Elevator Pre-transfer 4 Delay' added to register bit 50:11
Status flag 'Elevator Post-transfer 4 Delay' added to register bit 50:12
Warning flag 'Manual Retransfer Required' added to register bit 57:7
Added register 'Generator Exerciser Delay Ongoing value Low' @264
Added register 'Generator Exerciser Delay Ongoing value High' @265
Added register 'Status Warnings Alarms 6' @58
Status flag 'Manual Retransfer DIP-Switch Status' added to register bit 58:0
Added register 'HMI PIN User Low' @773
Added register 'HMI PIN User High' @774
Status flag 'New HMI Serial Number' removed from register bit 42:15
Status flag 'Core Fw Update' added to register bit 42:2
02.00 | 2022-04-10 | Synchronization Window parameter moved from 252 to 720
Temperature PT100/1000 sensor value moved from 263 to 256
Contact wear end of life date added in 262 and 263
Password required 1 added in 41:10
Password required 2 added in 41:11
Exerciser programmed added in 41:12
Generator start failure added in 44:13
Unbalance drop-out added to 930
Unbalance pick-up added to 931
Unbalance measuring enabled added to 780:12
Metering visible added in 780:13
MAN Retransfer Override added in 780:14
ATS connected added to 58:1
ATS test added to 58:2
Bypass connected added to 58:3
Bypass test added to 58:4
Positions of ATS/Bypass added to digital input functions table
ATS in position OI and OII added to digital output functions table
Digital output function "Load Shed" renamed to "Load Shed Output Signal" in 56:15
Digital input function "Inhibit Transfer w/ Override" added in 58:5
Digital input function "Load Shed Input Signal" added in 58:6
Digital output function "Transfer Alarm" added in 58:7
Ekip 10K present flag added to 47:1
Ekip 10K input status added to 60
Ekip 10K output status added to 63
Ekip 10K configurations added to 1588…1627
Ekip Link present flag removed from 46:8
Invalid HMI type added to the value range of 523 and 860
Pre-transfer signal 2…4 info flags added to 58:10,11,12
Elevator pre-transfer signal 2…4 info flags added to 58:13,14,15
Silence alarm command added
Switch position error (ATS/Bypass) added to 58:8
Manual momentary mode flag added to 40:12
Event table updated
HMI temperature added to register 252
TC: Sources unable to synchronize flag added to 58:9
Racking Enabled replaced unused flag in 58:0
TB: ATS switch feeding the load flag added to 45:1
Changed measured harmonics phase(register 401) value orders to align with controller software
Removed Stay On S1 with S2 Delay from register 662
Source 1 voltage unbalance added to register 549
Source 2 voltage unbalance added to register 550
Added 2 new commands for TC: WAIT & DELAY mode
Removed 780:11 Current sensing enabled flag(TC) because this functionality is transferred to 780:13
Fixed CAN addresses of modbus reg. 900(2050 to 2054) and register 930(204A to 2057)

## Map
Modbus Address (DEC) | Registers & Parameters Name | Nr of Reg | Bitfield | T1 only | TC only | Events | Range | Description | Units | Multiplier | Data Type | Read Write | Modbus |  |  |  |  | Mod Reserved |  |  | CAN Index (HEX) | CAN Index (HEX) | Fieldbus base number | DeviceNet™ and EtherNet/IP ™ Class ID (Attribute ID = 3) | Profibus slot | Profinet subslot (API=0, slot=3) | Cyclic data offset [bytes] | Data offset EtherNet/IP™ FW >= 02.12 | PDO [Address] | Access | Stored Volatile | N° of object | Type | Fieldbus cyclic data | Fieldbus update strategy | Process data category
[13 empty] | 03 | 04 | 06 | 16 | 70 | 72 - 03 | 72 - 06 | 72 - 16
0 | Commands | 2 | [9 empty] | RW | X | X | X | X |  |  |  |  | 2000 |  | 1 | 0x0064 | 0x01 | 0x0001 | [5 empty] | 1 | 32
0 | Command (type+parameter) | 2 |  |  |  |  | 0 ÷ 65535 | Command | - | - | E32 |  | X | X | X | X |  |  |  |  | 0 | [8 empty] | RW | V
3 | Time | 3 | [9 empty] | RW | X | X | X | X |  |  |  |  | 2001 |  | 2 | 0x0065 | 0x02 | 0x0002 | [5 empty] | 3 | 16
3 | Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | time = 0 --> 00:00:00.000 31 dec 1999 T min: 00:00:00.000 01 jan 2012 | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW
4 | Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW
5 | Milliseconds | 1 |  |  |  |  | 0 ÷ 999 |  | ms | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW
20 | Switch Statistical Data | 6 | [9 empty] | R |  | X | [6 empty] | 2002 |  | 3 | 0x0066 | 0x03 | 0x0003 | [5 empty] | 6 | 16
20 | Contact Wear | 1 |  |  |  |  | 0 … 65000, 65000 <=> 100% | Contact wear in percent | % | 1/650 | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
21 | Total Opearations | 1 |  |  |  |  | 0 … 65535 | Includes all switch position transitions | - | 1 | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
22 | Number of Load Transfers | 1 |  |  |  |  | 0 … 65535 | Number of times the transfer switch has transferred the load | - | 1 | U16 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | S
23 | Transfer Time | 1 |  |  |  |  | 0 … 65535 | Total time it took to transfer the load between sources | ms | 1 | U16 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | S
24 | Source Fail Transfers | 1 |  |  |  |  | 0 … 65535 | Number of times load is transferred due to source unacceptable | - | 1 | U16 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | S
25 | Days Energized | 1 |  |  |  |  | 0 … 65535 | Total number of days the ATS has been energized | d | 1 | U16 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | S
30 | Programming Fail Error Code | 1 | [9 empty] | R |  | X | [6 empty] | 2003 |  | 4 | 0x0067 | 0x04 | 0x0004 | [5 empty] | 1 | 16
30 | Programming Fail error code | 1 |  |  |  |  | 0 ÷ 65535 | Fail code | - | - | E16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
40 | Status | 20 | [9 empty] | R |  | X | [6 empty] | 2004 |  | 5 | 0x0068 | 0x05 | 0x0005 | [5 empty] | 20 | 16
40 | Status Global 1 | 1 | B |  |  |  | Bitfield | Global status information (summary) | - | - | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 | 0 | 0 | TPDO1[1] | R | V |  |  | yes | PDO sniffed | 100 ms / PDO
| Source 1 Connected |  | 0 |  |  | ▲▼ | 1 = Switch in position I | Switch position I status |  |  | BOOL | [18 empty] | R | V
| Manual Retransfer Mode |  | 1 |  |  |  | 1 = Manual retransfer mode on | Manual retransfer mode on |  |  | BOOL | [18 empty] | R | V
| Control Alarm |  | 2 |  |  |  | 1 = Alarm active | Switch control alarm active |  |  | BOOL | [18 empty] | R | V
| Source 1 Status |  | 3 |  |  | ▲▼ | 1 = Source 1 OK | Voltage source 1 status |  |  | BOOL | [18 empty] | R | V
| Auto Config Active |  | 4 |  |  | ▲▼ | 1 = Active | Auto configuration sequence activated |  |  | BOOL | [18 empty] | R | V
| Auto Config Ready |  | 5 |  |  | ▲ | 1 = Configuration ready | Auto configuration sequence completed |  |  | BOOL | [18 empty] | R | V
| Automatic Mode |  | 6 |  |  | ▲▼ | 1 = Automatic | Device in automatic operating mode |  |  | BOOL | [18 empty] | R | V
| Source 2 Connected |  | 7 |  |  | ▲▼ | 1 = Switch in position II | Switch position II status |  |  | BOOL | [18 empty] | R | V
| Local / Remote |  | 8 |  |  | ▲▼ | 1 = Remote |  |  |  | BOOL | [18 empty] | R | V
| Source 2 Status |  | 9 |  |  | ▲▼ | 1 = Source 2 OK | Voltage source 2 status |  |  | BOOL | [18 empty] | R | V
| Warning/Alarm/Info |  | 10 |  |  |  | 1 = Active | Any warning, alarm or info is activated |  |  | BOOL | [18 empty] | R | V
| Running Delay |  | 11 |  |  |  | 1 = Delay counter on | Transfer sequence delay running |  |  | BOOL | [18 empty] | R | V
| Manual Momentary Mode |  | 12 |  |  |  | 1 = Manual momentary mode active | Device in manual momentary mode |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| Off Position |  | 14 |  |  | ▲▼ | 1 = Swtch in position O | Switch position O status |  |  | BOOL | [18 empty] | R | V
| Other Alarm |  | 15 |  | X |  | 1 = Alarm active | Other alarm(s) active |  |  | BOOL | [18 empty] | R | V
41 | Status Global 2 | 1 | B |  |  |  | Bitfield | Global status information (summary) | - | - | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 | 2 | 2 |  | R | V |  |  | yes | always | 100 ms / HF
| Fw Update Ok |  | 0 |  |  |  | 1 = Fw update ok | FW update status |  |  | BOOL | [18 empty] | R | V
| Fw Update Failed |  | 1 |  |  |  | 1 = Fw update failed | FW update status |  |  | BOOL | [18 empty] | R | V
| FW Update Com Hub |  | 2 |  |  |  | 1 = Fw update Com Hub ok | FW update Com Hub status |  |  | BOOL | [18 empty] | R | V
| FW Update Com OADR |  | 3 |  |  |  | 1 = Fw update Com OADR ok | FW update Com OADR status |  |  | BOOL | [18 empty] | R | V
| On Primary |  | 4 |  |  |  | 1 = On primary source | Switch on primary source |  |  | BOOL | [18 empty] | R | V
| On Secondary |  | 5 |  |  |  | 1 = On secondary source | Switch on secondary source |  |  | BOOL | [18 empty] | R | V
| Transition Type |  | 6 |  |  |  | 0 ÷ 3 | 0 = No transition, 1 = Transition from primary to secondary, 2 = Transition from secondary to primary, 3 = NOT USED |  |  | U16 | [18 empty] | R | V
7
| Priority |  | 8 |  |  |  | 0 ÷ 3 | 0 = No priority, 1 = priority on S1, 2 = priority on S2, 3 = NOT USED |  |  | U16 | [18 empty] | R | V
9
| Password Required 1 |  | 10 |  |  |  | 1 = Password required for I command | Password authentication for a command |  |  | BOOL | [18 empty] | R | V
| Password Required 2 |  | 11 |  |  |  | 1 = Password required for II command | Password authentication for a command |  |  | BOOL | [18 empty] | R | V
| Exerciser Programmed |  | 12 |  |  |  | 1 = Exerciser event pending | Ecerciser event will be activated |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
42 | Status Glitch 1 | 1 | B |  |  |  | Bitfield | Information reset after read | - | - | U16 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 | 4 | 4 | TPDO2[1] | R | V |  |  | yes | PDO sniffed | 100 ms / PDO
| Parameter(s) Changed |  | 0 |  |  | ▲ | 1 = Parameter(s) changed | At least one parameter is changed because of a programming session |  |  | BOOL | [18 empty] | R | V
| Alarm Reset |  | 1 |  |  | ▲ | 1 = alarm reset | Alarm reset |  |  | BOOL | [18 empty] | R | V
| Core Fw Update |  | 2 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 4 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 5 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 6 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 7 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 8 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 9 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| Energy Reset |  | 12 |  |  | ▲ | 1 = Energy reset | Command received |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| New Event |  | 14 |  |  |  | 1 = New Event | A new event happens |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL
44 | Status Flags 1 | 1 | B |  |  |  | Bitfield | Device status | - | - | U16 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 | 6 | 6 |  | R | V |  |  | yes | always | 100 ms / HF
| Programming Source |  | 0 |  |  |  | 0 ÷ 3 | 0=No progr session opened, 1=Local Bus, 2=Test Bus, 3=HMI |  |  | BOOL | [18 empty] | R | V
|  |  | 1 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 4 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 5 | [7 empty] | BOOL | [18 empty] | R | V
| Supply from Vaux |  | 6 |  |  | ▲▼ | 1 = Supply from auxiliary voltage on | Auxiliary voltage on |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 7 | [7 empty] | BOOL | [18 empty] | R | V
| Supply from Voltage Module |  | 8 |  |  | ▲▼ | 1 = Supply from power module on | Supply from power module |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 9 | [7 empty] | BOOL | [18 empty] | R | V
| Programming Status |  | 10 |  |  |  | 0 ÷ 3 | 00 = No session, 01 = Program OK, 10 = Program Fail, 11 = Session running |  |  | BOOL | [18 empty] | R | V
|  |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| Generator Start Failure |  | 13 |  |  |  | 0 = Generator has started normally; 1 = Generator has not started | Generator start status |  |  | BOOL | [18 empty] | R | V
| Generator Usage |  | 14 |  |  | ▲▼ | 0 = No generator; 1 = Generator in use | Generator in use/not in use |  |  | BOOL | [18 empty] | R | V
| Generator Status |  | 15 |  |  | ▲▼ | 0 = Generator stopped; 1 = Generator started | Generator control status |  |  | BOOL | [18 empty] | R | V
45 | Status Flags 2 | 1 | B |  |  |  | Bitfield | Device status | - | - | U16 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 | 8 | 8 |  | R | V |  |  | yes | always | 100 ms / HF
| Synchronization Condition |  | 0 |  |  |  | 1 = Sources synchronized | Phase difference between voltage sources is below synchronization level |  |  | BOOL | [18 empty] | R | V
| ATS switch feeding the load (TB only) |  | 1 |  |  |  | 0 = Position O, 1 = Position I or II | Only used for Bypass switches |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 4 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 5 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 6 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 7 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 8 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 9 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
46 | Status Accessories 1 | 1 | B |  |  |  | Bitfield | Connected accessories | - | - | U16 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 | 10 | 10 |  | R | V |  |  | yes | Every 1s | 100 ms / HF
| Ekip Signalling 2K-1 |  | 0 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-2 |  | 1 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-3 |  | 2 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com EtherNet/IP™ |  | 3 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com Modbus RS-485 |  | 4 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com Profibus |  | 5 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com Modbus TCP |  | 6 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com DeviceNet ™ |  | 7 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 8 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 9 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Com Profinet |  | 12 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
47 | Status Accessories 2 | 1 | B |  |  |  | Bitfield | Accessories connected | - | - | U16 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 | 12 | 12 |  | R | V |  |  | yes | Every 1s | 100 ms / HF
| Ekip Signalling 10K |  | 0 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 1 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Com Modbus RS-485 Redundant |  | 3 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com Profibus Redundant |  | 4 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com Modbus TCP Redundant |  | 5 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com DeviceNet ™ Redundant |  | 6 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com Profinet Redundant |  | 7 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Ekip Com EtherNet/IP™ Redundant |  | 8 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 9 | [7 empty] | BOOL | [18 empty] | R | V
| Dip HMI |  | 10 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| LCD HMI |  | 11 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| Touch HMI |  | 12 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Com Hub |  | 14 |  |  |  | 1 = Present |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
48 | Status Timing 1 | 1 | B |  |  |  | Bitfield | Timings that bring to opening command | - | - | U16 |  |  | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 | 14 | 14 |  | R | V |  |  | yes | any timing | 100 ms / HF
| Override S1 Failure Delay |  | 0 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Transfer from S1 to S2 Delay |  | 1 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Override S2 Failure Delay |  | 2 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | R | V
| Transfer from S2 to S1 Delay |  | 4 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Generator Stop Delay |  | 5 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Center-Off Delay |  | 6 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Pre-transfer Delay |  | 7 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Post-transfer Delay |  | 8 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Pre-transfer Delay |  | 9 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Post-transfer Delay |  | 10 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| Load Shed Delay |  | 13 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Manual to Auto Delay |  | 14 |  |  |  | 1 = Slider switch has been in AUTO position less than three seconds |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
49 | Status Timing 2 | 1 |  |  |  |  | 0 … 65535 | Timer value of an active delay counter | s | 1 | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 | 16 | 16 |  | R | V |  |  | yes | any timing | 100 ms / HF
50 | Status Timing 3 | 1 | B |  |  |  | Bitfield | Timings | - | - | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 | 18 | 18 |  | R | V |  |  | yes | any timing | 100 ms / HF
| Generator Exerciser Delay |  | 0 |  |  |  | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Pre-transfer 2 Delay |  | 1 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Post-transfer 2 Delay |  | 2 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Pre-transfer 3 Delay |  | 3 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Post-transfer 3 Delay |  | 4 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Pre-transfer 4 Delay |  | 5 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Post-transfer 4 Delay |  | 6 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Pre-transfer 2 Delay |  | 7 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Post-transfer 2 Delay |  | 8 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Pre-transfer 3 Delay |  | 9 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Post-transfer 3 Delay |  | 10 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Pre-transfer 4 Delay |  | 11 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| Elevator Post-transfer 4 Delay |  | 12 |  |  | ▲▼ | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 |  |  |  | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 14 |  |  |  | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 15 |  |  |  | 1 = Timing |  |  |  | BOOL | [18 empty] | R | V
53 | Status Warnings Alarms 1 | 1 | B |  |  |  | Bitfield | Info / warning / alarm | - | - | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 | 4 | 4 |  | R | V |  |  | yes | Warning/Alarm/Info | 100 ms / HF
| Test on Load |  | 0 |  |  | ▲▼ | Info | Test on load activated/inactivated |  |  | BOOL | [18 empty] | R | V
| Test off Load |  | 1 |  |  | ▲▼ | Info | Test off load activated/inactivated |  |  | BOOL | [18 empty] | R | V
| Fire Fighting |  | 2 |  |  | ▲▼ | Alarm | Fire fighting input activated |  |  | BOOL | [18 empty] | R | V
| Voltage Sources Not in Sync |  | 3 |  |  |  | Warning | Source 1 and source 2 phase difference is too long |  |  | BOOL | [18 empty] | R | V
| Locked |  | 4 |  |  | ▲▼ | Alarm | Lock input activated |  |  | BOOL | [18 empty] | R | V
| Handle |  | 5 |  |  | ▲▼ | Alarm | Handle input activated |  |  | BOOL | [18 empty] | R | V
| No Communication on Local Bus |  | 6 |  |  |  | Alarm | Local bus communication error |  |  | BOOL | [18 empty] | R | V
| Incompatible HMI alarm |  | 7 |  |  | ▲▼ | Alarm | HMI incompatible |  |  | BOOL | [18 empty] | R | V
| Manual-Auto Mode |  | 8 |  |  | ▲ | Info | Toggle automatic control mode on/off |  |  | BOOL | [18 empty] | R | V
| Phases Crossed |  | 9 |  |  | ▲▼ | Alarm | Source 1 and source 2 phase rotations are different |  |  | BOOL | [18 empty] | R | V
| S1 Undervoltage |  | 10 |  |  | ▲▼ | Alarm | Source 1 voltage is under threshold level |  |  | BOOL | [18 empty] | R | V
| S1 Overvoltage |  | 11 |  |  | ▲▼ | Alarm | Source 1 voltage is over threshold level |  |  | BOOL | [18 empty] | R | V
| S1 Phase Missing |  | 12 |  |  | ▲▼ | Alarm | At least one phase is missing from source 1 |  |  | BOOL | [18 empty] | R | V
| S1 Unbalance |  | 13 |  |  | ▲▼ | Alarm | Source 1 U0 is over 30% of rated voltage |  |  | BOOL | [18 empty] | R | V
| S1 Phase Rotation |  | 14 |  |  | ▲▼ | Alarm | S1 phase rotation is wrong |  |  | BOOL | [18 empty] | R | V
| S1 Invalid Frequency |  | 15 |  |  | ▲▼ | Alarm | S1 frequency is out of threshold range |  |  | BOOL | [18 empty] | R | V
54 | Status Warnings Alarms 2 | 1 | B |  |  |  | Bitfield | Info / warning / alarm | - | - | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 | 6 | 6 |  | R | V |  |  | yes | Warning/Alarm/Info | 100 ms / HF
| Frequency Difference |  | 0 |  |  | ▲▼ | Alarm | Frequency difference of sources exceeds the limit while in-phase monitor is active |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Undervoltage |  | 1 |  |  | ▲▼ | Alarm | Source 2 voltage is under threshold level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Overvoltage |  | 2 |  |  | ▲▼ | Alarm | Source 2 voltage is over threshold level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Phase Missing |  | 3 |  |  | ▲▼ | Alarm | At least one phase is missing from source 2 |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Unbalance |  | 4 |  |  | ▲▼ | Alarm | Source 2 U0 is over 30% of rated voltage |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Phase Rotation |  | 5 |  |  | ▲▼ | Alarm | Source 2 phase rotation is wrong |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Invalid Frequency |  | 6 |  |  | ▲▼ | Alarm | Source 2 frequency is out of threshold range |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Contact Wear PreAlarm |  | 7 |  |  | ▲▼ | Alarm | Contact wear is over pre-alarm level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Contact Wear Alarm |  | 8 |  |  | ▲▼ | Alarm | Contact wear is over alarm level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Elevator Pre-transfer Signal |  | 9 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Open I Failure |  | 10 |  |  | ▲▼ | Alarm | Transfer from S1 failed |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Close I Failure |  | 11 |  |  | ▲▼ | Alarm | Transfer to S1 failed |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Open II Failure |  | 12 |  |  | ▲▼ | Alarm | Transfer from S2 failed |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Close II Failure |  | 13 |  |  | ▲▼ | Alarm | Transfer to S2 failed |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Switch Position Alarm |  | 14 |  |  | ▲▼ | Alarm | Switch position is not available |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| High Current Alarm |  | 15 |  |  | ▲▼ | Alarm | Current is over alarm level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
55 | Status Warnings Alarms 3 | 1 | B |  |  |  | Bitfield | Info / warning / alarm | - | - | U16 |  |  | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 | 8 | 8 |  | R | V |  |  | yes | Warning/Alarm/Info | 100 ms / HF
| Internal Error |  | 0 |  |  | ▲▼ | Alarm | Internal malfunction activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Alarm/Product Availability |  | 1 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| In Position I |  | 2 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Invalid Date Warning |  | 3 |  |  | ▲▼ | Info | Date is not set |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Control Voltage Failure |  | 4 |  |  | ▲▼ | Alarm | Control voltage collapsed below 140 V during transfer sequence |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Pole Temperature Alarm |  | 5 |  |  | ▲▼ | Alarm | Pole temperature is over alarm level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Pole Temperature Warning |  | 6 |  |  | ▲▼ | Warning | Pole temperature is over warning level |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Control Retry |  | 7 |  |  | ▲▼ | Warning | Retry failed control sequence |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| In Position O |  | 8 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| In Position II |  | 9 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Pre-transfer Signal |  | 10 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Auto Control Disabled |  | 11 |  |  | ▲▼ | Warning | Automatic Mode Off |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Permanent Manual Mode |  | 12 |  |  | ▲▼ | Alarm | Permanent Manual Mode activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Control Voltage Low |  | 13 |  |  | ▲▼ | Alarm | Solenoid control voltage is below 158.4 V |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Voltage Not Calibrated |  | 14 |  |  | ▲▼ | Warning | Voltage calibration factors not available or invalid |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Current Not Calibrated |  | 15 |  |  | ▲▼ | Warning | Current calibration factors not available or invalid |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
56 | Status Warnings Alarms 4 | 1 | B |  |  |  | Bitfield | Info / warning / alarm | - | - | U16 |  |  | X | [6 empty] | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 | 10 | 10 |  | R | V |  |  | yes | Warning/Alarm/Info | 100 ms / HF
| Emergency Stop |  | 0 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Remote Test on Load |  | 1 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Remote Test off Load |  | 2 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Inhibit ATS |  | 3 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Manual Retransfer |  | 4 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Priority S1 |  | 5 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Priority S2 |  | 6 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Inhibit Transfer |  | 7 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Bypass Running Delays |  | 8 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Remote Control to S1 |  | 9 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Remote Control to Off |  | 10 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Remote Control to S2 |  | 11 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Alarm Reset |  | 12 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Source 1 Available |  | 13 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Source 2 Available |  | 14 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Load Shed Output Signal |  | 15 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
57 | Status Warnings Alarms 5 | 1 | B |  |  |  | Bitfield | Info / warning / alarm | - | - | U16 |  |  | X | [6 empty] | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 | 12 | 12 |  | R | V |  |  | yes | Warning/Alarm/Info | 100 ms / HF
| IEEE1588 Out of Synch |  | 0 |  |  |  | Warning |  |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Heartbeat Error on Connected Modules Warning |  | 1 |  |  |  | Warning | Heartbeat error |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Configuration Error |  | 2 |  |  |  | Alarm | Configuration error |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S1 Neutral disconnected |  | 3 |  |  | ▲▼ | Alarm | Neutral disconnected on S1 |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| S2 Neutral disconnected |  | 4 |  |  | ▲▼ | Alarm | Neutral disconnected on S2 |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Rating Plug installation request |  | 5 |  | X |  | Alarm | Rating plug installation request |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| SNTP Out of Synch |  | 6 |  |  |  | Warning |  |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Manual Retransfer Required |  | 7 |  |  |  | Warning | Manual retransfer required |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Modules CRC error |  | 8 |  |  |  | Alarm |  |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Module Link Status Error |  | 9 |  |  |  | Alarm | One or mode modules has an Ethernet Link Status error (disconnection) |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Rating Plug alarm |  | 10 |  | X |  |  | Rating plug installation alarm |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Generator Exerciser Test on Load |  | 11 |  |  | ▲▼ | Info | Generator Exerciser Test on Load in progress |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Controller CRC error |  | 12 |  |  |  | Alarm |  |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Generator Exerciser Test off Load |  | 13 |  |  | ▲▼ | Info | Generator Exerciser Test off Load in progress |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Ekip Com Hub Alarm |  | 14 |  |  |  | Alarm | Alarm from Ekip Com Hub module (devices, cloud, configuration) |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Configuration Session Warning |  | 15 |  |  |  | Warning | Configuration session ports are open on at least one module (TFTP, Modbus) |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
58 | Status Warnings Alarms 6 | 1 | B |  |  |  | Bitfield | Info / warning / alarm | - | - | U16 |  |  | X | [6 empty] | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 | 14 | 14 |  | R | V |  |  | yes | Warning/Alarm/Info | 100 ms / HF
| Racking Enabled |  | 0 |  |  |  | Info | Set when firefighting DI is set in ATS or Bypass switch |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| ATS Connected |  | 1 |  |  |  | Info | ATS in connected position |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| ATS Test |  | 2 |  |  |  | Info | ATS in test position |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Bypass Connected |  | 3 |  |  |  | Info | Bypass in connected position |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Bypass Test |  | 4 |  |  |  | Info | Bypass in test position |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Inhibit Transfer w/ Override |  | 5 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Load Shed Input Signal |  | 6 |  |  | ▲▼ | Info | DI function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Transfer Alarm |  | 7 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Switch Position Error (ATS/Bypass) |  | 8 |  |  |  | Info | ATS switch: Bypass position error, Bypass switch: ATS position error |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Sources Unable to Synchronize |  | 9 |  | X |  | Info | Tried to synchronize for one minute during closed transition sequence |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Pre-transfer Signal 2 |  | 10 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Pre-transfer Signal 3 |  | 11 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Pre-transfer Signal 4 |  | 12 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Elevator Pre-transfer Signal 2 |  | 13 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Elevator Pre-transfer Signal 3 |  | 14 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
| Elevator Pre-transfer Signal 4 |  | 15 |  |  | ▲▼ | Info | DO function activated |  |  | BOOL | [18 empty] | R | V |  |  |  | Warning/Alarm/Info
60 | Status Ekip Signalling 10K input | 1 | B |  |  |  | Bitfield | Ekip Signalling 10K module input status | - | - | U16 |  |  | X | [6 empty] | 21 |  |  | Instance ID = 21 | index = 21 | index = 21 | 18 | 18 | TPDO1[8,9] | R | V |  |  | yes | PDO sniffed | 100 ms / PDO
| Ekip Signalling 10K-1.1 |  | 0 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.2 |  | 1 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.3 |  | 2 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.4 |  | 3 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.5 |  | 4 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.6 |  | 5 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.7 |  | 6 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.8 |  | 7 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.9 |  | 8 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.10 |  | 9 |  |  |  | 1= Input On |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
62 | Status Ekip Signalling 2K input | 1 | B |  |  |  | Bitfield | Ekip Signalling 2K module input status | - | - | U16 |  |  | X | [6 empty] | 23 |  |  | Instance ID = 23 | index = 23 | index = 23 | 22 | 22 | TPDO1[4,5,6] | R | V |  |  | yes | PDO sniffed | 100 ms / PDO
| Ekip Signalling 2K-1.1 |  | 0 |  |  |  | 1= Input on |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-1.2 |  | 1 |  |  |  | 1= Input on |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-2.1 |  | 4 |  |  |  | 1= Input on |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-2.2 |  | 5 |  |  |  | 1= Input on |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 6 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 7 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-3.1 |  | 8 |  |  |  | 1= Input on |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-3.2 |  | 9 |  |  |  | 1= Input on |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
63 | Status Ekip Signalling 10K output | 1 | B |  |  |  | Bitfield | Ekip Signalling 10K module output status | - | - | U16 |  |  | X | [6 empty] | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 | 24 | 24 | RPDO1[8] | R | V |  |  | yes | PDO sniffed | 100 ms / PDO
| Ekip Signalling 10K-1.1 |  | 0 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.2 |  | 1 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.3 |  | 2 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.4 |  | 3 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.5 |  | 4 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.6 |  | 5 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.7 |  | 6 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.8 |  | 7 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.9 |  | 8 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 10K-1.10 |  | 9 |  |  |  | 1= output On |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
65 | Status Ekip Signalling 2K output | 1 | B |  |  |  | Bitfield | Ekip Signalling 2K module output status | - | - | U16 |  |  | X | [6 empty] | 26 |  |  | Instance ID = 26 | index = 26 | index = 26 | 28 | 28 | RPDO1[8] | R | V |  |  | yes | PDO sniffed | 100 ms / PDO
| Ekip Signalling 2K-1.1 |  | 0 |  |  |  | 1= Output on |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-1.2 |  | 1 |  |  |  | 1= Output on |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-2.1 |  | 4 |  |  |  | 1= Output on |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-2.2 |  | 5 |  |  |  | 1= Output on |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 6 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 7 | [7 empty] | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-3.1 |  | 8 |  |  |  | 1= Output on |  |  |  | BOOL | [18 empty] | R | V
| Ekip Signalling 2K-3.2 |  | 9 |  |  |  | 1= Output on |  |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | R | V
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | R | V
100 | Current Measures | 14 | [9 empty] | R |  | X | [6 empty] | 2005 |  | 6 | 0x0069 | 0x06 | 0x0006 | [5 empty] | 7 | 32
100 | L1 current | 2 |  |  |  |  | 0 ÷ (2^32)-1 (2^32)-1 = measure not available | Example: 12345 → 1234,5 A | A | 0.1 | U32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 | 56 | 56 |  | R | V |  |  | yes | always | 200 ms / LF
102 | L2 current | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 | 60 | 60 |  | R | V |  |  | yes | always | 200 ms / LF
104 | L3 current | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 | 64 | 64 |  | R | V |  |  | yes | always | 200 ms / LF
106 | Ne current | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 | 68 | 68 |  | R | V |  |  | yes | always | 200 ms / LF
108 | Internal ground current | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 | 72 | 72 |  | R | V |  |  | yes | always | 200 ms / LF
112 | Maximum current | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 | 80 | 80 |  | R | V |  |  | yes | always | 200 ms / LF
114 | Maximum current phase | 2 |  |  |  |  | 0 = not available, 1 = L1, 2 = L2, 3 = L3, 4 = Ne | If all currents are 0, the max current phase = 0 (not available) | - | - | E32 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 | 84 | 84 |  | R | V |  |  | yes | always | 200 ms / LF
150 | Voltage Measures | 18 | [9 empty] | R |  | X | [6 empty] | 2006 |  | 7 | 0x006A | 0x07 | 0x0007 | [5 empty] | 18 | 16
150 | Source 1 U1 | 1 |  |  |  |  | 0 ... 65535 65535 = Not available | Example: 12345 → 1234,5 V | V | 0.1 | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 | 88 | 88 |  | R | V |  |  | yes | always | 200 ms / LF
151 | Source 1 U2 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 | 90 | 90 |  | R | V |  |  | yes | always | 200 ms / LF
152 | Source 1 U3 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 | 92 | 92 |  | R | V |  |  | yes | always | 200 ms / LF
153 | Source 1 U0 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 | 94 | 94 |  | R | V |  |  | yes | always | 200 ms / LF
154 | Source 1 U12 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 | 96 | 96 |  | R | V |  |  | yes | always | 200 ms / LF
155 | Source 1 U23 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 | 98 | 98 |  | R | V |  |  | yes | always | 200 ms / LF
156 | Source 1 U31 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 | 100 | 100 |  | R | V |  |  | yes | always | 200 ms / LF
157 | Source 1 Umax | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 | 102 | 102 |  | R | V |  |  | yes | always | 200 ms / LF
158 | Source 1 max phase | 1 |  |  |  |  | 0 = N/A, 1 = U1/U12, 2 = U2/U23, 3 = U3/U31 | If all voltages are 0, the max voltage phase = 0 (not available) | - | - | E16 |  |  | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 | 104 | 104 |  | R | V |  |  | yes | always | 200 ms / LF
159 | Source 2 U1 | 1 |  |  |  |  | 0 ... 65535 65535 = Not available | Example: 12345 → 1234,5 V | V | 0.1 | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | V
160 | Source 2 U2 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | V
161 | Source 2 U3 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | V
162 | Source 2 U0 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | R | V
163 | Source 2 U12 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 |  |  |  | R | V
164 | Source 2 U23 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 |  |  |  | R | V
165 | Source 2 U31 | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 20 |  |  | Instance ID = 20 | index = 20 | index = 20 |  |  |  | R | V
166 | Source 2 Umax | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 21 |  |  | Instance ID = 21 | index = 21 | index = 21 |  |  |  | R | V
167 | Source 2 max phase | 1 |  |  |  |  | 0 = N/A, 1 = U1/U12, 2 = U2/U23, 3 = U3/U31 | If all voltages are 0, the max voltage phase = 0 (not available) | - | - | U16 |  |  | X | [6 empty] | 22 | [8 empty] | R | V
200 | Power Measures | 34 | [9 empty] | R |  | X | [6 empty] | 2007 |  | 8 | 0x006B | 0x08 | 0x0008 | [5 empty] | 17 | 32
200 | Active power L1 | 2 |  |  |  |  | 0 ÷ (2^32)-1 (2^31)-1 = Not available | Example: 12345 → 1234,5 kW | kW | 0.1 | S32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 | 106 | 108 |  | R | V |  |  | yes | always | 200 ms / LF
202 | Active power L2 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 | 110 | 112 |  | R | V |  |  | yes | always | 200 ms / LF
204 | Active power L3 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 | 114 | 116 |  | R | V |  |  | yes | always | 200 ms / LF
206 | Active power Total | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 | 118 | 120 |  | R | V |  |  | yes | always | 200 ms / LF
208 | Reactive power L1 | 2 | [5 empty] | Example: 12345 → 1234,5 kVAr | kVAr | 0.1 | S32 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 | 122 | 124 |  | R | V |  |  | yes | always | 200 ms / LF
210 | Reactive power L2 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 | 126 | 128 |  | R | V |  |  | yes | always | 200 ms / LF
212 | Reactive power L3 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 | 130 | 132 |  | R | V |  |  | yes | always | 200 ms / LF
214 | Reactive power Total | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 | 134 | 136 |  | R | V |  |  | yes | always | 200 ms / LF
216 | Apparent power L1 | 2 | [5 empty] | Example: 12345 → 1234,5 kVA | kVA | 0.1 | S32 |  |  | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 | 138 | 140 |  | R | V |  |  | yes | always | 200 ms / LF
218 | Apparent power L2 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 | 142 | 144 |  | R | V |  |  | yes | always | 200 ms / LF
220 | Apparent power L3 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 | 146 | 148 |  | R | V |  |  | yes | always | 200 ms / LF
222 | Apparent power Total | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 | 150 | 152 |  | R | V |  |  | yes | always | 200 ms / LF
224 | Source 2 U1 - U2 | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | V |  |  | yes | always | 200 ms / LF
226 | Source 2 U3 - U0 | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | V |  |  | yes | always | 200 ms / LF
228 | Source 2 U12 - U23 | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | V |  |  | yes | always | 200 ms / LF
230 | Source 2 U31 - Umax | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | R | V |  |  | yes | always | 200 ms / LF
232 | Source 2 max phase | 2 | [8 empty] | U32 |  |  | X | [6 empty] | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | R | V |  |  | yes | always | 200 ms / LF
250 | Other Measures | 30 | [9 empty] | R |  | X | [6 empty] | 2008 |  | 9 | 0x006C | 0x09 | 0x0009 | [5 empty] | 30 | 16
250 | Synchronization Time to Sync | 1 |  |  |  |  | 0..65535, 65535 = not available | Time to next synchronization window | s | 1 | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
251 | Synchronization Period | 1 |  |  |  |  | 0..65535, 65535 = not available | Time between synchronization window starts | ms | 1 | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
252 | Temperature HMI | 1 |  |  |  |  | -32768..32767 (0x7FFF = N/A) | 250 <=> 25.0 degrees Celsius | C | 0.1 | S16 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3
253 | Power Factor Total | 1 |  |  |  |  | -1000 ÷ +1000 (0x7FFF = measure not available) | Example: the number 987 → cosɸ = 0.987 | U | 0.001 | S16 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 | 154 | 156 |  | R | V |  |  | yes | always | 200 ms / LF
254 | Source 1 frequency | 1 |  |  |  |  | 0 ÷ 65535 (0xFFFF = measure not available ) | Example: the number 502 → 50.2 Hz | Hz | 0.1 | U16 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 | 156 | 158 |  | R | V |  |  | yes | always | 200 ms / LF
255 | Source 2 frequency | 1 |  |  |  |  | 0 ÷ 65535 (0xFFFF = measure not available ) | Example: the number 502 → 50.2 Hz | Hz | 0.1 | U16 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | V
256 | Temperature PT100/1000 sensor | 1 |  |  | X |  | -5000 ÷ 25000; 0x7FFF = absent sensor | Temperature Sensor 1 Measure; -50.00 ÷ 250.00 °C step 0.01 °C | °C | 0.01 | U16 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | R | V
257 | Temperature Pole 1 | 1 |  | X |  |  | -32768..32767 (0x7FFF = not available) |  | % | 1 | S16 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 | 158 | 160 |  | R | V |  |  | yes | always | 200 ms / LF
258 | Temperature Pole 2 | 1 |  | X |  |  |  | -45 <=> 0.45 * tmin |  |  | S16 |  |  | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 | 160 | 162 |  | R | V |  |  | yes | always | 200 ms / LF
259 | Temperature Pole 3 | 1 |  | X |  |  |  | 87 <=> 0.87 * tmax |  |  | S16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 | 162 | 164 |  | R | V |  |  | yes | always | 200 ms / LF
260 | Temperature Pole 4 | 1 |  | X | [6 empty] | S16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 | 164 | 166 |  | R | V |  |  | yes | always | 200 ms / LF
261 | Temperature Internal | 1 |  |  |  |  | -32768..32767 (0x7FFF = N/A) | 250 <=> 25.0 degrees Celsius | C | 0.1 | S16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | V
262 | Contact Wear End of Life Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 00:00:00 31 dec 1999 | s | 1 | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | V
263 | Contact Wear End of Life High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | V
264 | Generator Exerciser Delay Ongoing value Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 24:00:00 | s | 1 | U16 |  |  | X | [6 empty] | 1
265 | Generator Exerciser Delay Ongoing value High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  |  | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | R | V
266 | Manual Operations | 1 |  |  |  |  | 0 ÷ 65535 | Number of switch transfers operated by the handle | - | 1 | U16 |  |  | X | [6 empty] | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | R | V
267 | Last Generator Start Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 00:00:00 31 dec 1999 | s | 1 | U16 |  |  | X | [6 empty] | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 |  |  |  | R | V
268 | Last Generatot Start Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  |  | X | [6 empty] | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 |  |  |  | R | V
269 | Generator Starting Time | 1 |  |  |  |  | 0 ÷ 65535 | How long it took for the generator voltage to become acceptable | s | 1 | U16 |  |  | X | [6 empty] | 20 |  |  | Instance ID = 20 | index = 20 | index = 20 |  |  |  | R | V
270 | In-phase Time | 1 |  |  |  |  | 0 ÷ 65535 | How long it took to run the in-phase monitor achieve in-phase transfer | s | 1 | U16 |  |  | X | [6 empty] | 21 |  |  | Instance ID = 21 | index = 21 | index = 21 |  |  |  | R | V
271 | Time Normal Available | 2 |  |  |  |  | 0 ÷ 0xFFFFFFFF | Total time the normal source has been available | min | 1 | U32 |  |  | X | [6 empty] | 22 |  |  | Instance ID = 22 | index = 22 | index = 22 |  |  |  | R | V
273 | Total Time on Normal | 2 |  |  |  |  | 0 ÷ 0xFFFFFFFF | Total time the load has been connected to the normal source | h | 1 | U32 |  |  | X | [6 empty] | 23 |  |  | Instance ID = 23 | index = 23 | index = 23 |  |  |  | R | V
275 | Time Emergency Available | 2 |  |  |  |  | 0 ÷ 0xFFFFFFFF | Total time the emergency source has been available | min | 1 | U32 |  |  | X | [6 empty] | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 |  |  |  | R | V
277 | Total Time on Emergency | 2 |  |  |  |  | 0 ÷ 0xFFFFFFFF | Total time the load has been connected to the emergency source | h | 1 | U32 |  |  | X | [6 empty] | 25 |  |  | Instance ID = 25 | index = 25 | index = 25 |  |  |  | R | V
279 | Reserved | 1 |  |  |  |  | 0..65535 | reserved |  |  | U16 |  |  | X | [6 empty] | 26 |  |  | Instance ID = 26 | index = 26 | index = 26 |  |  |  | R | V
300 | Energy Measures | 20 | [9 empty] | R |  | X | [6 empty] | 2009 |  | 10 | 0x006D | 0x0A | 0x000A | [5 empty] | 10 | 32
300 | Active Energy S1 | 2 |  |  |  |  | 0 ÷ (2^32)-1 | Example: 123456789 → 123456789 kWh | kWh | 1 | S32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 | 166 | 168 |  | R | V |  |  | yes | always | 200 ms / LF
302 | Active Energy S2 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 | 170 | 172 |  | R | V |  |  | yes | always | 200 ms / LF
304 | Reactive Energy S1 | 2 | [5 empty] | Example: 123456789 → 123456789 kVARh | kVARh | 1 | S32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 | 174 | 176 |  | R | V |  |  | yes | always | 200 ms / LF
306 | Reactive Energy S2 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 | 178 | 180 |  | R | V |  |  | yes | always | 200 ms / LF
308 | Apparent Energy S1 | 2 | [5 empty] | Example: 123456789 → 123456789 kVAh | kVAh | 1 | S32 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 | 182 | 184 |  | R | V |  |  | yes | always | 200 ms / LF
310 | Apparent Energy S2 | 2 | [8 empty] | S32 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 | 186 | 188 |  | R | V |  |  | yes | always | 200 ms / LF
314 | Energy Store Time | 2 | [5 empty] | Number of seconds of energy store time | s | 1 | U32 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | R | V
316 | Active Energy Total | 2 | [5 empty] | Example: 123456789 → 123456789 kWh | kWh | 1 | U32 |  |  | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | R | V
318 | Reactive Energy Total | 2 | [5 empty] | Example: 123456789 → 123456789 kVARh | kVARh | 1 | U32 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | V
320 | Apparent Energy Total | 2 | [5 empty] | Example: 123456789 → 123456789 kVAh | kVAh | 1 | U32 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | V
350 | Harmonics Measures | 52 | [9 empty] | R |  | X | [6 empty] | 2010 |  | 11 | 0x006E | 0x0B | 0x000B | [5 empty] | 52 | 16
350 | Voltage source 1 U1/U12 THD | 1 |  |  |  |  | 0 ÷ 10000 | 1000 => 10 % | % | 0.01 | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
351 | Voltage source 1 U2/U23 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | V
352 | Voltage source 1 U3/U31 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | V
353 | Voltage source 2 U1/U12 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | V
354 | Voltage source 2 U2/U23 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | V
355 | Voltage source 2 U3/U31 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | V
356 | Current I1 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | R | V
357 | Current I2 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | R | V
358 | Current I3 THD | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | R | V
359 | Voltage source 1 2nd harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | V
360 | Voltage source 1 3rd harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | V
361 | Voltage source 1 4th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | V
362 | Voltage source 1 5th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | V
363 | Voltage source 1 6th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | V
364 | Voltage source 1 7th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | V
365 | Voltage source 1 8th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | R | V
366 | Voltage source 1 9th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | R | V
367 | Voltage source 1 10th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 |  |  |  | R | V
368 | Voltage source 1 11th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 |  |  |  | R | V
369 | Voltage source 1 12th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 20 |  |  | Instance ID = 20 | index = 20 | index = 20 |  |  |  | R | V
370 | Voltage source 1 13th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 21 |  |  | Instance ID = 21 | index = 21 | index = 21 |  |  |  | R | V
371 | Voltage source 1 14th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 22 |  |  | Instance ID = 22 | index = 22 | index = 22 |  |  |  | R | V
372 | Voltage source 1 15th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 23 |  |  | Instance ID = 23 | index = 23 | index = 23 |  |  |  | R | V
373 | Voltage source 2 2nd harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 |  |  |  | R | V
374 | Voltage source 2 3rd harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 25 |  |  | Instance ID = 25 | index = 25 | index = 25 |  |  |  | R | V
375 | Voltage source 2 4th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 26 |  |  | Instance ID = 26 | index = 26 | index = 26 |  |  |  | R | V
376 | Voltage source 2 5th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 27 |  |  | Instance ID = 27 | index = 27 | index = 27 |  |  |  | R | V
377 | Voltage source 2 6th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 28 |  |  | Instance ID = 28 | index = 28 | index = 28 |  |  |  | R | V
378 | Voltage source 2 7th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 29 |  |  | Instance ID = 29 | index = 29 | index = 29 |  |  |  | R | V
379 | Voltage source 2 8th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 30 |  |  | Instance ID = 30 | index = 30 | index = 30 |  |  |  | R | V
380 | Voltage source 2 9th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 31 |  |  | Instance ID = 31 | index = 31 | index = 31 |  |  |  | R | V
381 | Voltage source 2 10th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 32 |  |  | Instance ID = 32 | index = 32 | index = 32 |  |  |  | R | V
382 | Voltage source 2 11th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 33 |  |  | Instance ID = 33 | index = 33 | index = 33 |  |  |  | R | V
383 | Voltage source 2 12th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 34 |  |  | Instance ID = 34 | index = 34 | index = 34 |  |  |  | R | V
384 | Voltage source 2 13th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 35 |  |  | Instance ID = 35 | index = 35 | index = 35 |  |  |  | R | V
385 | Voltage source 2 14th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 36 |  |  | Instance ID = 36 | index = 36 | index = 36 |  |  |  | R | V
386 | Voltage source 2 15th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 37 |  |  | Instance ID = 37 | index = 37 | index = 37 |  |  |  | R | V
387 | Current 2nd harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 38 |  |  | Instance ID = 38 | index = 38 | index = 38 |  |  |  | R | V
388 | Current 3rd harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 39 |  |  | Instance ID = 39 | index = 39 | index = 39 |  |  |  | R | V
389 | Current 4th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 40 |  |  | Instance ID = 40 | index = 40 | index = 40 |  |  |  | R | V
390 | Current 5th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 41 |  |  | Instance ID = 41 | index = 41 | index = 41 |  |  |  | R | V
391 | Current 6th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 42 |  |  | Instance ID = 42 | index = 42 | index = 42 |  |  |  | R | V
392 | Current 7th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 43 |  |  | Instance ID = 43 | index = 43 | index = 43 |  |  |  | R | V
393 | Current 8th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 44 |  |  | Instance ID = 44 | index = 44 | index = 44 |  |  |  | R | V
394 | Current 9th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 45 |  |  | Instance ID = 45 | index = 45 | index = 45 |  |  |  | R | V
395 | Current 10th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 46 |  |  | Instance ID = 46 | index = 46 | index = 46 |  |  |  | R | V
396 | Current 11th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 47 |  |  | Instance ID = 47 | index = 47 | index = 47 |  |  |  | R | V
397 | Current 12th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 48 |  |  | Instance ID = 48 | index = 48 | index = 48 |  |  |  | R | V
398 | Current 13th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 49 |  |  | Instance ID = 49 | index = 49 | index = 49 |  |  |  | R | V
399 | Current 14th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 50 |  |  | Instance ID = 50 | index = 50 | index = 50 |  |  |  | R | V
400 | Current 15th harmonic ratio | 1 | [6 empty] | % | 0.01 | U16 |  |  | X | [6 empty] | 51 |  |  | Instance ID = 51 | index = 51 | index = 51 |  |  |  | R | V
401 | Phase Number | 1 |  |  |  |  | 0 = none , 1 = phase 1, 2 = phase 2, 3 = phase 3 | Phase for harmonic components calculation | - | 1 | U16 | [6 empty] | X |  |  | 52 |  |  | Instance ID = 52 | index = 52 | index = 52 |  |  |  | R | V
500 | Information | 51 | [9 empty] | R |  | X | [6 empty] | 2014 |  | 12 | 0x006F | 0x0C | 0x000C | [5 empty] | 51 | 16
500 | Slave ID | 1 |  |  |  |  | 170 ÷ 172 | 170 = Level 2 (T1), 171 = Level 3 (T1), 172 = Level 4 (T1) , 173 = Level 2 (TC), 1714= Level 3 (TC), 175 = Level 4 (TC) | - | - | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
501 | SW Version | 1 |  |  |  |  | MAJOR.minor | SW version | - | - | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
502 | Product Standard Reference | 1 |  |  |  |  | 0 = IEC, 1 = UL | IEC/UL | - | - | U16 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | S
503 | Switch Flags | 1 | B |  |  |  | Bitfield |  | - | - | - |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4
| Cabling Direction |  | 0 |  |  |  | 0 or 1 | 0 = bottom entry; 1 = top entry
| NOT USED |  | 1
| NOT USED |  | 2
| NOT USED |  | 3
| NOT USED |  | 4
| NOT USED |  | 5
| NOT USED |  | 6
| NOT USED |  | 7
| NOT USED |  | 8
| NOT USED |  | 9
| NOT USED |  | 10
| NOT USED |  | 11
| NOT USED |  | 12
| NOT USED |  | 13
| NOT USED |  | 14
| NOT USED |  | 15
504 | Nominal Current | 1 |  |  |  |  | 30 ÷ 4000 | Nominal current | A | 1 | U16 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | S
505 | Number of Switch Positions | 1 |  |  |  |  | 0 = I - O - II , 1 = I - II valid for TruONE 0 = I - II , 1 = I - O - II , 2 = I - O - II CLOSED valid for TruCONTROL | Two or three switch positions | - | - | U16 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RrW | S
506 | Serial Number | 8 |  |  |  |  | 0 ÷ 65535 | 16 ASCII characters | - | - | CHAR |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RrW | S
514 | Type Designation | 8 |  |  |  |  | 0 ÷ 65535 | 16 ASCII characters | - | - | CHAR |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15
522 | Number of Poles | 1 |  |  |  |  | 2 ÷ 4 | Number of poles | - | - | U16 |  |  | X | [6 empty] | 23 |  |  | Instance ID = 23 | index = 23 | index = 23 |  |  |  | RrW | S
523 | HMI Type | 1 |  |  |  |  | 0 ÷ 6 | 0=DIP/I-O-II, 1=DIP/I-II, 2=LCD/I-O-II, 3=LCD/I-II, 4=TOUCH/I-O-II, 5=TOUCH/I-II, 6 = INVALID | - | - | U16 |  |  | X | [6 empty] | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 |  |  |  | RrW | S
524 | HMI SW Version | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware version | - | - | U16 |  |  | X | [6 empty] | 25 |  |  | Instance ID = 25 | index = 25 | index = 25 |  |  |  | RrW | S
525 | HMI SW Subversion | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware subversion | - | - | U16 |  |  | X | [6 empty] | 26 |  |  | Instance ID = 26 | index = 26 | index = 26
526 | HMI DIP SW CRC Low | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware CRC low | - | - | U16 |  |  | X | [6 empty] | 27 |  |  | Instance ID = 27 | index = 27 | index = 27
527 | HMI DIP SW CRC High | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware CRC high | - | - | U16 |  |  | X | [6 empty] | 28 |  |  | Instance ID = 28 | index = 28 | index = 28
528 | HMI Home Page | 1 |  |  |  |  | 0 ÷ 65535 | HMI home page | - | - | U16 |  |  | X | [6 empty] | 29 |  |  | Instance ID = 29 | index = 29 | index = 29
529 | HMI S1 Voltmeter Phase | 1 |  |  |  |  | 0 = Vmax, 1 = U12, 2 = U23, 3 = U31 | Meter value for voltage source 1 | - | - | U16 |  |  | X | [6 empty] | 30 |  |  | Instance ID = 30 | index = 30 | index = 30
530 | HMI S2 Voltmeter Phase | 1 |  |  |  |  | 0 = Vmax, 1 = U12, 2 = U23, 3 = U31 | Meter value for voltage source 2 | - | - | U16 |  |  | X | [6 empty] | 31 |  |  | Instance ID = 31 | index = 31 | index = 31
531 | HMI Ammeter Phase | 1 |  |  |  |  | 0 = Imax, 1 = L1, 2 = L2, 3 = L3, 4 = Ne | Meter value for current | - | - | U16 |  |  | X | [6 empty] | 32 |  |  | Instance ID = 32 | index = 32 | index = 32
532 | HMI Serial Number | 8 |  |  |  |  | 0 ÷ 65535 | 16 characters | - | - | U16 |  |  | X | [6 empty] | 33 |  |  | Instance ID = 33 | index = 33 | index = 33
540 | HMI LCD SW CRC Low | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware CRC low | - | - | U16 |  |  | X | [6 empty] | 41 |  |  | Instance ID = 41 | index = 41 | index = 41
541 | HMI LCD SW CRC High | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware CRC high | - | - | U16 |  |  | X | [6 empty] | 42 |  |  | Instance ID = 42 | index = 42 | index = 42
542 | HMI TOUCH SW CRC Low | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware CRC low | - | - | U16 |  |  | X | [6 empty] | 43 |  |  | Instance ID = 43 | index = 43 | index = 43
543 | HMI TOUCH SW CRC High | 1 |  |  |  |  | 0 ÷ 65535 | HMI firmware CRC high | - | - | U16 |  |  | X | [6 empty] | 44 |  |  | Instance ID = 44 | index = 44 | index = 44
544 | Unit Configuration | 1 | B |  |  |  | Bitfield |  | - | - | - |  |  | X | [6 empty] | 45 |  |  | Instance ID = 45 | index = 45 | index = 45 |  |  |  | RrW | S
| Local Bus |  | 0 |  |  |  | 0 or 1 | 0 = Disabled; 1 = Enabled |  |  | BOOL | [18 empty] | RrW | S
| NOT USED |  | 1 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 4 | [7 empty] | BOOL | [18 empty] | RrW | S
| Configuration Mode |  | 5 |  |  |  | 0 or 1 | 0 = Local; 1 = Remote |  |  | BOOL | [18 empty] | RrW | S
| NOT USED |  | 6 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 7 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 8 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 9 | [7 empty] | BOOL | [18 empty] | RrW
| NOT USED |  | 10 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | RrW | S
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | RrW | S
545 | Date Of Last Maintenance Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | Timestamp of last maintenace of CB (Seconds from 00:00:00 31 december 1999) | s | - | U16 |  |  | X | [6 empty] | 46 |  |  | Instance ID = 46 | index = 46 | index = 46 |  |  |  | RrW | S
546 | Date Of Last Maintenance Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  | s | - | U16 |  |  | X | [6 empty] | 47 |  |  | Instance ID = 47 | index = 47 | index = 47 |  |  |  | RrW | S
547 | Sensor Module Type | 1 |  |  |  |  | 0 ÷ 3 | 0 = None, 1 = 250 A, 2 = 800 A, 3 = 1600 A | - | - | U16 |  |  | X | [6 empty] | 48 |  |  | Instance ID = 48 | index = 48 | index = 48
548 | Switch Type | 1 |  |  |  |  | 0…2 | 0 = Standard, 1 = ATS, 2 = Bypass | - | - | U16 |  |  | X | [6 empty] | 49 |  |  | Instance ID = 49 | index = 49 | index = 49 |  |  |  | R | S
549 | Source 1 voltage unbalance | 1 |  |  |  |  | 0…100 | S1 U0 percentage of rated voltage | % | - | U16 |  |  | X | [6 empty] | 50 |  |  | Instance ID = 50 | index = 50 | index = 50 |  |  |  | R | S
550 | Source 2 voltage unbalance | 1 |  |  |  |  | 0…100 | S2 U0 percentage of rated voltage | % | - | U16 |  |  | X | [6 empty] | 51 |  |  | Instance ID = 51 | index = 51 | index = 51 |  |  |  | R | S
625 | Configuration | 37 | [9 empty] | RW | X | X | X | X |  |  |  |  | 201F | 401F | 13 | 0x0070 | 0x0D | 0x000D | [5 empty] | 37 | 16
625 | Time Zone settings | 1 | B |  |  |  | Bitfield |  | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
| UTC time zone |  | 0 | [7 empty] | U16
1
2
3
4
5
6
7
| DST enable |  | 8 |  |  |  | 0 = force OFF on module, 1 = force ON on module |  |  |  | BOOL
9
| UTC managed on CORE |  | 10 |  |  |  | 0 = UTC managed on modules, 1 = UTC managed on Protection Unit |  |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
626 | Installation Date Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | Seconds from 00:00:00 31 december 1999 | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
627 | Installation Date Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
628 | Switch Name | 5 |  |  |  |  | 0 ÷ 65535 | 10 character free space | - | - | CHAR |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
633 | User Data | 5 |  |  |  |  | 0 ÷ 65535 | 10 character free space | - | - | CHAR |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
638 | Source 1 Power Distribution System | 1 |  |  |  |  | 0 ÷ 4 | 0 = 1 phase, 1 = 2 phases, 2 = 3 phases, 3 = 3 phases + neutral, 4 = 3 phases + high leg | - | - | U16 |  | X | X | X | X |  |  |  |  | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | RrW | S
639 | Source 2 Power Distribution System | 1 |  |  |  |  | 0 ÷ 4 | 0 = 1 phase, 1 = 2 phases, 2 = 3 phases, 3 = 3 phases + neutral, 4 = 3 phases + high leg | - | - | U16 |  | X | X | X | X |  |  |  |  | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | RW | S
640 | Application | 1 |  |  |  |  | 0 ÷ 4 | 0 = S1-transf/S2-gen, 1 = S2-transf/S1-gen, 2 = 2 transf/S1 priority, 3 = 2 transf/S2 priority, 4 = 2 transf/No priority | - | - | U16 |  | X | X | X | X |  |  |  |  | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | RW | S
641 | Language | 1 |  |  |  |  | 0 ÷ 6 | 0 = ENG, 1 = ITA, 2 = FRA, 3 = GER, 4 = SPA, 5 = RUS, 6 = CHN | - | - | U16 |  | X | X | X | X |  |  |  |  | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | RW | S
642 | Override S1 Failure Delay | 1 |  |  |  |  | 0 ÷ 600 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 18 |  |  | Instance ID = 18 | index = 18 | index = 18
643 | Unit Configuration | 1 | B |  |  |  | Bitfield |  | - | - | - |  | X | X | X | X |  |  |  |  | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 |  |  |  | RW | S
| HMI Time Format |  | 0 |  |  |  | 0 ÷ 1 | 0 = 24 h, 1 = 12 h |  |  | BOOL
| HMI Temperature Format |  | 1 |  |  |  | 0 ÷ 1 | 0 = Celsius, 1 = Fahrenheit |  |  | BOOL
| Rated Frequency |  | 2 |  |  |  | 0 ÷ 1 | 0 = 50 Hz, 1 = 60 Hz |  |  | BOOL
| Manual Retransfer |  | 3 |  |  |  | 0 ÷ 1 | 0 = Off, 1 = On |  |  | BOOL
| High Current Alarm Enabled |  | 4 |  |  |  | 0 ÷ 1 | 0 = Disabled, 1 = Enabled |  |  | BOOL
| Bypass Local Test on Load in Case of Generator Failure |  | 5 |  |  |  | 0 ÷ 1 | 0 = Bypass if Gen. Fails, 1 = Stay on Gen. |  |  | BOOL
| Bypass Remote Test on Load in Case of Generator Failure |  | 6 |  |  |  | 0 ÷ 1 | 0 = Bypass if Gen. Fails, 1 = Stay on Gen. |  |  | BOOL
| In-Phase Monitor |  | 7 |  |  |  | 0 ÷ 1 | 0 = Off, 1 = On |  |  | BOOL
| Commit Transfer |  | 8 |  |  |  | 0 ÷ 1 | 0 = Off, 1 = On |  |  | BOOL
| Neutral Position |  | 9 |  |  |  | 0 ÷ 1 | 0 = Neutral in last pole; 1 = Neutral in first pole |  |  | BOOL
| Network Settings Retention |  | 10 |  |  |  | 0 ÷ 1 | 1 = Retain network settings for newly connected EKIP COM modules |  |  | BOOL
| HMI Control Keys Enabled |  | 11 |  |  |  | 0 ÷ 1 | 0 = Disabled, 1 = Enabled |  |  | BOOL
| Digital Input 1 Contact Type |  | 12 |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
| Digital Input 2 Contact Type |  | 13 |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
| Digital Input 3 Contact Type |  | 14 |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
| Digital Output 1 Contact Type |  | 15 |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
644 | Transfer from S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 3600 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 20 |  |  | Instance ID = 20 | index = 20 | index = 20 |  |  |  | RW | S
645 | Override S2 Failure Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 21 |  |  | Instance ID = 21 | index = 21 | index = 21
646 | Rated Voltage | 1 |  |  |  |  | 0 ÷ 28 | 0…12: 200 / 208 / 220 / 230 / 240 / 277 / 347 / 380 / 400 / 415 / 440 / 460 / 480 V (3 ph) 13…28: 200 / 220 / 230 / 240 / 254 / 265 / 277 / 318 / 333 / 347 / 380 / 400 / 415 / 440 / 460 / 480 V (1 ph) | - | - | U16 |  | X | X | X | X |  |  |  |  | 22 |  |  | Instance ID = 22 | index = 22 | index = 22
647 | Transfer from S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 7200 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 23 |  |  | Instance ID = 23 | index = 23 | index = 23
648 | Generator Stop Delay | 1 |  |  |  |  | 0 ÷ 3600 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 |  |  |  | RW | S
649 | Center-Off Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 25 |  |  | Instance ID = 25 | index = 25 | index = 25 |  |  |  | RW | S
650 | Pre-transfer 2 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 26 |  |  | Instance ID = 26 | index = 26 | index = 26 |  |  |  | RW | S
651 | Post-transfer 2 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 27 |  |  | Instance ID = 27 | index = 27 | index = 27
652 | Pre-transfer 2 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 28 |  |  | Instance ID = 28 | index = 28 | index = 28 |  |  |  | RW | S
653 | Post-transfer 2 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 29 |  |  | Instance ID = 29 | index = 29 | index = 29
654 | Pre-transfer 3 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 30 |  |  | Instance ID = 30 | index = 30 | index = 30 |  |  |  | RW | S
655 | Post-transfer 3 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 31 |  |  | Instance ID = 31 | index = 31 | index = 31
656 | Pre-transfer 3 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 32 |  |  | Instance ID = 32 | index = 32 | index = 32 |  |  |  | RW | S
657 | Post-transfer 3 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 33 |  |  | Instance ID = 33 | index = 33 | index = 33
658 | Pre-transfer 4 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 34 |  |  | Instance ID = 34 | index = 34 | index = 34 |  |  |  | RW | S
659 | Post-transfer 4 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 35 |  |  | Instance ID = 35 | index = 35 | index = 35
660 | Pre-transfer 4 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 36 |  |  | Instance ID = 36 | index = 36 | index = 36 |  |  |  | RW | S
661 | Post-transfer 4 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 37 |  |  | Instance ID = 37 | index = 37 | index = 37
700 | Configuration 2.1 | 9 | [10 empty] | X | X | X | X |  |  |  |  | 2040 | 4040 | 16 | 0x0073 | 0x10 | 0x0010 | [5 empty] | 9 | 16
700 | Harmonics Phase | 1 |  |  |  |  | 0 ÷ 3 | 0 = disabled, 1 = phase 1/12, 2 = phase 2/23, 3 = phase3/31 | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
701 | DI 1 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
702 | DI 2 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
703 | DI 3 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
704 | DO 1 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
705 | Pre-transfer 1 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
706 | Post-transfer 1 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
707 | Pre-transfer 1 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 8 | [8 empty] | RW | S
708 | Post-transfer 1 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 300 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 9 | [8 empty] | RW | S
710 | Configuration 2.2 | 9 | [10 empty] | X | X | X | X |  |  |  |  | 2041 | 4041 | 17 | 0x0074 | 0x11 | 0x0011 | [5 empty] | 9 | 16
710 | LCD Contrast | 1 |  |  |  |  | 20 ÷ 80 | LCD contrast | % | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
711 | DIP Switch Values | 1 | B |  |  |  | Bitfield |  |  |  | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
| Auto Configuration |  | 0 |  |  |  | 0 ÷ 1 | 0 = Off; 1 = On |  |  | BOOL | [18 empty] | RW | S
| In-phase Monitor |  | 1 |  |  |  | 0 ÷ 1 | 0 = Off; 1 = On |  |  | BOOL | [18 empty] | RW | S
| Application (Priority) |  | 2 |  |  |  | 0 ÷ 1 | 0 = Two transformers/No priority ; 1 = S1-Transformer/S2-Generator |  |  | BOOL | [18 empty] | RW | S
| Manual Retransfer |  | 3 |  |  |  | 0 ÷ 1 | 0 = Off ; 1 = On |  |  | BOOL | [18 empty] | RW | S
| Generator Stop Delay |  | 4 |  |  |  | 0 ÷ 1 | 0 = 4 min ; 1 = 30 s |  |  | BOOL | [18 empty] | RW | S
| Center-Off Delay |  | 5 |  |  |  | 0 ÷ 1 | 0 = 4 s ; 1 = 0 s |  |  | BOOL | [18 empty] | RW | S
| Override S1 Failure Delay |  | 6 |  |  |  | 0 ÷ 15 | 0 = 0 s; 1 = 1 s; 2 = 2 s; 3 = 3 s; 4 = 4 s; 5 = 5 s; 6 = 10 s; 7 = 15 s; 8 = 20 s; 9-15 = 30 s |  |  | BOOL | [18 empty] | RW | S
|  |  | 7 | [7 empty] | BOOL | [18 empty] | RW | S
|  |  | 8 | [7 empty] | BOOL | [18 empty] | RW | S
|  |  | 9 | [7 empty] | BOOL | [18 empty] | RW | S
| Transfer from S2 to S1 Delay |  | 10 |  |  |  | 0 ÷ 15 | 0 = 0 min; 1 = 1 min; 2 = 2 min; 3 = 3 min; 4 = 4 min; 5 = 5 min; 6 = 10 min; 7 = 15 min; 8 = 20 min; 9-15 = 30 min |  |  | BOOL | [18 empty] | RW | S
|  |  | 11 | [7 empty] | BOOL | [18 empty] | RW | S
|  |  | 12 | [7 empty] | BOOL | [18 empty] | RW | S
|  |  | 13 | [7 empty] | BOOL | [18 empty] | RW | S
| Drop-out Voltage and Frequency |  | 14 |  |  |  | 0 ÷ 3 | 0 = 5 % Un / 5 % fn; 1 = 10 % Un / 5 % fn; 2 = 15 % Un / 10 % fn; 3 = 20 % Un / 10 % fn |  |  | BOOL | [18 empty] | RW | S
|  |  | 15 | [7 empty] | BOOL | [18 empty] | RW | S
712 | Load Shed Delay | 1 |  |  |  |  | 0 ÷ 60 | Switching sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
713 | Active Alarms | 1 |  |  |  |  | 0 ÷ 0x0fff | Active alarm bits | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
714 | Operation Mode | 1 |  |  |  |  | 0 ÷ 3 | 0: AUTO, 1: MAN momentary, 2: MAN permanent, 3: MAN retransfer, | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
715 | Test Mode | 1 |  |  |  |  | 0 ÷ 6 | 0 = NONE, 1 = OFF Load Local, 2 = OFF Load Rempte, 3 = OFF Load Exerciser, 4 = ON Load Local, 5 = ON Load Remote, 6 = ON Load Exerciser | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
716 | Generator Exerciser Event 1 Status | 1 |  |  |  |  | 0 ÷ 6 | 0 = Disabled, 1 = Non-periodic, 2 = Daily, 3 = Weekly, 4 = Bi-weekly, 5 = Monthly, 6 = Yearly | - | - | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
717 | Generator Exerciser Event 2 Status | 1 |  |  |  |  | 0 ÷ 6 | 0 = Disabled, 1 = Non-periodic, 2 = Daily, 3 = Weekly, 4 = Bi-weekly, 5 = Monthly, 6 = Yearly | - | - | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
718 | Generator Exerciser Event 3 Status | 1 |  |  |  |  | 0 ÷ 6 | 0 = Disabled, 1 = Non-periodic, 2 = Daily, 3 = Weekly, 4 = Bi-weekly, 5 = Monthly, 6 = Yearly | - | - | U16 |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
720 | Configuration 2.3 | 4 | [10 empty] | X | X | X | X |  |  |  |  | 2042 | 4042 | 18 | 0x0075 | 0x12 | 0x0012 | [5 empty] | 4 | 16
720 | Synchronization Window | 1 |  |  |  |  | 1 ÷ 10 step 1 | Accepted synchronization window in degrees | deg | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
721 | Generator Exerciser Event 4 Status | 1 |  |  |  |  | 0 ÷ 6 | 0 = Disabled, 1 = Non-periodic, 2 = Daily, 3 = Weekly, 4 = Bi-weekly, 5 = Monthly, 6 = Yearly | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
722 | Phase Rotation | 1 |  |  |  |  | 0 ÷ 2 | 0 = ABC, 1 = ACB, 2 = Disabled | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
723 | HMI S1 Voltmeter Phase | 1 |  |  |  |  | 0 ÷ 3 | 0 = Vmax, 1 = U12, 2 = U23, 3 = U31 | - | - | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
730 | Configuration 2.4 | 9 | [10 empty] | X | X | X | X |  |  |  |  | 2043 | 4043 | 19 | 0x0076 | 0x13 | 0x0013 | [5 empty] | 9 | 16
730 | Generator Exerciser Event 1 Function | 1 |  |  |  |  | 0 ÷ 2 | 0 = No function, 1 = Test on Load, 2 = Test off load | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
731 | S1 Dropout Voltage High | 1 |  |  |  |  | 102 ÷ 120 step 1 | +2% ÷ +20% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
732 | S1 Dropout Voltage Low | 1 |  |  |  |  | 70 ÷ 98 step 1 | -2% ÷ -30% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
733 | S1 Pickup Voltage High | 1 |  |  |  |  | 101 ÷ 119 step 1 | +1% ÷ +19% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
734 | S1 Pickup Voltage Low | 1 |  |  |  |  | 71 ÷ 99 step 1 | -1% ÷ -29% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
735 | S1 Dropout Frequency High | 1 |  |  |  |  | 1010 ÷ 1200 step 1 | +0,1% ÷ +2,0% f rated | % f | 1 | E16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
736 | S1 Dropout Frequency Low | 1 |  |  |  |  | 800 ÷ 990 step 1 | -0,1% ÷ -2,0% f rated | % f | 1 | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
737 | S1 Pickup Frequency High | 1 |  |  |  |  | 1005 ÷ 1195 step 1 | +0.1% ÷ +19.0% f rated (100.5%-119.5%) | % f | 0.1 | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
738 | S1 Pickup Frequency Low | 1 |  |  |  |  | 805 ÷ 995 step 1 | -0.1% ÷ -19.0% f rated (80.5%-99.5%) | % f | 0.1 | U16 |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
740 | Configuration 2.5 | 6 | [10 empty] | X | X | X | X |  |  |  |  | 2044 | 4044 | 20 | 0x0077 | 0x14 | 0x0014 | [5 empty] | 6 | 16
740 | Generator Exerciser Event 2 Function | 1 |  |  |  |  | 0 ÷ 2 | 0 = No function, 1 = Test on Load, 2 = Test off load | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
741 | S2 Dropout Voltage High | 1 |  |  |  |  | 102 ÷ 120 step 1 | +2% ÷ +20% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
742 | S2 Dropout Voltage Low | 1 |  |  |  |  | 70 ÷ 98 step 1 | -2% ÷ -30% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
743 | S2 Pickup Voltage High | 1 |  |  |  |  | 101 ÷ 119 step 1 | +1% ÷ +19% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
744 | S2 Pickup Voltage Low | 1 |  |  |  |  | 71 ÷ 99 step 1 | -1% ÷ -29% Un | % Un | 1 | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
745 | S2 Dropout Frequency High | 1 |  |  |  |  | 1010 ÷ 1200 step 1 | +0,1% ÷ +2,0% f rated | % f | 1 | E16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
750 | Configuration 2.6 | 9 | [10 empty] | X | X | X | X |  |  |  |  | 2045 | 4045 | 21 | 0x0078 | 0x15 | 0x0015 | [5 empty] | 9 | 16
750 | Generator Exerciser Event 3 Function | 1 |  |  |  |  | 0 ÷ 2 | 0 = No function, 1 = Test on Load, 2 = Test off load | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
751 | S2 Dropout Frequency Low | 1 |  |  |  |  | 800 ÷ 990 step 1 | -0,1% ÷ -2,0% f rated | % f | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
752 | S2 Pickup Frequency High | 1 |  |  |  |  | 1005 ÷ 1195 step 1 | +0.5% ÷ +19.5% f rated (100.5%-119.5%) | % f | 0.1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
753 | S2 Pickup Frequency Low | 1 |  |  |  |  | 805 ÷ 995 step 1 | -0.5% ÷ -19.5% f rated (80.5%-99.5%) | % f | 0.1 | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
754 | Generator Exerciser Event 4 Function | 1 |  |  |  |  | 0 ÷ 2 | 0 = No function, 1 = Test on Load, 2 = Test off load | - | - | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
755 | Generator Exerciser Event 1 Duration Minutes | 1 |  |  |  |  | 0 ÷ 1440 | Generator exerciser event 1 minutes (0…24 h) | min | 1 | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
756 | Generator Exerciser Event 1 Duration Seconds | 1 |  |  |  |  | 0 ÷ 59 | Generator exerciser event 1 seconds | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
757 | Generator Exerciser Event 2 Duration Minutes | 1 |  |  |  |  | 0 ÷ 1440 | Generator exerciser event 1 minutes (0…24 h) | min | 1 | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
758 | Generator Exerciser Event 2 Duration Seconds | 1 |  |  |  |  | 0 ÷ 59 | Generator exerciser event 1 seconds | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
760 | Generator Exerciser events | 8 | [10 empty] | X | X | X | X |  |  |  |  | 2046 | 4046 | 22 | 0x0079 | 0x16 | 0x0016 | [5 empty] | 8 | 16
760 | Generator Exerciser Event 1 Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 00:00:00 31 dec 1999 | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
761 | Generator Exerciser Event 1 Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
762 | Generator Exerciser Event 2 Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 00:00:00 31 dec 1999 | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
763 | Generator Exerciser Event 2 Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
764 | Generator Exerciser Event 3 Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 00:00:00 31 dec 1999 | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
765 | Generator Exerciser Event 3 Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
766 | Generator Exerciser Event 4 Seconds Low | 1 |  |  |  |  | 0 ÷ 65535 | 0 <=> 00:00:00 31 dec 1999 | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
767 | Generator Exerciser Event 4 Seconds High | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
770 | Configuration 2.7 | 5 | [10 empty] | X | X | X | X |  |  |  |  | 2047 | 4047 | 23 | 0x007A | 0x17 | 0x0017 | [5 empty] | 5 | 16
770 | HMI Home Page | 1 |  |  |  |  | 0 ÷ 65535 | HMI home page | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
771 | HMI Ammeter Phase | 1 |  |  |  |  | 0 ÷ 4 | 0 = Imax, 1 = L1, 2 = L2, 3 = L3, 4 = Ne | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
772 | HMI S2 Voltmeter Phase | 1 |  |  |  |  | 0 ÷ 3 | 0 = Vmax, 1 = U12, 2 = U23, 3 = U31 | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
773 | HMI PIN User Low | 1 |  |  |  |  | 0 ÷ 65535 | HMI PIN User | - | - | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
774 | HMI PIN User High | 1 |  |  |  |  | 0 ÷ 65535 |  | - | - | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
780 | Configuration 2.8 / Generator Exerciser | 3 | [10 empty] | X | X | X | X |  |  |  |  | 2048 | 4048 | 24 | 0x007B | 0x18 | 0x0018 | [5 empty] | 3 | 16
780 | Unit Configuration 2 | 1 | B |  |  |  | Bitfield |  | - | - | - |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
| Transfer to Dead Source |  | 0 |  |  |  | 0 ÷ 1 | 1 = Transfer to an unavailable source enabled |  |  | BOOL | [18 empty] | RW | S
| Center OFF delay |  | 1 |  |  |  | 0 = disable ; 1 = enable | 0 = Bypass the Center OFF delay , 1 = The timer always run |  |  | BOOL | [18 empty] | RrWr
| Pre Signal delay |  | 2 |  |  |  | 0 = disable ; 1 = enable | 0 = Bypass the Pre Signal delay , 1 = The timer always run |  |  | BOOL | [18 empty] | RW | S
| Branded device |  | 3 |  |  |  | 0…1 | 0 = Unbranded ; 1 = Branded |  |  | BOOL | [18 empty] | RrWr
| High current reset required enabled |  | 4 |  |  |  | 0 = disable ; 1 = enable | 0 = Alarm turns OFF when high current status is over, 1 = The user must reset the alarms |  |  | BOOL
| Generator start manually |  | 5 |  |  |  | 0 = disable ; 1 = enable | Inhibit gen start if slide switch not in AUTO |  |  | BOOL
| Bypass Generator Exerciser |  | 6 |  |  |  | 0 = disable ; 1 = enable | 0 = Bypass Generator Exerciser , 1 = The timer always run |  |  | BOOL
| Temp Sensor PT100/1000 enabled |  | 7 |  |  |  | 0 = disable ; 1 = enable | Enable Temperature Sensor PT100/1000 |  |  | BOOL
| Digital Output 2 Contact Type |  | 8 |  | X |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
| Digital Output 3 Contact Type |  | 9 |  | X |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
| Digital Output 4 Contact Type |  | 10 |  | X |  | 0 ÷ 1 | 0 = NC, 1 = NO |  |  | BOOL
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | RrWr
| Unbalance Measuring Enabled |  | 12 |  |  |  | 0 = disable ; 1 = enable | Voltage source asymmetry monitoring on/off |  |  | BOOL | [18 empty] | RW | S
| Metering Visible |  | 13 |  |  |  | 1 = Current measures visible | Enable/disable current measurement visualization |  |  | BOOL | [18 empty] | RW | S
| MAN Retransfer Override |  | 14 |  |  |  | 0 = off ; 1 = on | Enable automatic retransfer to healthy priority in case non-priority source has failed |  |  | BOOL | [18 empty] | RW | S
| NOT USED |  | 15 |  | X | [5 empty] | BOOL | [18 empty] | RW | S
781 | Generator Exerciser Event 3 Duration Minutes | 1 |  |  |  |  | 0 ÷ 1440 | Generator exerciser event 1 minutes (0…24 h) | min | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
782 | Generator Exerciser Event 3 Duration Seconds | 1 |  |  |  |  | 0 ÷ 59 | Generator exerciser event 1 seconds | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
790 | Elevator Pre-transfer | 3 | [10 empty] | X | X | X | X |  |  |  |  | 2049 | 4049 | 25 | 0x007C | 0x19 | 0x0019 | [5 empty] | 3 | 16
790 | Elevator Pre-transfer S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
791 | Generator Exerciser Event 4 Duration Minutes | 1 |  |  |  |  | 0 ÷ 1440 | Generator exerciser event 1 minutes (0…24 h) | min | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
792 | Generator Exerciser Event 4 Duration Seconds | 1 |  |  |  |  | 0 ÷ 59 | Generator exerciser event 1 seconds | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
800 | Elevator Pre-Post transfer 1 | 4 | [10 empty] | X | X | X | X |  |  |  |  | 204A | 404A | 26 | 0x007D | 0x1A | 0x001A | [5 empty] | 4 | 16
800 | Elevator Post-transfer 1 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
801 | Elevator Pre-transfer 1 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
802 | Elevator Post-transfer 1 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3
803 | Elevator Pre-transfer 2 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4
810 | Elevator Pre-Post transfer 2 | 3 | [10 empty] | X | X | X | X |  |  |  |  | 204B | 404B | 27 | 0x007E | 0x1B | 0x001B | [5 empty] | 3 | 16
810 | Elevator Post-transfer 2 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
811 | Elevator Pre-transfer 2 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
812 | Elevator Post-transfer 2 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3
820 | Elevator Pre-Post transfer 3 | 3 | [10 empty] | X | X | X | X |  |  |  |  | 204C | 404C | 28 | 0x007F | 0x1C | 0x001C | [5 empty] | 3 | 16
820 | Elevator Pre-transfer 3 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
821 | Elevator Post-transfer 3 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
822 | Elevator Pre-transfer 3 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3
830 | Elevator Pre-Post transfer 4 | 3 | [10 empty] | X | X | X | X |  |  |  |  | 204D | 404D | 29 | 0x0080 | 0x1D | 0x001D | [5 empty] | 3 | 16
830 | Elevator Post-transfer 3 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
831 | Elevator Pre-transfer 4 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
832 | Elevator Post-transfer 4 S1 to S2 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3
850 | Elevator Pre-Post transfer 4.1 | 2 | [10 empty] | X | X | X | X |  |  |  |  | 204F | 404F | 31 | 0x0082 | 0x1F | 0x001F | [5 empty] | 2 | 16
850 | Elevator Pre-transfer 4 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
851 | Elevator Post-transfer 4 S2 to S1 Delay | 1 |  |  |  |  | 0 ÷ 60 | Transfer sequence delay | s | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
860 | HMI informations | 5 | [10 empty] | X | X | X | X |  |  |  |  | 2050 | 4050 | 32 | 0x0083 | 0x20 | 0x0020 | [5 empty] | 5 | 16
860 | HMI type | 1 |  |  |  |  | 0 ÷ 6 | 0 = OXBMI L2 ; 1 = OXAMI L2 ; 2 = OXBMI L3 ; 3 = OXAMI L3 ; 4 = OXBMI L4 ; 5 = OXAMI L4 ; 6 = INVALID | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
861 | HMI SW version | 1 | [5 empty] | SW version | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
862 | HMI SW subversion | 1 | [5 empty] | SW sub version | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
863 | HMI SW CRC Low | 1 | [6 empty] | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
864 | HMI SW CRC High | 1 | [6 empty] | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
900 | HMI informations 2 | 20 | [10 empty] | X | X | X | X |  |  |  |  | 2054 | 4054 | 32 | 0x0083 | 0x20 | 0x0020 | [5 empty] | 20 | 16
900 | HMI Serial number | 8 | [5 empty] | 16 ASCII characters S/N | - | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
930 | Voltage Unbalance / Unit Configuration 3 | 3 | [10 empty] | X | X | X | X |  |  |  |  | 2057 | 4057 | 26 | 0x007D | 0x1A | 0x001A | [5 empty] | 3 | 16
930 | Unbalance Drop-out | 1 |  |  |  |  | 5 ÷ 30 | 5…30% Un | % | 1 | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
931 | Unbalance Pick-up | 1 |  |  |  |  | 3 ÷ 28 | 3…28% Un | % | 1 | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2
932 | Unit Configuration 3 | 1 | B |  |  |  | Bitfield |  | - | - | - |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1
| NOT USED |  | 0 | [7 empty] | BOOL | [18 empty] | RW | S
| NOT USED |  | 1 | [7 empty] | BOOL | [18 empty] | RrWr
| NOT USED |  | 2 | [7 empty] | BOOL | [18 empty] | RW | S
| NOT USED |  | 3 | [7 empty] | BOOL | [18 empty] | RrWr
| NOT USED |  | 4 | [7 empty] | BOOL
| NOT USED |  | 5 | [7 empty] | BOOL
| NOT USED |  | 6 | [7 empty] | BOOL
| NOT USED |  | 7 | [7 empty] | BOOL
| NOT USED |  | 8 | [7 empty] | BOOL
| NOT USED |  | 9 | [7 empty] | BOOL
| NOT USED |  | 10 | [7 empty] | BOOL
| NOT USED |  | 11 | [7 empty] | BOOL | [18 empty] | RrWr
| NOT USED |  | 12 | [7 empty] | BOOL | [18 empty] | RW | S
| NOT USED |  | 13 | [7 empty] | BOOL | [18 empty] | RW | S
| NOT USED |  | 14 | [7 empty] | BOOL | [18 empty] | RW | S
| NOT USED |  | 15 | [7 empty] | BOOL | [18 empty] | RW | S
1000 | Configuration 2.9 / DO Functions | 3 | [10 empty] | X | X | X | X |  |  |  |  | 205E | 405E | 46 | 0x0091 | 0x2E | 0x002E | [5 empty] | 3 | 16
1000 | DO 2 Function | 1 |  |  | X |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
1001 | DO 3 Function | 1 |  |  | X |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
1002 | DO 4 Function | 1 |  |  | X |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
1500 | Advanced Configuration | [10 empty] | RW | X | X | X | X |  |  |  |  | 2150 | 4150 | 80
1520 | Ekip Signalling 2K Outputs | 12 | [10 empty] | X | X | X | X |  |  |  |  | 2160 | 4160 | 81 | 0x00B4 | 0x51 | 0x0051 | [5 empty] | 12 | 16
1521 | Ekip 2K-1 O11 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
1522 | Ekip 2K-1 O11 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
1523 | Ekip 2K-1 O12 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
1524 | Ekip 2K-1 O12 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
1525 | Ekip 2K-2 O21 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
1526 | Ekip 2K-2 O21 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
1527 | Ekip 2K-2 O22 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
1528 | Ekip 2K-2 O22 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
1529 | Ekip 2K-3 O31 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | RW | S
1530 | Ekip 2K-3 O31 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | RW | S
1531 | Ekip 2K-3 O32 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | RW | S
1532 | Ekip 2K-3 O32 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | RW | S
1580 | Ekip Signalling 10K | 40 | [10 empty] | X | X | X | X |  |  |  |  | 2160 | 4160 | 81 | 0x00B4 | 0x51 | 0x0051 | [5 empty] | 40 | 16
1588 | Ekip 10K I1 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
1589 | Ekip 10K I1 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
1590 | Ekip 10K I2 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
1591 | Ekip 10K I2 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
1592 | Ekip 10K I3 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
1593 | Ekip 10K I3 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
1594 | Ekip 10K I4 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
1595 | Ekip 10K I4 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
1596 | Ekip 10K I5 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
1597 | Ekip 10K I5 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | RW | S
1598 | Ekip 10K I6 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | RW | S
1599 | Ekip 10K I6 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | RW | S
1600 | Ekip 10K I7 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | RW | S
1601 | Ekip 10K I7 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | RW | S
1602 | Ekip 10K I8 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | RW | S
1603 | Ekip 10K I8 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | RW | S
1604 | Ekip 10K I9 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | RW | S
1605 | Ekip 10K I9 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 |  |  |  | RW | S
1606 | Ekip 10K I10 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 |  |  |  | RW | S
1607 | Ekip 10K I10 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 20 |  |  | Instance ID = 20 | index = 20 | index = 20 |  |  |  | RW | S
1608 | Ekip 10K O1 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 21 |  |  | Instance ID = 21 | index = 21 | index = 21 |  |  |  | RW | S
1609 | Ekip 10K O1 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 22 |  |  | Instance ID = 22 | index = 22 | index = 22 |  |  |  | RW | S
1610 | Ekip 10K O2 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 23 |  |  | Instance ID = 23 | index = 23 | index = 23 |  |  |  | RW | S
1611 | Ekip 10K O2 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 |  |  |  | RW | S
1612 | Ekip 10K O3 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 25 |  |  | Instance ID = 25 | index = 25 | index = 25 |  |  |  | RW | S
1613 | Ekip 10K O3 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 26 |  |  | Instance ID = 26 | index = 26 | index = 26 |  |  |  | RW | S
1614 | Ekip 10K O4 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 27 |  |  | Instance ID = 27 | index = 27 | index = 27 |  |  |  | RW | S
1615 | Ekip 10K O4 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 28 |  |  | Instance ID = 28 | index = 28 | index = 28 |  |  |  | RW | S
1616 | Ekip 10K O5 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 29 |  |  | Instance ID = 29 | index = 29 | index = 29 |  |  |  | RW | S
1617 | Ekip 10K O5 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 30 |  |  | Instance ID = 30 | index = 30 | index = 30 |  |  |  | RW | S
1618 | Ekip 10K O6 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 31 |  |  | Instance ID = 31 | index = 31 | index = 31 |  |  |  | RW | S
1619 | Ekip 10K O6 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 32 |  |  | Instance ID = 32 | index = 32 | index = 32 |  |  |  | RW | S
1620 | Ekip 10K O7 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 33 |  |  | Instance ID = 33 | index = 33 | index = 33 |  |  |  | RW | S
1621 | Ekip 10K O7 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 34 |  |  | Instance ID = 34 | index = 34 | index = 34 |  |  |  | RW | S
1622 | Ekip 10K O8 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 35 |  |  | Instance ID = 35 | index = 35 | index = 35 |  |  |  | RW | S
1623 | Ekip 10K O8 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 36 |  |  | Instance ID = 36 | index = 36 | index = 36 |  |  |  | RW | S
1624 | Ekip 10K O9 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 37 |  |  | Instance ID = 37 | index = 37 | index = 37 |  |  |  | RW | S
1625 | Ekip 10K O9 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 38 |  |  | Instance ID = 38 | index = 38 | index = 38 |  |  |  | RW | S
1626 | Ekip 10K O10 Function | 1 |  |  |  |  | 0 ÷ 18 | Digital Output Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 39 |  |  | Instance ID = 39 | index = 39 | index = 39 |  |  |  | RW | S
1627 | Ekip 10K O10 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 40 |  |  | Instance ID = 40 | index = 40 | index = 40 |  |  |  | RW | S
1660 | Ekip Signalling 2K Inputs | 12 | [10 empty] | X | X | X | X |  |  |  |  | 2191 | 4191 | 85 | 0x00B8 | 0x55 | 0x0055 | [5 empty] | 12 | 16
1660 | Ekip 2K-1 I11 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
1661 | Ekip 2K-1 I11 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
1662 | Ekip 2K-1 I12 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
1663 | Ekip 2K-1 I12 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
1664 | Ekip 2K-2 I21 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
1665 | Ekip 2K-2 I21 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | RW | S
1666 | Ekip 2K-2 I22 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | RW | S
1667 | Ekip 2K-2 I22 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | RW | S
1668 | Ekip 2K-3 I31 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | RW | S
1669 | Ekip 2K-3 I31 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | RW | S
1670 | Ekip 2K-3 I32 Function | 1 |  |  |  |  | 0 ÷ 26 | Digital Input Functions | - | - | U16 |  | X | X | X | X |  |  |  |  | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | RW | S
1671 | Ekip 2K-3 I32 Contact Type | 1 |  |  |  |  | 0 ÷ 1 | 0 = NC, 1 = NO | - | - | U16 |  | X | X | X | X |  |  |  |  | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | RW | S
3500 | Event Log | 1000 | [9 empty] | R |  | X | [6 empty] | 2220 |  | 88 | 0x00BB | 0x58 | 0x0058 | [5 empty] | 200 | DOMAIN
3500 | Event Log 1 (newest) | 4 | [11 empty] | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
3500 | Event type | 1 |  |  |  |  | 0 ÷ 65535 step 1 | Tab Events | - | - | E16 |  |  | X | [15 empty] | R | S
3501 | Time stamp seconds low | 1 |  |  |  |  | 0 ÷ 65535 step 1 | Seconds from 31 Dec 1999; 0 <=> 00:00:00.000 31 dec 1999 | s | 1 | U16 |  |  | X | [15 empty] | R | S
3502 | Time stamp seconds high | 1 |  |  |  |  | 0 ÷ 65535 step 1 |  | s | 1 | U16 |  |  | X | [15 empty] | R | S
3503 | Time stamp milliseconds | 1 |  |  |  |  | 0 ÷ 999 step 1 |  | ms | 1 | U16 |  |  | X | [15 empty] | R | S
3504 | Event Log 2 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
3508 | Event Log 3 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | S
3512 | Event Log 4 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | S
3516 | Event Log 5 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | S
3520 | Event Log 6 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | S
3524 | Event Log 7 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | R | S
3528 | Event Log 8 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 8 |  |  | Instance ID = 8 | index = 8 | index = 8 |  |  |  | R | S
3532 | Event Log 9 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 9 |  |  | Instance ID = 9 | index = 9 | index = 9 |  |  |  | R | S
3536 | Event Log 10 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
3540 | Event Log 11 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
3544 | Event Log 12 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
3548 | Event Log 13 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
3552 | Event Log 14 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
3556 | Event Log 15 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
3560 | Event Log 16 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | R | S
3564 | Event Log 17 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | R | S
3568 | Event Log 18 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 |  |  |  | R | S
…
Event Log 199
| Event Log 200 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | … |  |  | Instance ID = … | … | … |  |  |  | R | S
…
4496 | Event Log 250 | 4 | [5 empty] | See Event Log 1 | [5 empty] | X | [6 empty] | 250 |  |  | Instance ID = 250 | index = 250 | index = 250 |  |  |  | R | S
5000 | External Modules Parameters | [10 empty] | RW | X | X | X | X
5000 | Ekip COM Modbus RS-485 | 4 | [10 empty] | X | X | X | X |  |  |  |  | 2300 | 4300 | 94 | 0x0300 | 0x5E | 0x005E | [5 empty] | 4 | 16
5000 | Slave Address | 1 |  |  |  |  | 1..247 | Default = 247 |  |  | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5001 | Baud Rate | 1 |  |  |  |  | 0=9600 baud, 1=19200 baud, 2=38400 baud | Default = 19200 |  |  | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5002 | Protocol Type | 1 |  |  |  |  | 0=E81, 1=O81, 2=N82, 3=N81 | Default = E81 |  |  | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5003 | Flags | 1 | B |  |  |  |  | Device specific configurations flags |  |  | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Slave or Master selection bit |  | 0 |  |  |  | 0 = Modbus Slave ; 1 = Modbus Master | Changes device role from Slave to Master on Modbus RS-485 bus |  |  | BOOL
| NOT USED |  | 1 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5010 | Ekip COM Modbus RS-485 Redundant (installed) | 4 | [10 empty] | X | X | X | X |  |  |  |  | 2310 | 4310 | 95 | 0x0301 | 0x5F | 0x005F | [5 empty] | 4 | 16
5010 | Slave Address | 1 |  |  |  |  | 1..247 | Default = 246 |  |  | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5011 | Baud Rate | 1 |  |  |  |  | 0=9600 baud, 1=19200 baud, 2=38400 baud | Default = 19200 |  |  | U16 |  | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5012 | Protocol Type | 1 |  |  |  |  | 0=E81, 1=O81, 2=N82, 3=N81 | Default = E81 |  |  | U16 |  | X | X | X | X |  |  |  |  | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5013 | Flags | 1 | B |  |  |  |  | Device specific configurations flags |  |  | U16 |  | X | X | X | X |  |  |  |  | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Slave or Master selection bit |  | 0 |  |  |  | 0 = Modbus Slave ; 1 = Modbus Master | Changes device role from Slave to Master on Modbus RS-485 bus |  |  | BOOL
| NOT USED |  | 1 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 2 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  |  | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  |  | NOT USED |  |  | BOOL
5025 | Ekip COM Modbus TCP | 10 | [10 empty] | X | X | X | X |  |  |  |  | 2301 | 4301 | 96 | 0x0302 | 0x60 | 0x0060 | [5 empty] | 5 | 32
5025 | Static IP address | 2 | [5 empty] | Module IP address (if Static IP addess is used) (Note b) |  |  | U32 | [9 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5027 | Static IP mask | 2 | [5 empty] | Module IP mask (if Static IP addess is used) (Note b) |  |  | U32 | [9 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5029 | Static IP gateway address | 2 | [5 empty] | Module IP gateway (if Static IP addess is used) (Note b) |  |  | U32 | [9 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5031 | Flags | 2 | B |  |  |  |  | (Note b) |  |  | U32 | [9 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Use Static IP |  | 0 |  |  |  | 0 = Don't use static address ; 1 = Latched | Force static IP address |  |  | BOOL
| Enable IEEE 1588 |  | 1 |  |  |  | 0 = disable ; 1 = enable | Enable IEEE 1588 Time Synchronization |  |  | BOOL
| IEEE 1588 master role |  | 2 |  |  |  | 0 = disable ; 1 = enable | IEEE 1588 Master Role |  |  | BOOL
| Modbus TCP |  | 3 |  |  |  | 1 = Ekip COM Modbus/TCP, 0 not used | Transform the module into a Modbus/TCP server and disable HTTP Server |  |  | BOOL
| Disable Gratuitous ARP |  | 4 |  |  |  | 0 = gratuitous ARP enabled ; 1 = gratuitous ARP disabled | Gratuitous ARP management (device heartbeat on network) |  |  | BOOL
| Password required |  | 5 |  |  |  | 0 = password not required; 1 = password required | Password required for Modbus protocol access |  |  | BOOL
| Modbus TCP Client Enable |  | 6 |  |  |  | 0 = Server only; 1 = Client and Server | Enables Modbus TCP Client services for Ekip Com Hub |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| Enable SNTP |  | 8 |  |  |  | 0 = disable ; 1 = enable | Enable SNTP Time Synchronization |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Delay Mechanism |  | 15 |  |  |  | 0 = End-to-End (E2E); 1 = Peer-to-Peer (P2P) | Switch between two delay mechanisms supported by IEEE1588 standard, more generic (E2E) more optimized (P2P) |  |  | BOOL
| NOT USED |  | 16 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 17 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 18 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 19 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 20 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 21 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 22 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 23 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 24 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 25 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 26 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 27 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 28 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 29 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 30 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 31 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5033 | SNTP Server | 2 | [5 empty] | SNTP Server IP address |  |  | U32 | [9 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
5037 | Ekip COM Modbus TCP Redundant (installed) | 10 | [10 empty] | X | X | X | X |  |  |  |  | 2311 | 4311 | 97 | 0x0303 | 0x61 | 0x0061 | [5 empty] | 5 | 32
5037 | Static IP address | 2 | [5 empty] | Module IP address (if Static IP addess is used) |  |  | U32 | [9 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5039 | Static IP mask | 2 | [5 empty] | Module IP mask (if Static IP addess is used) |  |  | U32 | [9 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5041 | Static IP gateway address | 2 | [5 empty] | Module IP gateway (if Static IP addess is used) |  |  | U32 | [9 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5043 | Flags | 2 | B | [7 empty] | U32 | [9 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Use Static IP |  | 0 |  |  |  | 0 = Don't use static address ; 1 = Latched | Force static IP address |  |  | BOOL
| Enable IEEE 1588 |  | 1 |  |  |  | 0 = disable ; 1 = enable | Enable IEEE 1588 Time Synchronization |  |  | BOOL
| IEEE 1588 master role |  | 2 |  |  |  | 0 = disable ; 1 = enable | IEEE 1588 Master Role |  |  | BOOL
| Modbus TCP |  | 3 |  |  |  | 0 = Ekip Com HTTP Server; 0 not used | Transform the module into a Modbus/TCP server and disable HTTP Server |  |  | BOOL
| Disable Gratuitous ARP |  | 4 |  |  |  | 0 = gratuitous ARP enabled ; 1 = gratuitous ARP disabled | Gratuitous ARP management (device heartbeat on network) |  |  | BOOL
| Password required |  | 5 |  |  |  | 0 = password not required; 1 = password required | Password required for Modbus protocol access |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Boundary Clock |  | 7 |  |  |  | 0 = Standard master; 1 = Master act as boundary clock | Configures IEEE 1588 Master as boundary clock |  |  | BOOL
| Enable SNTP |  | 8 |  |  |  | 0 = disable ; 1 = enable | Enable SNTP Time Synchronization |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Delay Mechanism |  | 15 |  |  |  | 0 = End-to-End (E2E); 1 = Peer-to-Peer (P2P) | Switch between two delay mechanisms supported by IEEE1588 standard, more generic (E2E) more optimized (P2P) |  |  | BOOL
| NOT USED |  | 16 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 17 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 18 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 19 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 20 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 21 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 22 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 23 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 24 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 25 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 26 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 27 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 28 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 29 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 30 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 31 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5045 | SNTP Server | 2 | [5 empty] | SNTP Server IP address |  |  | U32 | [9 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
5060 | Ekip COM EtherNet/IP™ | 10 | [10 empty] | X | X | X | X |  |  |  |  | 2321 | 4321 | 153 | 0x033B | 0x99 | 0x0099 | [5 empty] | 5 | 32
5060 | Static IP address | 2 | [5 empty] | Module IP address (if Static IP addess is used) |  |  | U32 | [9 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5062 | Static IP mask | 2 | [5 empty] | Module IP mask (if Static IP addess is used) |  |  | U32 | [9 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5064 | Static IP gateway address | 2 | [5 empty] | Module IP gateway (if Static IP addess is used) |  |  | U32 | [9 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5066 | Flags | 2 | B | [7 empty] | U32 | [9 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Use Static IP |  | 0 |  |  |  | 0 = Don't use static address ; 1 = Latched | Force static IP address |  |  | BOOL
| Enable IEEE 1588 |  | 1 |  |  |  | 0 = disable ; 1 = enable | Enable IEEE 1588 Time Synchronization |  |  | BOOL
| IEEE 1588 master role |  | 2 |  |  |  | 0 = disable ; 1 = enable | IEEE 1588 Master Role |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Boundary Clock |  | 7 |  |  |  | 0 = Standard master; 1 = Master act as boundary clock | Configures IEEE 1588 Master as boundary clock |  |  | BOOL
| Enable SNTP |  | 8 |  |  |  | 0 = disable ; 1 = enable | Enable SNTP Time Synchronization |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Delay Mechanism |  | 15 |  |  |  | 0 = End-to-End (E2E); 1 = Peer-to-Peer (P2P) | Switch between two delay mechanisms supported by IEEE1588 standard, more generic (E2E) more optimized (P2P) |  |  | BOOL
| NOT USED |  | 16 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 17 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 18 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 19 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 20 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 21 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 22 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 23 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 24 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 25 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 26 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 27 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 28 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 29 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 30 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 31 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5068 | SNTP Server | 2 | [5 empty] | SNTP Server IP address |  |  | U32 | [9 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
5075 | Ekip COM Profibus | 1 | [10 empty] | X | X | X | X |  |  |  |  | 2303 | 4303 | 99 | 0x0305 | 0x63 | 0x0063 | [5 empty] | 1 | 16
5075 | Slave Address | 1 |  |  |  |  | 1..125 | Default = 2 |  |  | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5078 | Ekip COM Profibus Redundant (installed) | 1 | [10 empty] | X | X | X | X |  |  |  |  | 2313 | 4313 | 100 | 0x0306 | 0x64 | 0x0064 | [5 empty] | 1 | 16
5078 | Slave Address | 1 |  |  |  |  | 1..125 | Default = 3 |  |  | U16 |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5082 | Ekip COM EtherNet/IP™ Redundant (installed) | 10 | [10 empty] | X | X | X | X |  |  |  |  | 2322 | 4322 | 154 | 0x033C | 0x9A | 0x009A | [5 empty] | 5 | 32
5082 | Static IP address | 2 | [5 empty] | Module IP address (if Static IP addess is used) |  |  | U32 | [9 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5084 | Static IP mask | 2 | [5 empty] | Module IP mask (if Static IP addess is used) |  |  | U32 | [9 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5086 | Static IP gateway address | 2 | [5 empty] | Module IP gateway (if Static IP addess is used) |  |  | U32 | [9 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5088 | Flags | 2 | B | [7 empty] | U32 | [9 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Use Static IP |  | 0 |  |  |  | 0 = Don't use static address ; 1 = Latched | Force static IP address |  |  | BOOL
| Enable IEEE 1588 |  | 1 |  |  |  | 0 = disable ; 1 = enable | Enable IEEE 1588 Time Synchronization |  |  | BOOL
| IEEE 1588 master role |  | 2 |  |  |  | 0 = disable ; 1 = enable | IEEE 1588 Master Role |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Boundary Clock |  | 7 |  |  |  | 0 = Standard master; 1 = Master act as boundary clock | Configures IEEE 1588 Master as boundary clock |  |  | BOOL
| Enable SNTP |  | 8 |  |  |  | 0 = disable ; 1 = enable | Enable SNTP Time Synchronization |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| IEEE 1588 Delay Mechanism |  | 15 |  |  |  | 0 = End-to-End (E2E); 1 = Peer-to-Peer (P2P) | Switch between two delay mechanisms supported by IEEE1588 standard, more generic (E2E) more optimized (P2P) |  |  | BOOL
| NOT USED |  | 16 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 17 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 18 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 19 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 20 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 21 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 22 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 23 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 24 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 25 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 26 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 27 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 28 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 29 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 30 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 31 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5090 | SNTP Server | 2 | [5 empty] | SNTP Server IP address |  |  | U32 | [9 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
5230 | Ekip COM DeviceNet™ | 2 | [10 empty] | X | X | X | X |  |  |  |  | 2309 | 4309 | 105 | 0x030B | 0x69 | 0x0069 |  |  |  | RW |  | 2 | 16
5230 | MAC ID | 1 | [5 empty] | DeviceNet ™ MAC ID (module address) |  |  |  |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW
5231 | Flags | 1 | B | [9 empty] | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW
| Baud Rate |  | 0 |  |  |  | 0=125 kbit/s; 1=250 kbit/s; 2=500kbit/s | Baud Rate on DeviceNet ™ communication bus |  |  | BOOL
|  |  | 1 | [7 empty] | BOOL
| 16-bit CLASS ID |  | 2 |  |  |  | 0=8 bit CLASS ID; 1=16 bit CLASS ID | CLASS ID width |  |  | BOOL
| Autorecover on DeviceNet ™ communication protocol |  | 3 |  |  |  | 0=Normal DeviceNet ™ behavior; 1=Auto-exit from Bus-Off condition | Bus-off autoexit behaviour |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5235 | Ekip COM Devicenet™ Redundant (installed) | 2 | [10 empty] | X | X | X | X |  |  |  |  | 2319 | 4319 | 106 | 0x030C | 0x6A | 0x006A |  |  |  | RW |  | 2 | 16
5235 | MAC ID | 1 | [5 empty] | DeviceNet ™MAC ID (module address) |  |  |  |  | X | X | X | X |  |  |  |  | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW
5236 | Flags | 1 | B | [9 empty] | X | X | X | X |  |  |  |  | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW
| Baud Rate |  | 0 |  |  |  | 0=125 kbit/s; 1=250 kbit/s; 2=500kbit/s | Baud Rate on DeviceNet ™ communication bus |  |  | BOOL
|  |  | 1 | [7 empty] | BOOL
| 16-bit CLASS ID |  | 2 |  |  |  | 0=8 bit CLASS ID; 1=16 bit CLASS ID | CLASS ID width |  |  | BOOL
| Autorecover on DeviceNet ™ communication protocol |  | 3 |  |  |  | 0=Normal DeviceNet ™ behavior; 1=Auto-exit from Bus-Off condition | Bus-off autoexit behaviour |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5380 | Ekip Com Hub | 10 | [10 empty] | X | X | X | X |  |  |  |  | 2329 | 4329 | 318 | 0x03E0 | Not Available | 0x013E | [5 empty] | 5 | 32
5380 | Static IP address | 2 | [5 empty] | Module IP address (if Static IP addess is used) (Note b) |  |  | U32 | [9 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | RW | S
5382 | Static IP mask | 2 | [5 empty] | Module IP mask (if Static IP addess is used) (Note b) |  |  | U32 | [9 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | RW | S
5384 | Static IP gateway address | 2 | [5 empty] | Module IP gateway (if Static IP addess is used) (Note b) |  |  | U32 | [9 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | RW | S
5386 | Flags | 2 | B |  |  |  |  | (Note b) |  |  | U32 | [9 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | RW | S
| Use Static IP |  | 0 |  |  |  | 0 = Don't use static address ; 1 = Latched | Force static IP address |  |  | BOOL
| NOT USED |  | 1 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| Modbus TCP |  | 3 |  |  |  | 0 = Ekip Com HTTP Server; 1 = Ekip COM Modbus/TCP | Transform the module into a Modbus/TCP server and disable HTTP Server |  |  | BOOL
| Disable Gratuitous ARP |  | 4 |  |  |  | 0 = gratuitous ARP enabled ; 1 = gratuitous ARP disabled | Gratuitous ARP management (device heartbeat on network) |  |  | BOOL
| RESERVED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| Enable IOT |  | 6 |  |  |  | 0 = IOT disabled ; 1 = IOT enabled | Enable IOT operations (Data harvesting, logging and expedition) |  |  | BOOL
| Enable Server Diagnostics |  | 7 |  |  |  | 0 = disable ; 1 = enable | Enable diagnostics to be embedded in server communication |  |  | BOOL
| Enable CRL |  | 8 |  |  |  | 0 = disable ; 1 = enable | Enable the use of CRL |  |  | BOOL
| Compact JSON format |  | 9 |  |  |  | 0 = disable ; 1 = enable | Select a compact format for the JSON data |  |  | BOOL
| Enable clock update hardening |  | 10 |  |  |  | 0 = disable ; 1 = enable | Enable the check of clock update at NTP event compared to the UTC from API Device |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| SNTP internal server |  | 12 |  |  |  | 0 = external; 1 = internal | Location of SNTP server: external or internal compared to the LAN of the module |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| Enable SNTP |  | 15 |  |  |  | 0 = disable ; 1 = enable | Enable SNTP Time Synchronization |  |  | BOOL
| NOT USED |  | 16 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 17 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 18 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 19 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 20 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 21 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 22 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 23 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 24 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 25 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 26 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 27 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 28 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 29 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 30 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 31 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5388 | SNTP Server | 2 | [5 empty] | SNTP Server IP address |  |  | U32 | [9 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | RW | S
5400 | External Modules Information | [10 empty] | R |  | X | [6 empty] | 2350 |  | 109 | 0x030F
5400 | Ekip COM DeviceNet ™ Redundant | 12 | [11 empty] | X | [6 empty] | 2370 |  | 109 | 0x030F | 0x6D | 0x006D | [5 empty] | 12 | 16
5400 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5401 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5409 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5410 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5411 | Status | 1 | [5 empty] | Module Status ( Vnetwork, DeviceNet ™ status, alarms ) |  |  | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Network Power |  | 2 |  |  |  | 0=Off; 1=On | Network Power status |  |  | BOOL
| Network Access State Machine |  | 3 |  |  |  | 1= Sending DID, 2= Waiting DID, 3= On line, 4= Communication Fault | Network Access state machine status |  |  | BOOL
|  |  | 4 | [7 empty] | BOOL
| Master MAC ID |  | 5 |  |  |  | Master MAC ID 0xFF = Not Owned | MAC ID of the Master owning the device |  |  | BOOL
|  |  | 6 | [7 empty] | BOOL
|  |  | 7 | [7 empty] | BOOL
|  |  | 8 | [7 empty] | BOOL
|  |  | 9 | [7 empty] | BOOL
|  |  | 10 | [7 empty] | BOOL
|  |  | 11 | [7 empty] | BOOL
|  |  | 12 | [7 empty] | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5414 | Ekip COM EtherNet/IP™ (32 bit) | 8 | [11 empty] | X | [6 empty] | 237A |  | 157 | 0x033F | 0x9D | 0x009D | [5 empty] | 4 | 32
5414 | Module IP address | 2 |  |  |  |  | IPv4 | IP address |  |  | U32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
5416 | Module Network mask | 2 |  |  |  |  | IPv4 | Network mask |  |  | U32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | V
5418 | Module gateway address | 2 |  |  |  |  | IPv4 | Gateway address |  |  | U32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | V
5420 | IEEE1588 Grand Master Clock IP address | 2 |  |  |  |  | IPv4 | Grand Master Clock address |  |  | U32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | V
5425 | Ekip COM Profinet Redundant | 15 | [11 empty] | X | [6 empty] | 2371 |  | 110 | 0x0310 | 0x6E | 0x006E | [5 empty] | 15 | 16
5425 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5426 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5434 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5437 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
5438 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
5439 | Module Status | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| SNTP Server Error |  | 3 |  |  |  | 0=No SNTP error; 1=SNTP server is not responding | SNTP Synchronisation error |  |  | BOOL
| SNTP Server Not Synchronized |  | 4 |  |  |  | 0=No SNTP error; 1=SNTP synchronisation error | SNTP Synchronisation status |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5450 | Ekip COM Modbus RS-485 Redundant | 12 | [11 empty] | X | [6 empty] | 2372 |  | 111 | 0x0311 | 0x6F | 0x006F | [5 empty] | 12 | 16
5450 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5451 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5459 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5460 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5461 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5464 | Ekip COM EtherNet/IP™ Redundant (32 bit) | 8 | [11 empty] | X | [6 empty] | 237B |  | 158 | 0x0340 | 0x9E | 0x009E | [5 empty] | 4 | 32
5464 | Module IP address | 2 |  |  |  |  | IPv4 | Module IPv4 address |  |  | U32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
5466 | Module Network mask | 2 |  |  |  |  | IPv4 | Network mask |  |  | U32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | V
5468 | Module gateway address | 2 |  |  |  |  | IPv4 | Gateway address |  |  | U32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | V
5470 | IEEE1588 Grand Master Clock IP address | 2 |  |  |  |  | IPv4 | Grand Master Clock address |  |  | U32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | V
5475 | Ekip COM Modbus TCP Redundant | 15 | [11 empty] | X | [6 empty] | 2373 |  | 112 | 0x0312 | 0x70 | 0x0070 | [5 empty] | 15 | 16
5475 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5476 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5484 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5487 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
5488 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
5489 | Module Status | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| SNTP Server Error |  | 3 |  |  |  | 0=No SNTP error; 1=SNTP server is not responding | SNTP Synchronisation error |  |  | BOOL
| SNTP Server Not Synchronized |  | 4 |  |  |  | 0=No SNTP error; 1=SNTP synchronisation error | SNTP Synchronisation status |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5500 | Ekip COM Modbus TCP Redundant (32 bit) | 14 | [11 empty] | X | [6 empty] | 2374 |  | 113 | 0x0313 | 0x71 | 0x0071 | [5 empty] | 7 | 32
5500 | Module IP address | 2 |  |  |  |  | IPv4 | IP address |  |  | U32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
5502 | Module Network mask | 2 |  |  |  |  | IPv4 | Network mask |  |  | U32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | V
5504 | Module gateway address | 2 |  |  |  |  | IPv4 | Gateway address |  |  | U32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | V
5506 | Modbus TCP Client n.1 | 2 |  |  |  |  | IPv4 | IP address of 1st connected client |  |  | U32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | V
5508 | Modbus TCP Client n.2 | 2 |  |  |  |  | IPv4 | IP address of 2nd connected client |  |  | U32 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | V
5510 | Modbus TCP Client n.3 | 2 |  |  |  |  | IPv4 | IP address of 3rd connected client |  |  | U32 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | V
5512 | IEEE1588 Grand Master Clock IP address | 2 |  |  |  |  | IPv4 | Grand Master Clock address |  |  | U32 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | R | V
5525 | Ekip COM Profibus Redundant | 12 | [11 empty] | X | [6 empty] | 2375 |  | 114 | 0x0314 | 0x72 | 0x0072 | [5 empty] | 12 | 16
5525 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5526 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5534 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5535 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5536 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 0 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 1 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 2 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 3 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 4 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 5 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 6 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 7 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 8 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 9 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 10 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 11 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 12 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 13 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 14 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
| NOT USED |  | 15 |  |  |  |  | NOT USED |  |  | BOOL | [18 empty] | R | V
5600 | Ekip COM Modbus RS-485 | 12 | [11 empty] | X | [6 empty] | 2350 |  | 117 | 0x0317 | 0x75 | 0x0075 | [5 empty] | 12 | 16
5600 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5601 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5609 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5610 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5611 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5625 | Ekip COM Modbus TCP | 15 | [11 empty] | X | [6 empty] | 2351 |  | 118 | 0x0318 | 0x76 | 0x0076 | [5 empty] | 15 | 16
5625 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5626 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5634 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5637 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
5638 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
5639 | Module Status | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| SNTP Server Error |  | 3 |  |  |  | 0=No SNTP error; 1=SNTP server is not responding | SNTP Synchronisation error |  |  | BOOL
| SNTP Server Not Synchronized |  | 4 |  |  |  | 0=No SNTP error; 1=SNTP synchronisation error | SNTP Synchronisation status |  |  | BOOL
| Other IEEE1588 Master detected |  | 5 |  |  |  | 0= Slave or PTP Master Active, 1 = PTP Master but Passive | Set to one when a better Grand Master clock is in the network |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5640 | Ekip COM Modbus TCP (32 bit) | 14 | [11 empty] | X | [6 empty] | 2352 |  | 119 | 0x0319 | 0x77 | 0x0077 | [5 empty] | 7 | 32
5640 | Module IP address | 2 |  |  |  |  | IPv4 | IP address |  |  | U32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
5642 | Module Network mask | 2 |  |  |  |  | IPv4 | Network mask |  |  | U32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | V
5644 | Module gateway address | 2 |  |  |  |  | IPv4 | Gateway address |  |  | U32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | V
5646 | Modbus TCP Client n.1 | 2 |  |  |  |  | IPv4 | Pointer to connection block ( 0 = No connection ) |  |  | U32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | V
5648 | Modbus TCP Client n.2 | 2 |  |  |  |  | IPv4 | Pointer to connection block ( 0 = No connection ) |  |  | U32 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | V
5650 | Modbus TCP Client n.3 | 2 |  |  |  |  | IPv4 | Pointer to connection block ( 0 = No connection ) |  |  | U32 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | V
5652 | IEEE1588 Grand Master Clock IP address | 2 |  |  |  |  | IPv4 | Grand Master Clock address |  |  | U32 |  |  | X | [6 empty] | 7 |  |  | Instance ID = 7 | index = 7 | index = 7 |  |  |  | R | V
5675 | Ekip COM Profibus | 12 | [11 empty] | X | [6 empty] | 2353 |  | 120 | 0x031A | 0x78 | 0x0078 | [5 empty] | 12 | 16
5675 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5676 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5684 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5685 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5686 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5725 | Ekip 2K-1 | 12 | [11 empty] | X | [6 empty] | 2355 |  | 122 | 0x031C | 0x7A | 0x007A | [5 empty] | 12 | 16
5725 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5726 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5734 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5735 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5736 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5750 | Ekip 2K-2 | 12 | [11 empty] | X | [6 empty] | 2356 |  | 123 | 0x031D | 0x7B | 0x007B | [5 empty] | 12 | 16
5750 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5751 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5759 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5760 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5761 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5762 | Ekip 2K-3 | 12 | [11 empty] | X | [6 empty] | 235D |  | 124 | 0x031E | 0x7C | 0x007C | [5 empty] | 12 | 16
5762 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5763 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5771 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5772 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5773 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5818 | Ekip COM EtherNet/IP™ | 15 | [11 empty] | X | [6 empty] | 2376 |  | 161 | 0x0343 | 0xA1 | 0x00A1 | [5 empty] | 15 | 16
5818 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5819 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5827 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5830 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
5831 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
5832 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| SNTP Server Error |  | 3 |  |  |  | 0=No SNTP error; 1=SNTP server is not responding | SNTP Synchronisation error |  |  | BOOL
| SNTP Server Not Synchronized |  | 4 |  |  |  | 0=No SNTP error; 1=SNTP synchronisation error | SNTP Synchronisation status |  |  | BOOL
| Other IEEE1588 Master detected |  | 5 |  |  |  | 0= Slave or PTP Master Active, 1 = PTP Master but Passive | Set to one when a better Grand Master clock is in the network |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5834 | Ekip COM EtherNet/IP™ Redundant | 15 | [11 empty] | X | [6 empty] | 2377 |  | 162 | 0x0344 | 0xA2 | 0x00A2 | [5 empty] | 15 | 16
5834 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5835 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5843 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5846 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
5847 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
5848 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| SNTP Server Error |  | 3 |  |  |  | 0=No SNTP error; 1=SNTP server is not responding | SNTP Synchronisation error |  |  | BOOL
| SNTP Server Not Synchronized |  | 4 |  |  |  | 0=No SNTP error; 1=SNTP synchronisation error | SNTP Synchronisation status |  |  | BOOL
| Other IEEE1588 Master detected |  | 5 |  |  |  | 0= Slave or PTP Master Active, 1 = PTP Master but Passive | Set to one when a better Grand Master clock is in the network |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5850 | Ekip COM DeviceNet ™ | 12 | [11 empty] | X | [6 empty] | 235B |  | 128 | 0x0322 | 0x80 | 0x0080 | [5 empty] | 12 | 16
5850 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5851 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5859 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5860 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5861 | Status | 1 | B |  |  |  |  | Module Status ( Vnetwork, DeviceNet ™ status, alarms ) |  |  | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Network Power |  | 2 |  |  |  | 0=Off; 1=On | Network Power status |  |  | BOOL
| Network Access State Machine |  | 3 |  |  |  | 1= Sending DID, 2= Waiting DID, 3= On line, 4= Communication Fault | Network Access state machine status |  |  | BOOL
|  |  | 4 | [7 empty] | BOOL
| Master MAC ID |  | 5 |  |  |  | Master MAC ID 0xFF = Not Owned | MAC ID of the Master owning the device |  |  | BOOL
|  |  | 6 | [7 empty] | BOOL
|  |  | 7 | [7 empty] | BOOL
|  |  | 8 | [7 empty] | BOOL
|  |  | 9 | [7 empty] | BOOL
|  |  | 10 | [7 empty] | BOOL
|  |  | 11 | [7 empty] | BOOL
|  |  | 12 | [7 empty] | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5875 | Ekip COM Profinet | 15 | [11 empty] | X | [6 empty] | 235C |  | 129 | 0x0323 | 0x81 | 0x0081 | [5 empty] | 15 | 16
5875 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5876 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5884 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5887 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
5888 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
5889 | Module Status | 1 | B | [7 empty] | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
5900 | Ekip 10K-1 | 12 | [11 empty] | X | [6 empty] | 2360 |  | 130 | 0x0324 | 0x82 | 0x0082 | [5 empty] | 12 | 16
5900 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
5901 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
5909 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
5910 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 11 |  |  | Instance ID = 11 | index = 11 | index = 11 |  |  |  | R | S
5911 | Module Status | 1 | [8 empty] | U16 |  |  | X | [6 empty] | 12 |  |  | Instance ID = 12 | index = 12 | index = 12 |  |  |  | R | S
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| NOT USED |  | 2 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 3 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 4 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 5 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 6 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 7 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 8 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 9 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 10 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 11 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 12 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 13 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 14 |  |  |  | Always 0 | NOT USED |  |  | BOOL
| NOT USED |  | 15 |  |  |  | Always 0 | NOT USED |  |  | BOOL
6990 | Ekip Com Hub (32 bit) | 12 | [11 empty] | X | [6 empty] | 2386 |  | 319 | 0x03E1 | Not Available | 0x013F | [5 empty] | 6 | 32
6990 | Module IP address | 2 |  |  |  |  | IPv4 | IP address |  |  | U32 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | V
6992 | Module Network mask | 2 |  |  |  |  | IPv4 | Network mask |  |  | U32 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | V
6994 | Module gateway address | 2 |  |  |  |  | IPv4 | Gateway address |  |  | U32 |  |  | X | [6 empty] | 3 |  |  | Instance ID = 3 | index = 3 | index = 3 |  |  |  | R | V
6996 | Modbus TCP Client n.1 | 2 |  |  |  |  | IPv4 | Pointer to connection block ( 0 = No connection ) |  |  | U32 |  |  | X | [6 empty] | 4 |  |  | Instance ID = 4 | index = 4 | index = 4 |  |  |  | R | V
6998 | Modbus TCP Client n.2 | 2 |  |  |  |  | IPv4 | Pointer to connection block ( 0 = No connection ) |  |  | U32 |  |  | X | [6 empty] | 5 |  |  | Instance ID = 5 | index = 5 | index = 5 |  |  |  | R | V
7000 | Modbus TCP Client n.3 | 2 |  |  |  |  | IPv4 | Pointer to connection block ( 0 = No connection ) |  |  | U32 |  |  | X | [6 empty] | 6 |  |  | Instance ID = 6 | index = 6 | index = 6 |  |  |  | R | V
7010 | Ekip Com Hub | 15 | [11 empty] | X | [6 empty] | 2387 |  | 320 | 0x03E2 | Not Available | 0x0140 | [5 empty] | 15 | 16
7010 | SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module SW version |  |  | U16 |  |  | X | [6 empty] | 1 |  |  | Instance ID = 1 | index = 1 | index = 1 |  |  |  | R | S
7011 | Module serial number | 8 |  |  |  |  | 16 ASCII characters CB S/N | Module Serial number |  |  | U16 |  |  | X | [6 empty] | 2 |  |  | Instance ID = 2 | index = 2 | index = 2 |  |  |  | R | S
7019 | MAC Address | 3 |  |  |  |  | ac:d3:64:xx:xx:xx | Module MAC address |  |  | U16 |  |  | X | [6 empty] | 10 |  |  | Instance ID = 10 | index = 10 | index = 10 |  |  |  | R | S
7022 | Boot SW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Boot SW version |  |  | U16 |  |  | X | [6 empty] | 13 |  |  | Instance ID = 13 | index = 13 | index = 13 |  |  |  | R | S
7023 | HW Version | 1 |  |  |  |  | MAJOR.minor (MSB.LSB) | Module HW version |  |  | U16 |  |  | X | [6 empty] | 14 |  |  | Instance ID = 14 | index = 14 | index = 14 |  |  |  | R | S
7024 | Module Status | 1 | [5 empty] | Module Status |  |  | U16 |  |  | X | [6 empty] | 15 |  |  | Instance ID = 15 | index = 15 | index = 15 |  |  |  | R | V
| CRC Error |  | 0 |  |  |  | 0=CRC ok; 1=CRC error | CRC error condition (calculated for the application program portion) |  |  | BOOL
| CRC Calculated |  | 1 |  |  |  | 0=CRC calculation in progress; 1=1st calculation done | CRC calculation completed: CRC error field is valid |  |  | BOOL
| Ethernet Link Status Error |  | 2 |  |  |  | 0=Ethernet link established; 1=Ethernet link error | Ethernet Link status |  |  | BOOL
| SNTP Server Error |  | 3 |  |  |  | 0=No SNTP error; 1=SNTP server is not responding | SNTP Synchronisation error |  |  | BOOL
| SNTP Server Not Synchronized |  | 4 |  |  |  | 0=No SNTP error; 1=SNTP synchronisation error | SNTP Synchronisation status |  |  | BOOL
| Connected device communication error |  | 5 |  |  |  | 0=No device error; 1= At least a device presents a communication error | Connected device communication error |  |  | BOOL
| TLS Event Hub Error |  | 6 |  |  |  | 0=No error, 1=TLS connection error, 2=TLS handshake error, | TLS comunication error between Ekip Com Hub and Event Hub Server |  |  | BOOL
|  |  | 7 |  |  |  | 3=TLS application data error |  |  |  | BOOL
| Missing Ekip Link |  | 8 |  |  |  | 0=No error; 1= Required Ekip Link not found | Missing Ekip Link |  |  | BOOL
| Missing Ekip COM Modbus TCP |  | 9 |  |  |  | 0=No error; 1= Required Ekip COM Modbus TCP not found | Missing Ekip COM Modbus TCP |  |  | BOOL
| x.509 Certificates Error (Renew) |  | 10 |  |  |  | 0=No error; 1= Certificates cannot be resolved | x.509 Certificates Error (Renew)) |  |  | BOOL
| x.509 Certificates Error (Data publish) |  | 11 |  |  |  | 0=No error; 1= Certificates cannot be resolved | x.509 Certificates Error (Data publish) |  |  | BOOL
| TLS API Device Error |  | 12 |  |  |  | 0=No error, 1=TLS connection error, 2=TLS handshake error, | TLS comunication error between Ekip Com Hub and API Device Server |  |  | BOOL
|  |  | 13 |  |  |  | 3=TLS application data error |  |  |  | BOOL
| Missing Ekip COM Modbus RS485 |  | 14 |  |  |  | 0=No error; 1= Required Ekip COM Modbus RS485 not found | Missing Ekip COM Modbus RS485 |  |  | BOOL
| Internal Timer Not Synchronized |  | 15 |  |  |  | 0=No SNTP error; 1=Internal timer synchronisation error | Excessive deviation between the internal timer and the reference timer |  |  | BOOL
7025 | Timestamp of Last Log - Seconds (Low) | 1 |  |  |  |  | 0 ÷ 65535 | time = 0 --> 00:00:00.000 31 dec 1999 T min: 00:00:00.000 01 jan 2012 |  |  | U16 |  |  | X | [6 empty] | 16 |  |  | Instance ID = 16 | index = 16 | index = 16 |  |  |  | R | V
7026 | Timestamp of Last Log - Seconds (High) | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  |  | X | [6 empty] | 17 |  |  | Instance ID = 17 | index = 17 | index = 17 |  |  |  | R | V
7027 | Timestamp of Last Upload - Seconds (Low) | 1 |  |  |  |  | 0 ÷ 65535 | time = 0 --> 00:00:00.000 31 dec 1999 T min: 00:00:00.000 01 jan 2012 |  |  | U16 |  |  | X | [6 empty] | 18 |  |  | Instance ID = 18 | index = 18 | index = 18 |  |  |  | R | V
7028 | Timestamp of Last Upload - Seconds (High) | 1 |  |  |  |  | 0 ÷ 65535 |  |  |  | U16 |  |  | X | [6 empty] | 19 |  |  | Instance ID = 19 | index = 19 | index = 19 |  |  |  | R | V
7029 | Parser Error Code | 1 |  |  |  |  | 1 = Configuration File(.csv) not found or corrupted ! 2 = Security file(.txt) not found or corrupted ! 3 = Allocation error ! 4 = Max devices(50) exceeded ! 5 = Too many registers ! 6 = Ethernet module role error ! 7 = Ekip COM Modbus RS - 485 role error ! 8 = Max queries per device exceeded ! 9 = Too many characters inside a line of a file ! 10 = Insufficient heap space for CRL ! 11 = Bad version in the publishing file ! 12 = Bad publisher in the publishing file ! 13 = Bad publish URL in the publishing file ! 14 = Bad publish header append in the publishing file ! 15 = Bad renew URL in the publishing file ! 16 = Bad renew date in the publishing file ! 17 = Bad publish root CA in the publishing file ! 18 = Bad renew root CA in the publishing file ! 19 = Bad publish enabled in the publishing file ! 20 = Bad poll URL in the publishing file ! 21 = Bad poll period in the publishing file ! 22 = Bad FW URL in the publishing file ! 23 = Bad FW available in the publishing file ! 24 = Bad FW version in the publishing file ! 25 = Bad FW hash in the publishing file ! 26 = Bad FW size in the publishing file ! 27 = Bad FW file name in the publishing file ! 28 = Bad CRL URL in the publishing file ! 29 = Bad identification string in the publishing file ! 30 = Bad SNTP server host name in the publishing file ! 31 = Bad SNTP key identifier in the publishing file ! 32 = Bad SNTP key value in the publishing file ! 33 = Bad API header append in the publishing file ! 34 = Bad version in the gathering file ! 35 = Bad upload time in the gathering file ! 36 = Bad routes number in the gathering file ! 37 = Bad route entry in the gathering file ! 38 = Bad device number in the gathering file ! 39 = Bad device name in the gathering file ! 40 = Bad device unit identifier in the gathering file ! 41 = Bad device tags number in the gathering file ! 42 = Bad device tags string in the gathering file ! 43 = Bad device tag data in the gathering file ! 44 = Bad device tag bind in the gathering file ! 45 = Insufficient heap space for the client's certificate ! 46 = Insufficient heap space for the client's key ! 47 = Certificate File(.crt) not found or corrupted ! 48 = key File(.key) not found or corrupted ! | Result of the parsing activity on the configuration and security files. |  |  | U16 |  |  | X | [6 empty] | 20 |  |  | Instance ID = 20 | index = 20 | index = 20 |  |  |  | R | S
7030 | ConfiguredDevices | 1 | [5 empty] | Number of configured devices |  |  | U16 |  |  | X | [6 empty] | 21 |  |  | Instance ID = 21 | index = 21 | index = 21 |  |  |  | R | S
7031 | Configured Sample Period | 1 | [5 empty] | Configured sample period |  |  | U16 |  |  | X | [6 empty] | 22 |  |  | Instance ID = 22 | index = 22 | index = 22 |  |  |  | R | S
7032 | Configured Log Period | 1 | [5 empty] | Configured Log period |  |  | U16 |  |  | X | [6 empty] | 23 |  |  | Instance ID = 23 | index = 23 | index = 23 |  |  |  | R | S
7033 | Configured Upload Period | 1 | [5 empty] | Configured Upload period |  |  | U16 |  |  | X | [6 empty] | 24 |  |  | Instance ID = 24 | index = 24 | index = 24 |  |  |  | R | S
7034 | Measured Sample Time | 1 | [5 empty] | Measured Sample time |  |  | U16 |  |  | X | [6 empty] | 25 |  |  | Instance ID = 25 | index = 25 | index = 25 |  |  |  | R | S
7035 | Max WD call rate | 1 | [5 empty] | Max delay between two consecutive call to WD refresh |  |  | U16 |  |  | X | [6 empty] | 26 |  |  | Instance ID = 26 | index = 26 | index = 26 |  |  |  | R | S
7036 | Misconnected device | 1 | [5 empty] | Device that presented a communication error |  |  | U16 |  |  | X | [6 empty] | 27 |  |  | Instance ID = 27 | index = 27 | index = 27 |  |  |  | R | S
7037 | Misconnection counter | 1 | [5 empty] | Communication error counters |  |  | U16 |  |  | X | [6 empty] | 28 |  |  | Instance ID = 28 | index = 28 | index = 28 |  |  |  | R | S
7038 | Configuration File | 17 |  |  |  |  | 32 ASCII characters configuration file | Name of the configuration file used |  |  | U16 |  |  | X | [6 empty] | 29 |  |  | Instance ID = 29 | index = 29 | index = 29 |  |  |  | R | S
7055 | Security File | 17 |  |  |  |  | 32 ASCII characters configuration file | Name of the security file used |  |  | U16 |  |  | X | [6 empty] | 46 |  |  | Instance ID = 46 | index = 46 | index = 46 |  |  |  | R | S
7072 | Resource occupation | 1 | [5 empty] | Communication error counters |  |  | U16 |  |  | X | [6 empty] | 63 |  |  | Instance ID = 63 | index = 63 | index = 63 |  |  |  | R | S
| Log buffer occupation |  | 0 |  |  |  | 0..100 = RAM occupation percentage | Log buffer occupation |  |  | BOOL
|  |  | 1 | [7 empty] | BOOL
|  |  | 2 | [7 empty] | BOOL
|  |  | 3 | [7 empty] | BOOL
|  |  | 4 | [7 empty] | BOOL
|  |  | 5 | [7 empty] | BOOL
|  |  | 6 | [7 empty] | BOOL
|  |  | 7 | [7 empty] | BOOL
| POST buffer occupation |  | 8 |  |  |  | 0..100 = RAM occupation percentage | POST buffer occupation |  |  | BOOL
|  |  | 9 | [7 empty] | BOOL
|  |  | 10 | [7 empty] | BOOL
|  |  | 11 | [7 empty] | BOOL
|  |  | 12 | [7 empty] | BOOL
|  |  | 13 | [7 empty] | BOOL
|  |  | 14 | [7 empty] | BOOL
|  |  | 15 | [7 empty] | BOOL
7073 | API events (Low) | 1 | [5 empty] | First 32 bits returned from API events (Low) |  |  | U16 |  |  | X | [6 empty] | 64 |  |  | Instance ID = 64 | index = 64 | index = 64 |  |  |  | R | S
7074 | API events (High) | 1 | [5 empty] | First 32 bits returned from API events (High) |  |  | U16 |  |  | X | [6 empty] | 65 |  |  | Instance ID = 65 | index = 65 | index = 65 |  |  |  | R | S
7075 | Module Status 2 | 1 | [5 empty] | Module Status 2 |  |  | U16 |  |  | X | [6 empty] | 66 |  |  | Instance ID = 66 | index = 66 | index = 66 |  |  |  | R | S
| API events response error |  | 0 |  |  |  | 0=response ok; 1=response is corrupted or doens't contain all fields | Condition of the response from API events |  |  | BOOL
| Certificate Revocation List parsing error |  | 1 |  |  |  | 0=CRL ok; 1= CRL cannot be parsed | CRL parsing error |  |  | BOOL
| Routing Table Disable |  | 2 |  |  |  | 0=Enabled; 1=Disabled | Exclusion of the routing table engine. Required for Discovery procedure |  |  | BOOL
| Publish enabled configuration file |  | 3 |  |  |  | 0=Disabled; 1=Enabled | Publish enabled field inside configuration file |  |  | BOOL
| New Firmware Version available and checked |  | 4 |  |  |  | 0=Not Available, 1=Available and checked | A new firmware version is available, ready for the update operation |  |  | BOOL
| Insufficient space in the JSON buffer |  | 5 |  |  |  | 0= sufficient free space in the JSON buffer; 1=insufficient free space in the JSON buffer | Availability of free space in the JSON buffer |  |  | BOOL
| TFTP Port open |  | 6 |  |  |  | 0= TFTP port closed, 1=TFTP port open | TFTP port open provides a TFTP server listening for client connections |  |  | BOOL
| Executable file matching error |  | 7 |  |  |  | 0 = the calculated hash (or size) of executable file matches with the reference hash (or size) | The comparison between the calculated hash (or size) of the executable file |  |  | BOOL
[7 empty] | of the executable file; 1 = the two hashes (or sizes) are different | and the reference hash (or size) of the executable file
| Clock update hardening error |  | 8 |  |  |  | 0=clock update ok; 1= clock update error | Error set when the time from NTP server is much deviated from the time from the API device. In this case the internal clock of the module isn't updated |  |  | BOOL
| Modbus enable |  | 9 |  |  |  | 0=Disabled; 1=Enabled | Enable Modbus TCP server |  |  | BOOL
| Client certificate error |  | 10 |  |  |  | 0=certificate correctly parsed; 1=parse error | Parsing of the certificate own by the module |  |  | BOOL
| Client key error |  | 11 |  |  |  | 0=key correctly parsed; 1=parse error | Parsing of the private key own by the module |  |  | BOOL
| Certificate Revocation List absent error |  | 12 |  |  |  | 0 = CRL is present; 1 = CRL is absent | The CRL is enable, but no file is present |  |  | BOOL
| Unused |  | 13 | [7 empty] | BOOL
| Unused |  | 14 | [7 empty] | BOOL
| Unused |  | 15 | [7 empty] | BOOL
7076 | API UTC (Low) | 1 | [5 empty] | UTC value returned from API events (Low) |  |  | U16 |  |  | X | [6 empty] | 67 |  |  | Instance ID = 67 | index = 67 | index = 67 |  |  |  | R | S
7077 | API UTC (High) | 1 | [5 empty] | UTC value returned from API events (High) |  |  | U16 |  |  | X | [6 empty] | 68 |  |  | Instance ID = 68 | index = 68 | index = 68 |  |  |  | R | S
7078 | Delta UTC (Low) | 1 | [5 empty] | Difference between UTC from API events and the internal timer (Low) |  |  | U16 |  |  | X | [6 empty] | 69 |  |  | Instance ID = 69 | index = 69 | index = 69 |  |  |  | R | S
7079 | Delta UTC (High) | 1 | [5 empty] | Difference between UTC from API events and the internal timer (High) |  |  | U16 |  |  | X | [6 empty] | 70 |  |  | Instance ID = 70 | index = 70 | index = 70 |  |  |  | R | S
7080 | Post test data operation state | 1 |  |  |  |  | 0 = absent, 1 = ready to start, 2 = in progress, 3 = finished, 4 = retry | State of post test data operation |  |  | U16 |  |  | X | [6 empty] | 71 |  |  | Instance ID = 71 | index = 71 | index = 71 |  |  |  | R | S
7081 | Post data operation state | 1 | [5 empty] | State of post data operation |  |  | U16 |  |  | X | [6 empty] | 72 |  |  | Instance ID = 72 | index = 72 | index = 72 |  |  |  | R | S
7082 | Get renew operation state | 1 | [5 empty] | State of get renew operation |  |  | U16 |  |  | X | [6 empty] | 73 |  |  | Instance ID = 73 | index = 73 | index = 73 |  |  |  | R | S
7083 | Get events operation state | 1 | [5 empty] | State of get events operation |  |  | U16 |  |  | X | [6 empty] | 74 |  |  | Instance ID = 74 | index = 74 | index = 74 |  |  |  | R | S
7084 | Get CRL operation state | 1 | [5 empty] | State of get CRL operation |  |  | U16 |  |  | X | [6 empty] | 75 |  |  | Instance ID = 75 | index = 75 | index = 75 |  |  |  | R | S
7085 | Certificate Revocation List file | 17 |  |  |  |  | 32 ASCII characters configuration file | Name of Configuration Revocation List file used |  |  | U16 |  |  | X | [6 empty] | 76 |  |  | Instance ID = 76 | index = 76 | index = 76 |  |  |  | R | S
7102 | Get events test operation state | 1 |  |  |  |  | 0 = absent, 1 = ready to start, 2 = in progress, 3 = finished, 4 = retry | State of get events test operation |  |  | U16 |  |  | X | [6 empty] | 93 |  |  | Instance ID = 93 | index = 93 | index = 93 |  |  |  | R | S
7103 | Get FW operation state | 1 |  |  |  |  | 0 = absent, 1 = ready to start, 2 = in progress, 3 = finished, 4 = retry | State of get FW operation |  |  | U16 |  |  | X | [6 empty] | 94 |  |  | Instance ID = 94 | index = 94 | index = 94 |  |  |  | R | S
7104 | Executable file | 18 |  |  |  |  | 35 ASCII characters executable file | Name of available executable (for FW Update) |  |  | U16 |  |  | X | [6 empty] | 95 |  |  | Instance ID = 95 | index = 95 | index = 95 |  |  |  | R | S
7122 | Retry Diagnostics | 1 |  |  |  |  | 8 least significant bits: retry exception code 8 most significant bits: Destination Node ID |  |  |  | U16 |  |  | X | [6 empty] | 113 |  |  | Instance ID = 113 | index = 113 | index = 113 |  |  |  | R | S
7123 | API Device communication error detail | 1 |  |  |  |  | -32768 ÷ 32767 | Detail about the error during the communication with API Device |  |  | U16 |  |  | X | [6 empty] | 114 |  |  | Instance ID = 114 | index = 114 | index = 114 |  |  |  | R | S
7124 | Event Hub communication error detail | 1 |  |  |  |  | -32768 ÷ 32767 | Detail about the error during the communication with Event Hub |  |  | U16 |  |  | X | [6 empty] | 115 |  |  | Instance ID = 115 | index = 115 | index = 115 |  |  |  | R | S
7125 | Polling period API Events | 1 |  |  |  |  | 0 ÷ 10080 | Polling period in minute of communication to API Events |  |  | U16 |  |  | X | [6 empty] | 116 |  |  | Instance ID = 116 | index = 116 | index = 116 |  |  |  | R | S

## Tables
COMMANDS |  |  | DIGITAL INPUT FUNCTIONS |  | DIGITAL OUTPUT FUNCTIONS
Type | Value | Parameters | Type | Value | Type | Value
DUMMY COMMAND | 0 | d.c | NO FUNCTION | 0 | NO FUNCTION | 0
ALARM RESET | 1 | d.c | EMERGENCY STOP | 1 | ALARM/PRODUCT AVAILABILITY | 1
SILENCE ALARM | 2 | d.c | REMOTE TEST ON LOAD | 2 | ATS IN POSITION I | 2
NOT USED | 3 |  | REMOTE TEST OFF LOAD | 3 | ATS IN POSITION O | 3
START PROGRAM | 4 | 0 | INHIBIT ATS | 4 | ATS IN POSITION II | 4
ABORT PROGRAM | 5 | d.c | MANUAL RETRANSFER TO PRIORITY SOURCE | 5 | PRE-TRANSFER SIGNAL 1 | 5
END PROGRAM | 6 | 0 | SOURCE PRIORITY S1 | 6 | SOURCE 1 AVAILABLE | 6
SWITCH TO I | 7 | d.c | SOURCE PRIORITY S2 | 7 | SOURCE 2 AVAILABLE | 7
SWITCH TO O | 8 | d.c | INHIBIT TRANSFER | 8 | LOAD SHED OUTPUT SIGNAL | 8
SWITCH TO II | 9 | d.c | BYPASS RUNNING TIME DELAYS | 9 | ELEVATOR PRE-SIGNAL 1 | 9
NOT USED | 10 |  | REMOTE CONTROL TO I | 10 | PRE-TRANSFER SIGNAL 2 | 10
NOT USED | 11 |  | REMOTE CONTROL TO O | 11 | PRE-TRANSFER SIGNAL 3 | 11
NOT USED | 12 |  | REMOTE CONTROL TO II | 12 | PRE-TRANSFER SIGNAL 4 | 12
NOT USED | 13 |  | RESET ALARM | 13 | ELEVATOR PRE-SIGNAL 2 | 13
NOT USED | 14 |  | MANUAL-AUTO MODE | 14 | ELEVATOR PRE-SIGNAL 3 | 14
ENERGY RESET | 15 | d.c | INHIBIT TRANSFER W/ OVERRIDE | 15 | ELEVATOR PRE-SIGNAL 4 | 15
NOT USED | 16 |  | LOAD SHED INPUT SIGNAL | 16 | TRANSFER ALARM | 16
NOT USED | 17 |  | ATS IN I | 17 | ATS IN POSITION OI | 17
NOT USED | 18 |  | ATS IN O | 18 | ATS IN POSITION OII | 18
NOT USED | 19 |  | ATS IN II | 19
NOT USED | 20 |  | ATS TEST | 20
NOT USED | 21 |  | ATS CONNECTED | 21
ACTIVATE AUTOMATIC CONFIGURATION | 22 | d.c | BYPASS IN I | 22
TruCONTROL: WAIT | 23 | d.c | BYPASS IN O | 23
TruCONTROL: DELAY mode | 24 | d.c | BYPASS IN II | 24
SET AUTO | 25 | d.c | BYPASS TEST | 25
SET MANUAL | 26 | d.c | BYPASS CONNECTED | 26
SET MANUAL RETRANSFER | 27 | d.c
TEST ON LOAD | 28 | d.c
TEST OFF LOAD | 29 | d.c
BYPASS TIME DELAY | 30 | d.c

## Events
EVENTS
Status | Nr | Ev
Status Global 1
Source 1 Connected | 1 | ▲▼
NOT USED | 2
NOT USED | 3
Source 1 Status | 4 | ▲▼
Auto Config Active | 5 | ▲▼
Auto Config Ready | 6 | ▲
Automatic Mode | 7 | ▲▼
Source 2 Connected | 8 | ▲▼
Local / Remote | 9 | ▲▼
Source 2 Status | 10 | ▲▼
NOT USED | 11
NOT USED | 12
NOT USED | 13
NOT USED | 14
Off Position | 15 | ▲▼
NOT USED | 16
Status Glitch 1
Parameter(s) Changed | 33 | ▲
Alarm Reset | 34 | ▲
NOT USED | 35
NOT USED | 36
NOT USED | 37
NOT USED | 38
NOT USED | 39
NOT USED | 40
NOT USED | 41
NOT USED | 42
NOT USED | 43
NOT USED | 44
Energy Reset | 45 | ▲
NOT USED | 46
NOT USED | 47
NOT USED | 48
Status Flags 1
NOT USED | 65
NOT USED | 66
NOT USED | 67
NOT USED | 68
NOT USED | 69
NOT USED | 70
Supply from Vaux | 71 | ▲▼
NOT USED | 72
Supply from Voltage Module | 73 | ▲▼
NOT USED | 74
NOT USED | 75
NOT USED | 76
NOT USED | 77
NOT USED | 78
Generator Usage | 79 | ▲▼
Generator Status | 80 | ▲▼
Status Timing 1
Override S1 Failure Delay | 129 | ▲▼
Transfer from S1 to S2 Delay | 130 | ▲▼
Override S2 Failure Delay | 131 | ▲▼
NOT USED | 132
Transfer from S2 to S1 Delay | 133 | ▲▼
Generator Stop Delay | 134 | ▲▼
Center-Off Delay | 135 | ▲▼
Elevator Pre-transfer Delay | 136 | ▲▼
Elevator Post-transfer Delay | 137 | ▲▼
Pre-transfer Delay | 138 | ▲▼
Post-transfer Delay | 139 | ▲▼
NOT USED | 140
NOT USED | 141
Load Shed Delay | 142 | ▲▼
NOT USED | 143
NOT USED | 144
Status Timing 3
NOT USED | 161
Pre-transfer 2 Delay | 162 | ▲▼
Post-transfer 2 Delay | 163 | ▲▼
Pre-transfer 3 Delay | 164 | ▲▼
Post-transfer 3 Delay | 165 | ▲▼
Pre-transfer 4 Delay | 166 | ▲▼
Post-transfer 4 Delay | 167 | ▲▼
Elevator Pre-transfer 2 Delay | 168 | ▲▼
Elevator Post-transfer 2 Delay | 169 | ▲▼
Elevator Pre-transfer 3 Delay | 170 | ▲▼
Elevator Post-transfer 3 Delay | 171 | ▲▼
Elevator Pre-transfer 4 Delay | 172 | ▲▼
Elevator Post-transfer 4 Delay | 173 | ▲▼
NOT USED | 174
NOT USED | 175
NOT USED | 176
Status Warnings Alarms 1
Test on Load | 209 | ▲▼
Test off Load | 210 | ▲▼
Fire Fighting | 211 | ▲▼
NOT USED | 212
Locked | 213 | ▲▼
Handle | 214 | ▲▼
NOT USED | 215
Incompatible HMI alarm | 216 | ▲▼
Manual-Auto Mode | 217 | ▲
Phases Crossed | 218 | ▲▼
S1 Undervoltage | 219 | ▲▼
S1 Overvoltage | 220 | ▲▼
S1 Phase Missing | 221 | ▲▼
S1 Unbalance | 222 | ▲▼
S1 Phase Rotation | 223 | ▲▼
S1 Invalid Frequency | 224 | ▲▼
Status Warnings Alarms 2
Frequency Difference | 225 | ▲▼
S2 Undervoltage | 226 | ▲▼
S2 Overvoltage | 227 | ▲▼
S2 Phase Missing | 228 | ▲▼
S2 Unbalance | 229 | ▲▼
S2 Phase Rotation | 230 | ▲▼
S2 Invalid Frequency | 231 | ▲▼
Contact Wear PreAlarm | 232 | ▲▼
Contact Wear Alarm | 233 | ▲▼
Elevator Pre-transfer Signal | 234 | ▲▼
Open I Failure | 235 | ▲▼
Close I Failure | 236 | ▲▼
Open II Failure | 237 | ▲▼
Close II Failure | 238 | ▲▼
Switch Position Alarm | 239 | ▲▼
High Current Alarm | 240 | ▲▼
Status Warnings Alarms 3
Internal Error | 241 | ▲▼
Alarm/Product Availability | 242 | ▲▼
In Position I | 243 | ▲▼
Invalid Date Warning | 244 | ▲▼
Control Voltage Failure | 245 | ▲▼
Pole Temperature Alarm | 246 | ▲▼
Pole Temperature Warning | 247 | ▲▼
Control Retry | 248 | ▲▼
In Position O | 249 | ▲▼
In Position II | 250 | ▲▼
Pre-transfer Signal | 251 | ▲▼
Auto Control Disabled | 252 | ▲▼
Permanent Manual Mode | 253 | ▲▼
Control Voltage Low | 254 | ▲▼
Voltage Not Calibrated | 255 | ▲▼
Current Not Calibrated | 256 | ▲▼
Status Warnings Alarms 4
Emergency Stop | 257 | ▲▼
Remote Test on Load | 258 | ▲▼
Remote Test off Load | 259 | ▲▼
Inhibit ATS | 260 | ▲▼
Manual Retransfer | 261 | ▲▼
Priority S1 | 262 | ▲▼
Priority S2 | 263 | ▲▼
Inhibit Transfer | 264 | ▲▼
Bypass Running Delays | 265 | ▲▼
Remote Control to S1 | 266 | ▲▼
Remote Control to Off | 267 | ▲▼
Remote Control to S2 | 268 | ▲▼
Alarm Reset | 269 | ▲▼
Source 1 Available | 270 | ▲▼
Source 2 Available | 271 | ▲▼
Load Shed | 272 | ▲▼
Status Warnings Alarms 5
NOT USED | 273
NOT USED | 274
NOT USED | 275
S1 Neutral disconnected | 276 | ▲▼
S2 Neutral disconnected | 277 | ▲▼
NOT USED | 278
NOT USED | 279
NOT USED | 280
NOT USED | 281
NOT USED | 282
NOT USED | 283
Generator Exerciser Test on Load | 284 | ▲▼
NOT USED | 285
Generator Exerciser Test off Load | 286 | ▲▼
NOT USED | 287
NOT USED | 288
Status Warnings Alarms 6
NOT USED | 289
NOT USED | 290
NOT USED | 291
NOT USED | 292
NOT USED | 293
Inhibit Transfer w/ Override | 294 | ▲▼
Load Shed Input Signal | 295 | ▲▼
Transfer Alarm | 296 | ▲▼
NOT USED | 297
NOT USED | 298
Pre-transfer Signal 2 | 299 | ▲▼
Pre-transfer Signal 3 | 300 | ▲▼
Pre-transfer Signal 4 | 301 | ▲▼
Elevator Pre-transfer Signal 2 | 302 | ▲▼
Elevator Pre-transfer Signal 3 | 303 | ▲▼
Elevator Pre-transfer Signal 4 | 304 | ▲▼